## Executive Summary
Executive Summary: ERAS-2025-001 Interconnection Facilities Study Report
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Expedited Resource Adequacy Study (ERAS) for generation interconnection requests received during the ERAS Queue Cluster Window which closed on October 2, 2025. The primary objective of this ERAS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this ERAS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. ERAS-2025-001 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest )
DISIS Manual Version 4.4
https://spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
This ERAS analyzes the impact of interconnecting new generation for total of:
13,262.06 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $784,546,773.71 Steady State Network Upgrade $337,892,742.32 Interconnection Costs: $446,654,031.39
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
By: SPP Generator Interconnection Department
Published:5/26/2026
Costs for Solar/Battery Requests were allocated using the 29SP (summer peak) model.
Costs for Wind Requests were allocated using the 29L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
For CQ projects sharing a generation interconnection line, the Reactive Compensation required for the line was split proportionally based on MW between all connected CQ projects.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4616800% | SPP | Draft Report

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status | JTIQ Particpant
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 20 | [9 empty] | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 10 | [9 empty] | ER | SPS
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | WIND | 19.8 | [9 empty] | ER | SPS
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | WIND | 11.5 | [9 empty] | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 35 | [9 empty] | ER | KCPL
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 35 | [9 empty] | ER | KCPL
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | WIND | 7.5 | [9 empty] | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
ERAS-2025-001 | 02 NEBRASKA | 23 | ERAS-2025-001 | Thermal | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 0 | ER/NR | LES | 84th & Bluff 115kV Substation | ERAS | Yes
ERAS-2025-002 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 217 | 0 | 208 | 0 | 208 | 0 | 208 | 217 | 217 | 0 | ER/NR | SPS | Xcel Tuco 345kV Substation | ERAS | No
ERAS-2025-003 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 0 | ER/NR | OGE | Redbud 345kV Substation | ERAS | Yes
ERAS-2025-004 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 763 | 763 | 763 | 763 | 763 | 763 | 763 | 763 | 763 | 0 | ER/NR | OGE | Horseshoe Lake 138kV Substation | ERAS | Yes
ERAS-2025-005 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Hybrid | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -0.77 | ER/NR | AEP | Danville - Magazine 161kV Line | ERAS | Yes
ERAS-2025-006 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 717.8 | 690 | 690 | 690 | 690 | 690 | 690 | 717.8 | 717.8 | 0 | ER/NR | WERE | Reno County 345 kV Substation #1443 | ERAS | No
ERAS-2025-007 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 450.6 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 450.6 | 450.6 | 0 | ER/NR | WERE | Mullin Creek 345 kV Substation | ERAS | Yes
ERAS-2025-008 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 721.1 | 693.2 | 638.0394 | 693.2 | 638.0394 | 693.2 | 638.0394 | 721.1 | 721.1 | 0 | ER/NR | WERE | Viola 345 kV Substation | ERAS | No
ERAS-2025-009 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 0 | ER/NR | GRDA | Grec #1 Interconnect 161kV Substation | ERAS | Yes
ERAS-2025-010 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 496 | 496 | 496 | 496 | 496 | 496 | 496 | 496 | 496 | 0 | ER/NR | OGE | Horseshoe Lake 138kV Substation | ERAS | Yes
ERAS-2025-011 | 01 NORTH | 23 | ERAS-2025-001 | Thermal | 750 | 0 | 0 | 750 | 750 | 0 | 0 | 0 | 0 | 0 | ER/NR | BEPC | Leland Olds 345kV Substation | ERAS | Yes
ERAS-2025-012 | 01 NORTH | 23 | ERAS-2025-001 | Thermal | 750 | 0 | 0 | 750 | 750 | 0 | 0 | 0 | 0 | 0 | ER/NR | BEPC | Leland Olds 345kV Substation | ERAS | Yes
ERAS-2025-013 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 450.6 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 425.1 | 450.6 | 450.6 | 0 | ER/NR | WERE | Mullin Creek 345 kV Substation | ERAS | Yes
ERAS-2025-014 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 159.5 | 0 | 120.5 | 0 | 120.5 | 0 | 120.5 | 159.5 | 159.5 | 0 | ER/NR | SPS | Hobbs-Andrews 345kV Line | ERAS | No
ERAS-2025-015 | 03 CENTRAL | 23 | ERAS-2025-001 | Hybrid | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | -5.5 | ER/NR | SEPC | Holcomb 345 kV Substation | ERAS | No
ERAS-2025-016 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 232.5 | 0 | 224.7 | 0 | 224.7 | 0 | 224.7 | 232.5 | 232.5 | 0 | ER/NR | SPS | Tolk 230kV Substation | ERAS | No
ERAS-2025-017 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 600 | 600 | 481.9803 | 600 | 481.9803 | 600 | 481.9803 | 600 | 600 | 0 | ER/NR | SEPC | Holcomb 345 kV Substation | ERAS | No
ERAS-2025-018 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Hybrid | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 256 | -8.89 | ER/NR | SPS | Oasis 230kV Substation | ERAS | No
ERAS-2025-019 | 03 CENTRAL | 23 | ERAS-2025-001 | Solar | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0.2 | ER/NR | MIDW | Kinsley 115 kV Substation | ERAS | No
ERAS-2025-020 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Hybrid | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.42 | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | ERAS | No
ERAS-2025-021 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Wind | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | -22.57 | ER/NR | SPS | Border-Tuco 345kV Line | ERAS | No
ERAS-2025-022 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Battery/Storage | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | 123 | -0.1 | ER/NR | PEC | Monte Vista 138 kV Substation | ERAS | Yes
ERAS-2025-023 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 510 | 505 | 505 | 505 | 505 | 505 | 505 | 510 | 510 | 0 | ER/NR | AEP | Northeastern 345 kV Substation | ERAS | Yes
ERAS-2025-024 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Thermal | 744 | 404.4588 | 542.437 | 404.4588 | 542.437 | 404.4588 | 542.437 | 744 | 744 | 0 | ER/NR | AEP | Comanche 138kV Substation | ERAS | No
ERAS-2025-025 | 04 SOUTHEAST | 23 | ERAS-2025-001 | Solar | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | -1.34 | ER/NR | WFEC | Washita 138kV Substation | ERAS | No
ERAS-2025-026 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Thermal | 744 | 0 | 665 | 0 | 665 | 0 | 665 | 744 | 744 | 0 | ER/NR | AEP | Oklaunion-Lawton East Side 345kV Line | ERAS | No
ERAS-2025-027 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 250 | -0.23 | ER/NR | SPS | Mahoney 230kV Substation | ERAS | No
ERAS-2025-028 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Solar | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 384 | -5.6 | ER/NR | SPS | Tuco-Yoakum 345kV Line | ERAS | No
ERAS-2025-029 | 03 CENTRAL | 23 | ERAS-2025-001 | Battery/Storage | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | -0.11296 | ER/NR | KACY | Nearman 161 kV Substation | ERAS | Yes
ERAS-2025-030 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Hybrid | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 350 | -22.18 | ER/NR | SPS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | ERAS | No
ERAS-2025-031 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | ER/NR | KACY | Quindaro 161kV Substation | ERAS | Yes
ERAS-2025-032 | 03 CENTRAL | 23 | ERAS-2025-001 | Hybrid | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -1 | ER/NR | SEPC | St. John 115 kV Substation | ERAS | No
ERAS-2025-033 | 03 CENTRAL | 23 | ERAS-2025-001 | Battery/Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -0.6 | ER/NR | SEPC | Fort Dodge 115 kV Substation | ERAS | No
ERAS-2025-034 | 03 CENTRAL | 23 | ERAS-2025-001 | Thermal | 250 | 205.1928 | 78.8246 | 205.1928 | 78.8246 | 205.1928 | 78.8246 | 250 | 250 | 0 | ER/NR | EMDE | State Line 439 161 kV Substation | ERAS | Yes
ERAS-2025-035 | 01 NORTH | 23 | ERAS-2025-001 | Thermal | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 137.96 | 0 | ER/NR | NWPS | Siebrecht 115 kV Substation | ERAS | Yes
ERAS-2025-036 | 05 SOUTHWEST | 23 | ERAS-2025-001 | Battery/Storage | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 140 | -0.27 | ER/NR | SPS | Newhart - Potter 230 kV Line | ERAS | No
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 75 | [9 empty] | ER | NPPD | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 16 | [9 empty] | ER/NR | BEPC-SPP
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 131.1 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEP |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 197.8 | [9 empty] | ER | OGE | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | MKEC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.5 | [9 empty] | ER | MIDW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 3 | DIS-09-1 | Thermal | 675 | [9 empty] | ER | MIPU |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 200 | [9 empty] | ER/NR | BEPC-SPP
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | [9 empty] | ER | MIDW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OGE | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 34 | [9 empty] | ER/NR | BEPC-SPP
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | 05 SOUTHWEST | 4 | DIS-10-1 | Thermal | 205 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | [9 empty] | ER | OGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | [9 empty] | ER | NPPD |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Hybrid: Solar and Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Hybrid: Solar and Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | [9 empty] | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC-SPP | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [9 empty] | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid: Solar | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | BEPC-SPP | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [9 empty] | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [9 empty] | ER | WERE | Neosho 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | BEPC-SPP | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA PENDING
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA PENDING
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | WITHDRAWN
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA PENDING
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA PENDING
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [9 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA PENDING
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid: Storage and Wind | 110 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA PENDING
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [9 empty] | ER | OPPD | 6846 Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | FACILITY STUDY STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [9 empty] | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | FACILITY STUDY STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [9 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [9 empty] | ER/NR | BEPC | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | FACILITY STUDY STAGE
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | [9 empty] | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | FACILITY STUDY STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | FACILITY STUDY STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Russell 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | FACILITY STUDY STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 21 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [9 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | FACILITY STUDY STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [9 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | FACILITY STUDY STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | FACILITY STUDY STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Patent Gate Substation 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | FACILITY STUDY STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-SR2 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-SR8 | 03 CENTRAL | 22.5 | SURPLUS | Solar | 42 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-SR9 | 03 CENTRAL | 22.5 | SURPLUS | Solar | 10 | [9 empty] | ER/NR | KCPL |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-GR1 | 04 SOUTHEAST | 22.5 | REPLACEMENT | THERMAL | 513 | [9 empty] | ER | AEPW |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR1 | 04 SOUTHEAST | 22.5 | REPLACEMENT | THERMAL | 97.488 | [9 empty] | ER | WFEC |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR2 | 04 SOUTHEAST | 22.5 | REPLACEMENT | THERMAL | 94.242 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR3 | 05 SOUTHWEST | 22.5 | REPLACEMENT | Wind | 80 | [9 empty] | ER/NR | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 22.5 | REPLACEMENT | Solar | 72 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR5 | 05 SOUTHWEST | 22.5 | REPLACEMENT | Solar | 150 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR1 | 02 NEBRASKA | 22.5 | SURPLUS | THERMAL | 21.9 | [9 empty] | ER/NR | NPPD |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR12 | 05 SOUTHWEST | 22.5 | SURPLUS | Battery/Storage | 120 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR13 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 70 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-SR16 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 70 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR18 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 80 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-SR28 | 03 CENTRAL | 22.5 | SURPLUS | Solar | 150 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR4 | 01 NORTH | 22.5 | SURPLUS | Battery/Storage | 170.02 | [9 empty] | ER | BEPC |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR5 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 85.01 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR8 | 05 SOUTHWEST | 22.5 | SURPLUS | Battery/Storage | 200 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-SR9 | 05 SOUTHWEST | 22.5 | SURPLUS | Battery/Storage | 50 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2024-SR2 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 72.774 | [9 empty] | ER/NR | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2024-SR3 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 72.766 | [9 empty] | ER/NR | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2024-SR5 | 04 SOUTHEAST | 22.5 | SURPLUS | Battery/Storage | 176.9 | [9 empty] | ER | OKGE |  | IA FULLY EXECUTED/ON SCHEDULE
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 40 | [9 empty] | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-106 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 350.08 | [9 empty] | ER/NR | AECI
GIA-107 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 250 | [9 empty] | ER/NR | AECI
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | [9 empty] | ER | AECI
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | Done
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | Done
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | Done
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | Done
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Done
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Done
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | Done
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Done
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Done
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | Done
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Done
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW | Traer 161-kV Substation | Done
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | Done
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | Done
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Done
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Done
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Done
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Done
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | Done
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | Done
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Done
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Done
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Done
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | Done
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Done
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Done
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Done
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | Done
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Done
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Done
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | Done
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | Done
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | Done
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | Done
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES | Goos Ferry | Done
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Done
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | Done
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 120 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | Done
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Done
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Pipestone to Split Rock 115kV | Done
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Done
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Done
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Done
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Done
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Done
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Done
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Done
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Done
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | Done
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Done
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | Done
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | [9 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Done
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | [9 empty] | ER/NR | DPC | Barron 161 kV | Done
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Done
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Done
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | Done
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Done
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | Done
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | WIND | 246 | [9 empty] | ER/NR | AMMO
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation | Done: Phase 3
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | WIND | 100 | [9 empty] | ER/NR | XEL
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | Done: GIA
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation | Done: Phase 3
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | Done: GIA
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Done: Phase 3
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation | Done: Phase 3
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: Phase 3
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: Phase 3
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: Phase 3
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: Phase 3
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL | Adams 345kV Substation | Done
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done
LLANOESTACADOWHITEDEER | 05 SOUTHWEST | 8 | PQ | WIND | 80 | [9 empty] | ER | SPS
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 170 | [9 empty] | ER | OTP
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 130 | [9 empty] | ER | OTP
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | [9 empty] | ER/NR | OTP
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | [9 empty] | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 300 | [9 empty] | ER/NR | OTP
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 400 | [9 empty] | ER/NR | OTP
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
NPPDSPRINGVIEW | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | WIND | 3 | [9 empty] | ER | NPPD
SPSCARSON | 05 SOUTHWEST | 8 | PQ | WIND | 10 | [9 empty] | ER | SPS
SPSDUMAS19THST | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSETTER | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSLEACOUNTY | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | SOLAR | 5.5 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
SPSMOOREE | 05 SOUTHWEST | 8 | PQ | WIND | 17.5 | [9 empty] | ER | SPS
SPSSHERMAN | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SUNRAY | 05 SOUTHWEST | 8 | PQ | WIND | 34.5 | [9 empty] | ER | SPS

## Assigned Upgrade Costs - FS
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | Lead Time | PTDF | Note | TO | Column1
ERAS-2025-001 | ERAS-2025-001 | 02 NEBRASKA | 170753 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (Non-shared NU) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | 0 | 100% | 0 | n/a | 1 | zero per TO | LES
ERAS-2025-001 | ERAS-2025-001 | 02 NEBRASKA | 170752 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (TOIF) (LES) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | 44275 | 100% | 44275 | 24 | 1 |  | LES
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 3903406.6554 | 3.173% | 9932652 |  | 0.01496
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 |  | N/A
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-002 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 351943.92 | 4.322% | 8143803 | 48 | 0.02928 |  | Evergy
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 170803 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | 0 | 100% | 0 | n/a | 1 | zero $ per TO via RMS #4836
ERAS-2025-002 | ERAS-2025-001 | 05 SOUTHWEST | 170802 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | 0 | 100% | 0 | n/a | 1 | zero $ per TO via RMS #4836
ERAS-2025-003 | ERAS-2025-001 CF | 04 SOUTHEAST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-003 | ERAS-2025-001 CF | 04 SOUTHEAST | 503211 | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 16661900 |  | N/A
ERAS-2025-003 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | NRIS | Trosper - Reno 138 kV Line Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | N/A
ERAS-2025-003 | ERAS-2025-001 | 04 SOUTHEAST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 342053.23 | 4.2% | 8143803 | 48 | 0.0332 |  | Evergy
ERAS-2025-003 | ERAS-2025-001 | 04 SOUTHEAST | 170795 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (Non-shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | 0 | 100% | 0 |  | 1 |  | OGE
ERAS-2025-003 | ERAS-2025-001 | 04 SOUTHEAST | 170794 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | 0 | 100% | 0 |  | 1 |  | OGE
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 503211 | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 16661900 |  | N/A
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 |  | 0.08308
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 |  | 0.18975
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | 0 | 0% | 61120000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 501015 | NRIS | NE 10th - Reno 138 kV Line Rebuild | Contingent | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 0 | 0% | 8392000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | NRIS | Trosper - Reno 138 kV Line Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | 0.12074
ERAS-2025-004 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | N/A
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 1372301.34 | 16.85% | 8143803 | 48 | 0.03247 |  | Evergy
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 170774 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004 (779MW/Thermal), into Horseshoe Lake 138kV Substation | 0 | 100% | 0 |  | 1 |  | OGE
ERAS-2025-004 | ERAS-2025-001 | 04 SOUTHEAST | 170807 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004/ERAS-2025-010 Interconnection (Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004/ERAS-2025-010 (779/496MW/Thermal/Thermal), into Horseshoe Lake 138kV Substation | 0 | 60.6% | 0 |  | 1 |  | OGE
ERAS-2025-005 | ERAS-2025-001 | 04 SOUTHEAST | 170763 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | 13962995 | 100% | 13962995 | 36 | 1 |  | AEP
ERAS-2025-005 | ERAS-2025-001 | 04 SOUTHEAST | 170762 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | 3735736 | 100% | 3735736 | 36 | 1 |  | AEP
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 58.56% | 3907935 |  | 0.02268
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 170816 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (Non-shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | 9918207 | 100% | 9918207 | 48 | 1 |  | Evergy
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 170815 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | 2118099 | 100% | 2118099 | 48 | 1 |  | Evergy
ERAS-2025-006 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 3784514.9795 | 14.39% | 26301311 | 40 | 0.03601 |  | SEPC
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | 170809 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | 2420597.3435 | 100% | 2122145 | 48 | 1 |  | Evergy
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | 170819 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007/013 Interconnection (Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007/013 (450.6/450.6MW/Thermal/Thermal), into Mullin Creek 345 kV Substation | 3786076.9278 | 50% | 24108835 |  | 1 |  | Evergy
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 2420597.3435 | 9.203% | 26301311 | 40 | 0.03669 |  | SEPC
ERAS-2025-007 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 5362127.84 | 39.51% | 13571142 | 48 | 0.07316 |  | Evergy
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 21.53% | 3907935 |  | 0.0083
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 170818 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (Non-shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | 1957314 | 100% | 1957314 | 48 | 1 | Cost updated per TO | Evergy
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 170817 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | 2122145 | 100% | 2122145 | 48 | 1 | Cost updated per TO | Evergy
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 3786076.93 | 14.4% | 26301311 | 40 | 0.03586 |  | SEPC
ERAS-2025-008 | ERAS-2025-001 | 03 CENTRAL | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 2104584.44 | 25.84% | 8143803 | 48 | 0.05269 |  | Evergy
ERAS-2025-009 | ERAS-2025-001 | 04 SOUTHEAST | 170766 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation | 2953500 | 100% | 2953500 |  | 1 |  | GRDA
ERAS-2025-009 | ERAS-2025-001 | 04 SOUTHEAST | 170767 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (Non-shared NU) (GRDA) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 0 | 100% | 0 | n/a | 1 | zero $ per TO | GRDA
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 503211 | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 16661900 |  | N/A
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 |  | 0.09855
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 500030 | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | 0 | 0% | 9044000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 |  | 0.21266
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 900189 | ERIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | 0 | 0% | 61120000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Horseshoe Lake Reconfiguration | Contingent | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | 0 | 0% | 61120000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 501015 | NRIS | NE 10th - Reno 138 kV Line Rebuild | Contingent | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | 0 | 0% | 8392000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | NRIS | Trosper - Reno 138 kV Line Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | 0.12339
ERAS-2025-010 | ERAS-2025-001 CF | 04 SOUTHEAST | 500003 | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | Contingent | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | 0 | 0% | 6178000 |  | N/A
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 894283.73 | 10.98% | 8143803 | 48 | 0.03255 |  | Evergy
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 170807 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004/ERAS-2025-010 Interconnection (Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004/ERAS-2025-010 (779/496MW/Thermal/Thermal), into Horseshoe Lake 138kV Substation | 0 | 39.4% | 0 |  | 1 |  | OGE
ERAS-2025-010 | ERAS-2025-001 | 04 SOUTHEAST | 170775 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-010 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-010 (496MW/Thermal), into Horseshoe Lake 138kV Substation | 0 | 100% | 0 |  | 1 |  | OGE
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 | 50% | 243120 |  | 0.02939
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 172058 | ERIS | Kummer Ridge 345 kV Capacitor Bank | Current Study | Install 300 MVAR Capacitor Bank at Kummer Ridge 345 kV substation | 13379860.5 | 50% | 26759721 | 64 | 0.01779 |  | BEPC
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 170808 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011/ (750MW/Thermal), into Leland Olds 345kV Switchyard | 11125027 | 100% | 11125027 | 64 | 1 |  | BEPC
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 170778 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011 (750MW/Thermal), into Leland Olds 345kV Switchyard | 3197273 | 100% | 3197273 | 64 | 1 |  | BEPC
ERAS-2025-011 | ERAS-2025-001 | 01 NORTH | 172064 | ERIS | Replacement of two disconnect switches at Antelope Valley Station | Current Study | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | 232573 | 50% | 465146 | 64 | 0.12488 |  | BEPC
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 | 50% | 243120 |  | 0.03379
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 172058 | ERIS | Kummer Ridge 345 kV Capacitor Bank | Current Study | Install 300 MVAR Capacitor Bank at Kummer Ridge 345 kV substation | 13379860.5 | 50% | 26759721 | 64 | 0.01779 |  | BEPC
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 170821 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | 2785359 | 100% | 2785359 | 64 | 1 |  | BEPC
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 170779 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | 3197273 | 100% | 3197273 | 64 | 1 |  | BEPC
ERAS-2025-012 | ERAS-2025-001 | 01 NORTH | 172064 | ERIS | Replacement of two disconnect switches at Antelope Valley Station | Current Study | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | 232573 | 50% | 465146 | 64 | 0.12488 |  | BEPC
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | 170819 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007/013 Interconnection (Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007/013 (450.6/450.6MW/Thermal/Thermal), into Mullin Creek 345 kV Substation | 12054417.5 | 50% | 24108835 |  | 1 |  | Evergy
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | 170810 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-013 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-013 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | 2122145 | 100% | 2122145 | 48 | 1 |  | Evergy
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 2420597.34 | 9.203% | 26301311 | 40 | 0.03669 |  | SEPC
ERAS-2025-013 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 5632127.84 | 39.51% | 13571142 | 48 | 0.07316 |  | Evergy
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% | 73524573 |  | 0.23195
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 5855109.983 | 2.005% | 9932652 |  | 0.01286
ERAS-2025-014 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-014 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-014 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 252679.14 | 3.103% | 8143803 | 48 | 0.0286 |  | Evergy
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 170769 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | 0 | 100% | 0 | n/a | 1 | zero $ per TO via RMS #4836 | SPS
ERAS-2025-014 | ERAS-2025-001 | 05 SOUTHWEST | 170768 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | 0 | 100% | 0 | n/a | 1 | zero $ per TO via RMS #4836 | SPS
ERAS-2025-015 | ERAS-2025-001 CF | 03 CENTRAL | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-015 | ERAS-2025-001 CF | 03 CENTRAL | 169968 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 0 | 0% | 1050598691 |  | N/A
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | 170772 | ERIS | Holcomb 345 kV Substation ERAS-2025-015 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015 (400MW/Hybrid), into Holcomb 345 kV Substation | 5238900 | 100% | 5238900 | 46 | 1 |  | SEPC
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | 170806 | ERIS | Holcomb 345 kV Substation ERAS-2025-015/ERAS-2025-017 Interconnection (Shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015/ERAS-2025-017 (400/600MW/Hybrid/Thermal), into Holcomb 345 kV Substation | 15408778.8 | 40% | 38521947 | 46 | 1 |  | SEPC
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 3903406.66 | 14.84% | 26301311 | 40 | 0.06665 |  | SEPC
ERAS-2025-015 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 761510.71 | 5.614% | 13571142 | 48 | 0.01171 |  | Evergy
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 389462.1794 | 2.841% | 9932652 |  | 0.0125
ERAS-2025-016 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-016 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-016 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 369355.67 | 4.535% | 8143803 | 48 | 0.02868 |  | Evergy
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 170797 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | 1844589 | 100% | 1844589 | 42 | 1 |  | SPS
ERAS-2025-016 | ERAS-2025-001 | 05 SOUTHWEST | 170796 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | 3997457 | 100% | 3997457 | 42 | 1 |  | SPS
ERAS-2025-017 | ERAS-2025-001 CF | 03 CENTRAL | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 169968 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 0 | 0% | 1050598691 |  | 0.10841
ERAS-2025-017 | ERAS-2025-001 CF | 03 CENTRAL | 169968 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 0 | 0% | 1050598691 |  | N/A
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 170806 | ERIS | Holcomb 345 kV Substation ERAS-2025-015/ERAS-2025-017 Interconnection (Shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015/ERAS-2025-017 (400/600MW/Hybrid/Thermal), into Holcomb 345 kV Substation | 23113168.2 | 60% | 38521947 | 46 | 1 |  | SEPC
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 170773 | ERIS | Holcomb 345 kV Substation ERAS-2025-017 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-017 (600MW/Thermal), into Holcomb 345 kV Substation | 5238900 | 100% | 5238900 | 46 | 1 |  | SEPC
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 5855109.98 | 22.26% | 26301311 | 40 | 0.06665 |  | SEPC
ERAS-2025-017 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 1142859.8 | 8.421% | 13571142 | 48 | 0.01171 |  | Evergy
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 1995728.3955 | 10.53% | 18952333 | 48 | 0.20461 |  | AEP
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 30072160.0128 | 10.53% | 285578735 | 48 | 0.20461 |  | AEP
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 904767.4954 | 3.128% | 9932652 |  | 0.0125
ERAS-2025-018 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-018 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 8.926% | 1366342009.8205 |  | 0.11172
ERAS-2025-018 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 13.81% | 224939250 |  | 0.12984
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 118957.92 | 11.51% | 1033518 | 24 | 0.05787 |  | AEP
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 5012787.55 | 11.51% | 43551586 | 48 | 0.05787 |  | AEP
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 170791 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | 25055453 | 100% | 25055453 | 42 | 1 |  | SPS
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 170790 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | 4121397 | 100% | 4121397 | 42 | 1 |  | SPS
ERAS-2025-018 | ERAS-2025-001 | 05 SOUTHWEST | 172065 | ERIS | Tolk 345/230 kV CKT 1 Transformer Replacement | Current Study | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | 25186202 | 100% | 25186202 | 42 | 0.18 |  | SPS
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 157186 | NRIS | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Contingent | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 0 | 34.77% | 593064 |  | 0.04856
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 4.869% | 3907935 |  | 0.01692
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 389462.18 | 1.481% | 26301311 | 40 | 0.03325 |  | SEPC
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 131809.72 | 0.9713% | 13571142 | 48 | 0.01013 |  | Evergy
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 170785 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (Non-shared NU) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | 7684468.75 | 100% | 7684468.75 | 32 | 1 | Cost updated from TO. TO provided consolidated cost for both UID 170785 abd 170784. | MIDW
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 170784 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (TOIF) (MIDW) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | 1206505.16 | 100% | 1206505.16 | 32 | 1 | Cost updated from TO. TO provided consolidated cost for both UID 170785 abd 170784. | MIDW
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 172062 | NRIS | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1 | Current Study | Replace the existing SEWRDMW3 to SEWARD 2 115-69 kV transformer 1 with a minimum rating of 55 MVA | 2255645.0159 | 34.78% | 6486381.72 | 30 | 0.09048 | Updated per TO | MIDW
ERAS-2025-019 | ERAS-2025-001 | 03 CENTRAL | 172061 | NRIS | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1 | Current Study | Rebuild the existing SEWARD 3 to ST-JOHN3 115 kV line 1 (14.69 miles) to a minimum rating of 115 MVA | 5108640.2743 | 34.78% | 14690000 |  | 0.43225 |  | SEPC
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 3281092.4309 | 17.31% | 18952333 | 48 | 0.21529 |  | AEP
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 49440363.1387 | 17.31% | 285578735 | 48 | 0.21529 |  | AEP
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% | 73524573 |  | 0.04787
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 798324.2606 | 5.052% | 9932652 |  | 0.01292
ERAS-2025-020 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-020 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 25.47% | 1366342009.8205 |  | 0.20406
ERAS-2025-020 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 20.82% | 224939250 |  | 0.12531
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 183139.39 | 17.72% | 1033518 | 24 | 0.05701 |  | AEP
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 7717341.04 | 17.72% | 43551586 | 48 | 0.05701 |  | AEP
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170771 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | 50675620 | 100% | 50675620 | 42 | 1 |  | SPS
ERAS-2025-020 | ERAS-2025-001 | 05 SOUTHWEST | 170770 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | 7390573 | 100% | 7390573 | 42 | 1 |  | SPS
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 4318349.8551 | 22.79% | 18952333 | 48 | 0.22668 |  | AEP
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 65070030.6347 | 22.79% | 285578735 | 48 | 0.22668 |  | AEP
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Contingent | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 0 | 0% | 73524573 |  | 0.01185
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 730241.5864 | 7.332% | 9932652 |  | 0.015
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 27.9% | 1366342009.8205 |  | 0.17881
ERAS-2025-021 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 10.85% | 224939250 |  | 0.05225
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 215798.56 | 20.88% | 1033518 | 24 | 0.05374 |  | AEP
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 9093571.16 | 20.88% | 43551586 | 48 | 0.05374 |  | AEP
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170759 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | 49350930 | 100% | 49350930 | 42 | 1 |  | SPS
ERAS-2025-021 | ERAS-2025-001 | 05 SOUTHWEST | 170758 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | 7384210 | 100% | 7384210 | 42 | 1 |  | SPS
ERAS-2025-022 | ERAS-2025-001 | 04 SOUTHEAST | 170783 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (Non-shared NU) (PEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | 1165190 | 100% | 1165190 | 22 | 1 |  | PEC
ERAS-2025-022 | ERAS-2025-001 | 04 SOUTHEAST | 170782 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (TOIF) (PEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | 2573308 | 100% | 2573308 | 14 | 1 |  | PEC
ERAS-2025-023 | ERAS-2025-001 | 04 SOUTHEAST | 170787 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | 3989596 | 100% | 3989596 | 36 | 1 | Updated per TO | AEP
ERAS-2025-023 | ERAS-2025-001 | 04 SOUTHEAST | 170786 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | 5476117 | 100% | 5476117 | 36 | 1 | Updated per TO | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172060 | ERIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | 3914582 | 100% | 3914582 | 42 | 0.06574 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 1308212.2455 | 24.12% | 9932652 |  | 0.03317
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 172050 | NRIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Contingent | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | 0 | 0% | 21600000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 172052 | NRIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 40710000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 172053 | NRIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | 0 | 0% | 9867000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 172054 | NRIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | 0 | 0% | 12006000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502412 | ERIS | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 8836000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502415 | ERIS | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 6112000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502409 | NRIS | Duncan - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502415 | NRIS | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 81256000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502412 | NRIS | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 502409 | ERIS | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 35100000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 170578 | NRIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 8970000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 CF | 04 SOUTHEAST | 172060 | NRIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | 0 | 0% | 2139000 |  | N/A
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172049 | ERIS | Comanche 345 kV New Substation | Current Study | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 33235024 | 100% | 33235024 |  | 0.33634 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172050 | ERIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | Current Study | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | 73656247 | 100% | 73656247 |  | 0.37149 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172051 | ERIS | Comanche Tap-New Comanche 345 kV Ckt 1 New Line | Current Study | Build a 4 mile 345 kV Ckt 1 from Comanche Tap to the Comanche 345 kV New Substation | 29627840 | 100% | 29627840 | 48 | 0.0772 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172052 | ERIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 16376220.91 | 52.31% | 31306100 |  | 0.04901 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172053 | ERIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | 15826535.47 | 100% | 9867000 | 42 | 0.11475 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172054 | ERIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | 4300398.04 | 100% | 4300398.04 |  | 0.10602 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172055 | ERIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 3772435.56 | 52.31% | 7211691 | 42 | 0.04901 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 1229331.05 | 15.1% | 8143803 | 48 | 0.02983 |  | Evergy
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 170761 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | 14657924 | 100% | 14657924 | 36 | 1 |  | AEP
ERAS-2025-024 | ERAS-2025-001 | 04 SOUTHEAST | 170760 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | 3914582 | 100% | 3914582 | 36 | 1 |  | AEP
ERAS-2025-025 | ERAS-2025-001 | 04 SOUTHEAST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 16.43% | 9932652 |  | 0.09603
ERAS-2025-025 | ERAS-2025-001 | 04 SOUTHEAST | 170801 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | 17000000 | 100% | 17000000 | 60 | 1 |  | WFEC
ERAS-2025-025 | ERAS-2025-001 | 04 SOUTHEAST | 170800 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | 2000018 | 100% | 2000018 | 60 | 1 |  | WFEC
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 23.04% | 9932652 |  | 0.03168
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 172049 | NRIS | Comanche 345 kV New Substation | Contingent | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | 0 | 0% | 16200000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 172052 | NRIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 40710000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502412 | ERIS | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 8836000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502415 | ERIS | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 6112000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502409 | NRIS | Duncan - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502415 | NRIS | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | Contingent | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | 0 | 0% | 81256000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502412 | NRIS | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | Contingent | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 81256000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 502409 | ERIS | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild | Contingent | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | 0 | 0% | 35100000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | 170578 | NRIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Contingent | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 0 | 0% | 8970000 |  | N/A
ERAS-2025-026 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 172052 | ERIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | 14929879.09 | 47.69% | 31603100 |  | 0.04469 |  | AEP
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 172055 | ERIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | Current Study | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | 3439255.44 | 47.69% | 7211691 | 42 | 0.04469 |  | AEP
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 172059 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | Current Study | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | 1227270.49 | 15.07% | 8143803 | 48 | 0.02978 |  | Evergy
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 170793 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | 24836452 | 100% | 24836452 | 42 | 1 |  | AEP
ERAS-2025-026 | ERAS-2025-001 | 05 SOUTHWEST | 170792 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | 5314811 | 100% | 5314811 | 42 | 1 |  | AEP
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 2108691.307 | 11.13% | 18952333 | 48 | 0.22138 |  | AEP
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 31774314.8534 | 11.13% | 285578735 | 48 | 0.22138 |  | AEP
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 3.226% | 9932652 |  | 0.0132
ERAS-2025-027 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-027 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 8.204% | 1366342009.8205 |  | 0.10515
ERAS-2025-027 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 12.1% | 224939250 |  | 0.11655
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 114203.74 | 11.05% | 1033518 | 24 | 0.05687 |  | AEP
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 4812450.25 | 11.05% | 43551586 | 48 | 0.05687 |  | AEP
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 170781 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | 14182594 | 100% | 14182594 |  | 1 |  | SPS
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 170780 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | 4947579 | 100% | 4947579 |  | 1 |  | SPS
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172042 | ERIS | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade | Current Study | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to MUSTANG 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | 511920 | 100% | 511920 | 36 | 0.30607 |  | SPS
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172043 | ERIS | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade | Current Study | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to XTO_MAHONEY 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | 318721 | 100% | 318721 | 36 | 0.30607 |  | SPS
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172044 | ERIS | BRU SUB to XTO MAHONEY 230 kV Line Rebuild | Current Study | Rebuild 1.76 miles BRU_SUB to XTO_MAHONEY 230 kV line to a minimum of 680 MVA | 4497794 | 100% | 4497794 | 40 | 0.69393 |  | SPS
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172066 | ERIS | YOAKUM to BRU SUB 230 kV Line Rebuild | Current Study | Rebuild 5.35 miles YOAKUM to BRU_SUB 230 kV line to a minimum of 665 MVA | 9319312 | 100% | 9319312 | 40 | 0.69393 |  | SPS
ERAS-2025-027 | ERAS-2025-001 | 05 SOUTHWEST | 172067 | ERIS | YOAKUM to MUSTANG 230 kV Line Rebuild | Current Study | Rebuild 15.65 miles YOAKUM to MUSTANG 230 kV line to a minimum of 620 MVA | 18475361 | 100% | 18475361 | 40 | 0.15548 |  | SPS
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 3547072.911 | 18.72% | 18952333 | 48 | 0.24244 |  | AEP
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 53448226.9208 | 18.72% | 285578735 | 48 | 0.24244 |  | AEP
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 5.3% | 9932652 |  | 0.01412
ERAS-2025-028 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-028 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 3.255% | 1366342009.8205 |  | 0.02716
ERAS-2025-028 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 15.22% | 224939250 |  | 0.09543
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 172287.45 | 16.67% | 1033518 | 24 | 0.05586 |  | AEP
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 7260049.39 | 16.67% | 43551586 | 48 | 0.05586 |  | AEP
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 170799 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | 1902616 | 100% | 1902616 | 42 | 1 |  | SPS
ERAS-2025-028 | ERAS-2025-001 | 05 SOUTHWEST | 170798 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | 4621467 | 100% | 4621467 | 42 | 1 |  | SPS
ERAS-2025-029 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 904767.5 | 3.44% | 26301311 | 40 | 0.03635 |  | SEPC
ERAS-2025-029 | ERAS-2025-001 | 03 CENTRAL | 170812 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (Non-shared NU) (KBPU) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | 3159667 | 100% | 3159667 | 31 | 1 |  | KACY
ERAS-2025-029 | ERAS-2025-001 | 03 CENTRAL | 170811 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (TOIF) (KBPU) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | 450000 | 100% | 450000 | 24 | 1 |  | KACY
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 2803345.9263 | 14.79% | 18952333 | 48 | 0.21022 |  | AEP
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 42241553.2382 | 14.79% | 285578735 | 48 | 0.21022 |  | AEP
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 82115 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | 0 | 4.349% | 9932652 |  | 0.01271
ERAS-2025-030 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-030 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 21.94% | 1366342009.8205 |  | 0.20086
ERAS-2025-030 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 18.74% | 224939250 |  | 0.12893
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 161228.81 | 15.6% | 1033518 | 24 | 0.05734 |  | AEP
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 6794047.42 | 15.6% | 43551586 | 48 | 0.05734 |  | AEP
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 170765 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (NSNU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | 30977228 | 100% | 30977228 | 42 | 1 |  | SPS
ERAS-2025-030 | ERAS-2025-001 | 05 SOUTHWEST | 170764 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | 5100814 | 100% | 5100814 | 42 | 1 |  | SPS
ERAS-2025-031 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 798324.26 | 3.035% | 26301311 | 40 | 0.03635 |  | SEPC
ERAS-2025-031 | ERAS-2025-001 | 03 CENTRAL | 170814 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (Non-shared NU) (KBPU) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | 2548040 | 100% | 2548040 | 31 | 1 |  | KACY
ERAS-2025-031 | ERAS-2025-001 | 03 CENTRAL | 170813 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (TOIF) (KBPU) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | 720844 | 100% | 720844 | 24 | 1 |  | KACY
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 170805 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (Non-shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | 683308 | 100% | 683308 | 40 | 1 |  | SEPC
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 170804 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | 3848749 | 100% | 3848749 | 40 | 1 |  | SEPC
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 157186 | NRIS | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Contingent | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 0 | 65.23% | 593064 |  | 0.04858
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 9.129% | 3907935 |  | 0.01692
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 730241.59 | 2.776% | 26301311 | 40 | 0.03325 |  | SEPC
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 247164.42 | 1.821% | 13571142 | 48 | 0.01013 |  | Evergy
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 172062 | NRIS | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1 | Current Study | Replace the existing SEWRDMW3 to SEWARD 2 115-69 kV transformer 1 with a minimum rating of 55 MVA | 4230736.7041 | 65.22% | 6486381.72 | 30 | 0.09051 | Updated per TO | MIDW
ERAS-2025-032 | ERAS-2025-001 | 03 CENTRAL | 172061 | NRIS | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1 | Current Study | Rebuild the existing SEWARD 3 to ST-JOHN3 115 kV line 1 (14.69 miles) to a minimum rating of 115 MVA | 9581359.7257 | 65.22% | 14690000 |  | 0.43237 |  | SEPC
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 159449 | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | Contingent | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | 0 | 5.919% | 3907935 |  | 0.01097
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 264806.91 | 1.949% | 13571142 | 48 | 0.01084 |  | Evergy
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 170757 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (Non-shared NU) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | 0 | 100% | 0 | n/a | 1 | zero per TO | SEPC
ERAS-2025-033 | ERAS-2025-001 | 03 CENTRAL | 170756 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (TOIF) (SEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | 0 | 100% | 0 | n/a | 1 | zero per TO | SEPC
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 172045 | NRIS | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | Current Study | Build a new CARTHAG5 to CARTHG 2 161-69 kV transformer 3 with a rating of 84 MVA | 6099973.09 | 100% | 6099973.09 |  | 0.01479 |  | SWPA
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 172046 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | Current Study | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | 1308212.25 | 4.974% | 26301311 | 40 | 0.03574 |  | SEPC
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 172063 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | Current Study | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | 298734.76 | 2.199% | 13571142 | 48 | 0.00734 |  | Evergy
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 170777 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/thermal), into State Line 439 161 kV Substation | 25701384 | 100% | 25701384 | 54 | 1 |  | EDE
ERAS-2025-034 | ERAS-2025-001 | 03 CENTRAL | 170776 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/Thermal), into State Line 439 161 kV Substation | 1357898 | 100% | 1357898 | 54 | 1 |  | EDE
ERAS-2025-035 | ERAS-2025-001 | 01 NORTH | 170789 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (Non-shared NU) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 9856000 | 100% | 9856000 |  | 1 |  | NWE
ERAS-2025-035 | ERAS-2025-001 | 01 NORTH | 170788 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (TOIF) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 1451000 | 100% | 1451000 |  | 1 |  | NWE
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 172047 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | Current Study | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 898052.1742 | 4.738% | 18952333 | 48 | 0.16836 |  | AEP
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 172048 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | Current Study | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | 13532086.2015 | 4.738% | 285578735 | 48 | 0.16836 |  | AEP
ERAS-2025-036 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-036 | ERAS-2025-001 CF | 05 SOUTHWEST | 172047 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | Contingent | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | 0 | 0% | 18952333 | 48 | N/A
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | TBD | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 4.302% | 1366342009.8205 |  | 0.09847
ERAS-2025-036 | ERAS-2025-001 CF | 05 SOUTHWEST | TBD | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | Contingent | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | 0 | 0% | 1366342009.8205 |  | N/A
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 170066, 170093 | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | Contingent | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 8.455% | 224939250 |  | 0.14539
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 172056 | ERIS | ELKCITY 230/138 kV Transformer Replacement | Current Study | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | 67798.78 | 6.559% | 1033518 | 24 | 0.06028 |  | AEP
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 172057 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | Current Study | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | 2856984.04 | 6.559% | 43551586 | 48 | 0.06028 |  | AEP
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 170755 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | 25619705 | 100% | 25619705 | 42 | 1 |  | SPS
ERAS-2025-036 | ERAS-2025-001 | 05 SOUTHWEST | 170754 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | 4222767 | 100% | 4222767 | 42 | 1 |  | SPS
Total | [7 empty] | 1230667490.93 |  | 35381504437.249

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Replacement of two disconnect switches at Antelope Valley Station | TBD | Replace two disconnect switches at Antelope Valley Station for the Antelope Valley Station – Leland Old 345 kV Ckt 1 | BEPC | TBD (36-month lead time) | 250000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | LACYGNE7-G20-007-TAP 345 kV Ckt 1 Rebuild | TBD | Rebuild the existing LACYGNE to G20-007 TAP 345 kV Ckt 1 (0.6 miles) to a minimum normal rating of 1210 MVA | KCPL | TBD (36-month lead time) | 1320000
Contingent | ERAS-2025-001 | Steady State | 03 CENTRAL | 2024 ITP | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 169968 | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | SUNC | 4784800% | 1050598691
Model Correction | ERAS-2025-001 | Steady State | 03 CENTRAL | 2021 ITP | ERIS | Joplin West 7th - Stateline 161 kV Line (Model Correction) | 92143 | Rebuild approximately 5.5 miles of the existing 161 kV line from Joplin West 7th to Stateline to 558 MVA. | EMDE | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | TBD | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | AEPW | TBD (36-month lead time) | 21600000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 345 kV New Substation | TBD | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | AEPW | TBD (36-month lead time) | 16200000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche Tap-New Comanche 345 kV Ckt 1 New Line | TBD | Build a 4 mile 345 kV Ckt 1 from Comanche Tap to the Comanche 345 kV New Substation | AEPW | TBD (36-month lead time) | 15600000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | AEPW | TBD (36-month lead time) | 12006000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | AEPW | TBD (36-month lead time) | 9867000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | AEPW | TBD (36-month lead time) | 2139000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36-month lead time) | 8970000
Current Study | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36-month lead time) | 40710000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | 500030 | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 9044000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | 500003 | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 6178000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Multi - Horseshoe Lake Reconfiguration | 900189 | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | OKGE | TBD (36-month lead time) | 61120000
Model Correction | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | ERAS-2025-004 and ERAS-2025-010 Model Correction | N/A | Turn on the auxillary loads at ERAS-2025-004 and ERAS-2025-010 | OKGE | N/A | 0
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Dunjee-Reno 138 kV Ckt 1 Rebuild | 500030 | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 9044000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Trosper-Reno 138 kV Ckt 1 Rebuild | 500003 | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | OKGE | TBD (36-month lead time) | 6178000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Multi - Horseshoe Lake Reconfiguration | 900189 | Convert the existing Kelly Ave. - Remington Ckt 1 line from 69 kV to 138 kV Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Convert the existing Stonewall - Remington Ckt 1 line from 69 kV to 138 kV Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Convert the existing Remington - Green Pastures Ckt 1 line to 138 kV Convert the existing Horseshoe Lake - Green Pastures Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation Construct new Farrier 138 kV Substation across lake from exisiting HSL 138 kV station New Farrier - Green Pastures 138kV Termination New Farrier - Hamm Tap 138kV Termination New Farrier - Dale 138kV Termination New Farrier - ERAS Units 4-1 & 4-2 (15.1 & 15.2) Termination New Line Midway - Farrier 138 kV Line New Line Horseshoe Lake - Farrier 138 kV Double-Circuit Line | OKGE | TBD (36-month lead time) | 61120000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Duncan-4-DuncherTap4 138 kV Ckt 1 Rebuild | 502409 | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | AEPW | TBD (36-month lead time) | 35100000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | D.E.S-4-DuncherTap4 138 kV Ckt 1 Rebuild | 502412 | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | AEPW | TBD (36-month lead time) | 8836000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | D.E.S-4-Omdune-4 138 kV Ckt 1 Rebuild | 502415 | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | AEPW | TBD (36-month lead time) | 6112000
Contingent | ERAS-2025-001 | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | TBD | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | SPS | TBD (36-month lead time) | 1366342009.8205
Contingent | ERAS-2025-001 | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Potter to Beckham 345 kV Line (2024 ITP) | 170066, 170093 | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA | OKGE/SPS | TBD (36-month lead time) | 224939250
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | COMANC7 TAP to LES 345 kV Line Rebuild | TBD | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | AEPW | TBD (36-month lead time) | 6031219.88
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | COMANC7 TAP to OKU 345 kV Line Rebuild | TBD | Rebuild 61.53 miles COMANC7_TAP to OKU 345 kV line to a minimum of 1390 MVA | AEPW | TBD (36-month lead time) | 70417639.32
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | ELKCITY 230/138 kV Transformer Replacement | TBD | Replace ELKCITY 230/138 kV Transfomer to a minimum of 450 MVA | AEPW | TBD (36-month lead time) | 6621188
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | ELKCITY6 to CHISHOLM6 230 kV Line Rebuild | TBD | Rebuild 18.75 miles ELKCITY6 to CHISHOLM6 230 kV line to a minimum of 480 MVA | AEPW | TBD (36-month lead time) | 16565793.75
Model Correction | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | MCDWL_CREEK6 to POTTER_CO 230 kV Line (Model Correction) | TBD | Correct the Mcdowel Creek to Potter County 230 kV Line rating to SN/SE 497.2/547 MVA. | SPS | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tolk 345/230 kV CKT 1 Transformer Replacement | TBD | Replace Tolk 345/230 kV CKT 1 Transformer to 748 MVA | SPS | TBD (36-month lead time) | 8302968
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | AMOCOWASSON6 to XTO MAHONEY 230 kV Line Terminal Upgrade | TBD | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to XTO_MAHONEY 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | SPS | TBD (36-month lead time) | 4081811.58
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | AMOCOWASSON6 to MUSTANG 230 kV Line Terminal Upgrade | TBD | Upgrade terminal equipment at the Amoco Wasson Substation on the AMOCOWASSON6 to MUSTANG 230 kV line to achieve a SN/SE rating of 498/547.8 MVA | SPS | TBD (36-month lead time) | 3136456.95
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | YOAKUM to BRU SUB 230 kV Line Rebuild | TBD | Rebuild 5.35 miles YOAKUM to BRU_SUB 230 kV line to a minimum of 665 MVA | SPS | TBD (36-month lead time) | 4726773.15
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | YOAKUM to MUSTANG 230 kV Line Rebuild | TBD | Rebuild 15.65 miles YOAKUM to MUSTANG 230 kV line to a minimum of 620 MVA | SPS | TBD (36-month lead time) | 13826915.85
Current Study | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | BRU SUB to XTO MAHONEY 230 kV Line Rebuild | TBD | Rebuild 1.76 miles BRU_SUB to XTO_MAHONEY 230 kV line to a minimum of 680 MVA | SPS | TBD (36-month lead time) | 1554975.84
Contingent | ERAS-2025-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Andrews to Road Runner 345 kV Line | 170597 | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | SPS | TBD (36-month lead time) | 73524573
Current Study | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Kummer Ridge 345 kV Capacitor Bank | TBD | Install 300 MVAR Capacitor Bank at Kummer Ridge 345 kV substation | BEPC | TBD (60-month lead time) | 20000000
Model Correction | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Antelope Valley Station – Leland Old 345 kV Ckt 1 and Ckt 2 Model Correction | TBD | Correct the Antelope Valley Station – Leland Old 345 kV Ckt 1 and Ckt 2 Summer Ratings to 1127 (summer normal)/1195 (summer emergency) and Winter Ratings to 1195 (winter normal)/1195 (winter emergency) | BEPC | N/A | 0
Model Correction | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | NRIS | Roadrunner 345/115 kV transformer #2 Model Correction | TBD | Model correction on the Roadrunner 345/115 kV transformer #2 | SPS | N/A | 0
Model Correction | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | NRIS | Roadrunner 345/115 kV transformer #3 Model Correction | TBD | Model correction on the Roadrunner 345/115 kV transformer #3 | SPS | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Build the CARTHAG5 to CARTHG 2 161kV Transformer 3 | TBD | Build a new CARTHAG5 to CARTHG 2 161-69 kV transformer 3 with a rating of 84 MVA | SWPA | TBD (36-month lead time) | 6075000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Build the HOLCOMB7 to HOLCOMB3 345kV Transformer 2 | TBD | Build a new HOLCOMB7 to HOLCOMB3 345-115 kV transformer 2 with a rating of 336 MVA | SUNC | TBD (36-month lead time) | 15000000
Contingent | ERAS-2025-001 | Steady State | 04 SOUTHEAST/05 SOUTHWEST | DPA-2017-December-815 | NRIS | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | 82115 | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | WFEC | 4644600% | 9932652
Model Correction | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | S.W.S.-4 to NORGE--4 138kV Line 1 Rating Update | TBD | Update the existing S.W.S.-4 to NORGE--4 138 kV line 1 (22.35 miles) to a rating of 366 MVA | AEPW | N/A | 0
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Replace the SIBLEY 7 to SIBLEY 5 345kV Transformer 1 | TBD | Replace the existing SIBLEY 7 to SIBLEY 5 345-161 kV transformer 1 with a minimum rating of 510 MVA | N/A | TBD (36-month lead time) | 12200000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Replace the SEWRDMW3 to SEWARD 2 115kV Transformer 1 | TBD | Replace the existing SEWRDMW3 to SEWARD 2 115-69 kV transformer 1 with a minimum rating of 55 MVA | MIDW | TBD (36-month lead time) | 6000000
Current Study | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | Rebuild the SEWARD 3 to ST-JOHN3 115kV Line 1 | TBD | Rebuild the existing SEWARD 3 to ST-JOHN3 115 kV line 1 (14.69 miles) to a minimum rating of 115 MVA | SUNC | TBD (36-month lead time) | 14690000
Model Correction | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | NRIS | SEWRDMW3 to SEWARD 3 115kV Line 1 Rating Update | TBD | Update the existing SEWRDMW3 to SEWARD 3 115 kV line 1 (2.91 miles) to a rating of 60 MVA | MIDW | N/A | 0
Contingent | ERAS-2025-001 | Steady State | 03 CENTRAL | 2024 ITP | NRIS | Evans Energy Center North - Maize 138 kV Ckt 1 Rebuild | 159449 | Rebuild 4.9-mile Ckt 1 line from Evans Energy Center North 138 kV substation to Maize 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 478 MVA. | EKC | 4711800% | 3907935
Contingent | ERAS-2025-001 | Steady State | 03 CENTRAL | 2023 ITP | NRIS | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | 157186 | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | SEPC | 4656800% | 593064
Contingent | ERAS-2025-001 | Steady State | 01 NORTH | 2022 ITP | NRIS | Fargo 230 kV Terminal Upgrade | 156282 | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | WAPA | 2025-12-31 (Delayed) | 243120
Model Correction | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | NRIS | ANTELOPE-BE3 to CHARL_CK-BE3 345kV Line 1 Rating Update | TBD | Update the existing ANTELOPE-BE3 to CHARL_CK-BE3 345 kV line 1 (69.9 miles) to a rating of 1195 MVA | BEPC-SPP | N/A | 0
Interconnection | ERAS-2025-001 | Steady State | 02 NEBRASKA | ERAS-2025-001 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (Non-shared NU) (LES) | 170753 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | LES | 36 | 0
Interconnection | ERAS-2025-001 | Steady State | 02 NEBRASKA | ERAS-2025-001 | ERIS | 84th & Bluff 115 kV Substation ERAS-2025-001 Interconnection (TOIF) (LES) | 170752 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-001 (104MW/Thermal), into 84th & Bluff 115 kV Substation | LES | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (Non-shared NU) (SPS) | 170803 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | SPS | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Xcel Tuco 345kV Substation ERAS-2025-002 Interconnection (TOIF) (SPS) | 170802 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-002 (217MW/Thermal), into Xcel Tuco 345kV Substation | SPS | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (Non-shared NU) (OGE) | 170795 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | OKGE | 6 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Redbud 345kV Substation ERAS-2025-003 Interconnection (TOIF) (OGE) | 170794 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-003 (186MW/Thermal), into Redbud 345kV Substation | OKGE | 6 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004 Interconnection (TOIF) (OGE) | 170774 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004 (779MW/Thermal), into Horseshoe Lake 138kV Substation | OKGE | 24 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-004/ERAS-2025-010 Interconnection (Shared NU) (OGE) | 170807 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-004/ERAS-2025-010 (779/496MW/Thermal/Thermal), into Horseshoe Lake 138kV Substation | OKGE | 24 | 0
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (Non-shared NU) (AEP) | 170763 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | AEPW | 36 | 15452461
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Danville - Magazine 161 kV Line ERAS-2025-005 Interconnection (TOIF) (AEP) | 170762 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-005 (150MW/Hybrid), into Danville - Magazine 161 kV Line | AEPW | 36 | 3790119
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007 Interconnection (TOIF) (Evergy) | 170809 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | Evergy | 48 | 2122145
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-013 Interconnection (TOIF) (Evergy) | 170810 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-013 (450.6MW/Thermal), into Mullin Creek 345 kV Substation | Evergy | 36 | 1765342
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (TOIF) (Evergy) | 170815 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | Evergy | 24 | 2118099
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Reno County 345 kV Substation #1443 ERAS-2025-006 Interconnection (Non-shared NU) (Evergy) | 170816 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-006 (717.8MW/Thermal), into Reno County 345 kV Substation #1443 | Evergy | 24 | 9918207
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (TOIF) (Evergy) | 170817 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | Evergy | 12 | 737202
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Viola 345 kV Substation ERAS-2025-008 Interconnection (Non-shared NU) (Evergy) | 170818 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-008 (360.55MW/Thermal), into Viola 345 kV Substation | Evergy | 12 | 6901474
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (Non-shared NU) (GRDA) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 170767 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | GRDA | TBD (36-month lead time) | TBD
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Grec #1 Interconnect 161 kV Substation ERAS-2025-009 Interconnection (TOIF) (GRDA) | 170766 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-009 (450MW/Thermal), into Grec #1 Interconnect 161 kV Substation | GRDA |  | 2953500
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Horseshoe Lake 138kV Substation ERAS-2025-010 Interconnection (TOIF) (OGE) | 170775 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-010 (496MW/Thermal), into Horseshoe Lake 138kV Substation | OKGE | 24 | 0
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (TOIF) (BEPC) | 170778 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011 (750MW/Thermal), into Leland Olds 345kV Switchyard | BEPC | 60 | 2927868
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (Non-Shared NU) (BEPC) | 170821 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | BEPC | 60 | 17000000
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-011 Interconnection (Non-Shared NU) (BEPC) | 170808 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-011/ (750MW/Thermal), into Leland Olds 345kV Switchyard | BEPC | 60 | 11450012
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Leland Olds 345kV Substation ERAS-2025-012 Interconnection (TOIF) (BEPC) | 170779 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-012 (750MW/Thermal), into Leland Olds 345kV Substation | BEPC | 60 | 13000000
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Mullin Creek 345 kV Substation ERAS-2025-007/013 Interconnection (Shared NU) (Evergy) | 170819 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-007/013 (450.6/450.6MW/Thermal/Thermal), into Mullin Creek 345 kV Substation | Evergy | 48 | 21894774
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (Non-shared NU) (SPS) | 170769 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | SPS | 18 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs-Andrews 345kV Line ERAS-2025-014 Interconnection (TOIF) (SPS) | 170768 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-014 (159.5MW/Thermal), into Hobbs-Andrews 345kV Line | SPS | 18 | 0
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Holcomb 345 kV Substation ERAS-2025-015 Interconnection (TOIF) (SEPC) | 170772 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015 (400MW/Hybrid), into Holcomb 345 kV Substation | SEPC | 60 | 5238900
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Holcomb 345 kV Substation ERAS-2025-015/ERAS-2025-017 Interconnection (Shared NU) (SEPC) | 170806 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-015/ERAS-2025-017 (400/600MW/Hybrid/Thermal), into Holcomb 345 kV Substation | SEPC | 60 | 38522200
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (Non-shared NU) (SPS) | 170797 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | SPS | 40 | 2030268
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tolk 230kV Substation ERAS-2025-016 Interconnection (TOIF) (SPS) | 170796 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-016 (232.5MW/Thermal), into Tolk 230kV Substation | SPS | 40 | 3809606
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Holcomb 345 kV Substation ERAS-2025-017 Interconnection (TOIF) (SEPC) | 170773 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-017 (600MW/Thermal), into Holcomb 345 kV Substation | SEPC | 60 | 5238900
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (Non-shared NU) (SPS) | 170791 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | SPS | 60 | 17180394
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Oasis 230kV Substation ERAS-2025-018 Interconnection (TOIF) (SPS) | 170790 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-018 (256MW/Hybrid), into Oasis 230kV Substation | SPS | 60 | 3113165
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (Non-shared NU) (MIDW) | 170785 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | MIDW | 30 | 6595300
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | North Kinsley 115kV Substation ERAS-2025-019 Interconnection (TOIF) (MIDW) | 170784 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-019 (80MW/Solar), into North Kinsley 115kV Substation | MIDW | 30 | 1035871
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (Non-shared NU) (SPS) | 170771 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | SPS | 60 | 32764203
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Hobbs - Yoakum 345 kV Line ERAS-2025-020 Interconnection (TOIF) (SPS) | 170770 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-020 (400MW/Hybrid), into Hobbs - Yoakum 345 kV Line | SPS | 60 | 3793557
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (Non-shared NU) (SPS) | 170759 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | SPS | 60 | 28993147
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Border-Tuco 345 kV Line ERAS-2025-021 Interconnection (TOIF) (SPS) | 170758 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-021 (500MW/Wind), into Border-Tuco 345 kV Line | SPS | 60 | 3817643
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (Non-shared NU) (PEC) | 170783 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | PEC | 52 | 1165190
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Monte Vista 138 kV Substation ERAS-2025-022 Interconnection (TOIF) (PEC) | 170782 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-022 (123MW/Battery/Storage), into Monte Vista 138 kV Substation | PEC | 52 | 2573308
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (Non-shared NU) (AEP) | 170787 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | AEPW | 36 | 3862241
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Northeastern 345 kV Substation ERAS-2025-023 Interconnection (TOIF) (AEP) | 170786 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-023 (510MW/Thermal), into Northeastern 345 kV Substation | AEPW | 36 | 5406476
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (Non-shared NU) (AEP) | 170761 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | AEPW | 36 | 14804258
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Comanche 138kV Substation ERAS-2025-024 Interconnection (TOIF) (AEP) | 170760 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-024 (744MW/Thermal), into Comanche 138kV Substation | AEPW | 36 | 3827454
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (Non-shared NU) (WFEC) | 170801 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | WFEC | 66 | 17000000
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Washita 138kV Substation ERAS-2025-025 Interconnection (TOIF) (WFEC) | 170800 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-025 (175MW/Solar), into Washita 138kV Substation | WFEC | 66 | 2000018
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (Non-shared NU) (AEP) | 170793 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | AEPW | 42 | 24133953
Interconnection | ERAS-2025-001 | Steady State | 04 SOUTHEAST | ERAS-2025-001 | ERIS | Oklaunion-Lawton East Side 345kV Line ERAS-2025-026 Interconnection (TOIF) (AEP) | 170792 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-026 (744MW/Thermal), into Oklaunion-Lawton East Side 345kV Line | AEPW | 42 | 5236562
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (Non-shared NU) (SPS) | 170781 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | SPS | 30 | 4641893
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Mahoney 230kV Substation ERAS-2025-027 Interconnection (TOIF) (SPS) | 170780 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-027 (250MW/Battery/Storage), into Mahoney 230kV Substation | SPS | 30 | 2743634
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (Non-shared NU) (SPS) | 170799 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | SPS | 60 | 1433543
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Tuco-Yoakum 345kV Line ERAS-2025-028 Interconnection (TOIF) (SPS) | 170798 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-028 (384MW/Solar), into Tuco-Yoakum 345kV Line | SPS | 60 | 2868488
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (Non-shared NU) (KACY) | 170812 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | KACY | 20 | 3159667
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Nearman 161 kV Substation ERAS-2025-029 Interconnection (TOIF) (KACY) | 170811 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-029 (170MW/Battery/Storage), into Nearman 161 kV Substation | KACY | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (NSNU) (SPS) | 170765 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | SPS | 60 | 24611060
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line ERAS-2025-030 (TOIF) (SPS) | 170764 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-030 (350MW/Solar), into G24-279 New Switch Station tying into Chaves - Eddy County 230 kV Line | SPS | 60 | 4055881
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (Non-shared NU) (KC BPU) | 170814 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | KC BPU | 20 | 2548040
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Quindaro 161kV Substation ERAS-2025-031 Interconnection (TOIF) (KC BPU) | 170813 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-031 (150MW/Thermal), into Quindaro 161kV Substation | KC BPU | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (Non-shared NU) (SEPC) | 170805 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | SEPC | 40 | 300000
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | St. John 115 kV Substation ERAS-2025-032 Interconnection (TOIF) (SEPC) | 170804 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-032 (150MW/Hybrid), into St. John 115 kV Substation | SEPC | 40 | 1809896
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (Non-shared NU) (SEPC) | 170757 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | SEPC | 0 | 0
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | Fort Dodge 115 kV Substation ERAS-2025-033 Interconnection (TOIF) (SEPC) | 170756 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-033 (150MW/Battery/Storage), into Fort Dodge 115 kV Substation | SEPC | 40 | 330000
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (Non-shared NU) (EDE) | 170777 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/thermal), into State Line 439 161 kV Substation | EDE | 54 | 28031567.78
Interconnection | ERAS-2025-001 | Steady State | 03 CENTRAL | ERAS-2025-001 | ERIS | State Line 439 161 kV Substation ERAS-2025-034 Interconnection (TOIF) (EDE) | 170776 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-034 (250MW/Thermal), into State Line 439 161 kV Substation | EDE | 54 | 1434591.61
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (Non-shared NU) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 170789 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | NWPS | TBD (36-month lead time) | TBD
Interconnection | ERAS-2025-001 | Steady State | 01 NORTH | ERAS-2025-001 | ERIS | Siebrecht 115 kV Substation ERAS-2025-035 Interconnection (TOIF) (NWPS) * Cost and Lead-Time under review by TO and will be provided during the facility study stage | 170788 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-035 (137.96MW/Thermal), into Siebrecht 115 kV Substation * Cost and Lead-Time under review by TO and will be provided during the facility study stage | NWPS | TBD (36-month lead time) | TBD
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (Non-shared NU) (SPS) | 170755 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | SPS | 48 | 20961370
Interconnection | ERAS-2025-001 | Steady State | 05 SOUTHWEST | ERAS-2025-001 | ERIS | Newhart - Potter 230 kV Line ERAS-2025-036 Interconnection (TOIF) (SPS) | 170754 | Interconnection upgrades and cost estimates needed to interconnect ERAS-2025-036 (140MW/Battery/Storage), into Newhart - Potter 230 kV Line | SPS | 48 | 3550583
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST/05 SOUTHWEST | ERAS-2025-001 | NRIS | COMANC7 TAP to LES 345 kV Line Rebuild | TBD | Rebuild 5.27 miles COMANC7_TAP to LES 345 kV line to a minimum of 1385 MVA | AEPW | TBD (36 month lead time) | 6031219.88
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST/05 SOUTHWEST | ERAS-2025-001 | NRIS | Comanche 345 kV New Substation | TBD | Install 345 kV substation near Comanche along the LES-Terry Road 345 kV Line | AEPW | TBD (36 month lead time) | 16200000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche 345/138 kV Ckt 1 and Ckt 2 Transformers | TBD | Install two new 345/138kV Ckt 1 and Ckt 2 transformers at Comanche | AEPW | TBD (36 month lead time) | 21600000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche Tap-OmDuncan 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche Tap to OmDuncan 138 kV Ckt 1 (17.7 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36 month lead time) | 40710000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Comanche Tap 138 kV Ckt 1 (4.29 miles) to a minimum rating of 340 MVA | AEPW | TBD (36 month lead time) | 9867000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Comanche-Lawton Eastside 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Comanche to Lawton Eastside 138 kV Ckt 1 (5.22 miles) to a minimum rating of 320 MVA | AEPW | TBD (36 month lead time) | 12006000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Duncan - Duncan Tap 138 kV Line Rebuild | 502409 | Rebuild 1.6-mile Ckt 1 line from Duncan 138 kV substation to Duncan Tap 138 kV substation | AEPW | 4616300% | 81256000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Duncan Eastside - Duncan Eastside 138 kV Line Rebuild | 502415 | Rebuild 1.26-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Eastside 138 kV substation | AEPW | 4616300% | 81256000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Duncan Eastside - Duncan Tap 138 kV Line Rebuild | 502412 | Rebuild 3.53-mile Ckt 1 line from Duncan Eastside 138 kV substation to Duncan Tap 138 kV substation | AEPW | 4616300% | 81256000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | DISIS-2020-001 | NRIS | Duncan-OmDuncan 138 kV Ckt 1 Rebuild | 170578 | Rebuild the existing Duncan to OmDuncan 138 kV Ckt 1 (3.9 miles) to a minimum summer rating of 250 MVA | AEPW | TBD (36 month lead time) | 8970000
Contingent | ERAS-2025-001 CF | Steady State | 03 CENTRAL | 2024 ITP | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 169968 | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | SEPC/TSGT/ITC GP | 4784800% | 1050598691
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | ERAS-2025-001 | NRIS | Lawton Eastside-Comanche Tap 138 kV Ckt 1 Rebuild | TBD | Rebuild the existing Lawton Eastside to Comanche Tap 138 kV Ckt 1 (0.93 miles) to a minimum summer rating of 200 MVA | AEPW | TBD (36 month lead time) | 2139000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST/05 SOUTHWEST | 2025 ITP | NRIS | Line - Crawfish Draw - Phantom 765 kV New Line (2025 ITP) | TBD | Tap the existing Oklaunion - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Tap the existing Border - Tuco 345 kV Ckt 1 line at new Crawfish Draw substation Build a 25.1-mile 345 kV Ckt 2 line from Tuco to Crawfish Draw Build a 239.2-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom Install 345 kV substation at Crawfish Draw Install 765 kV substation at Crawfish Draw Install 75 MVAR reactor at Oklaunion 345 kV substation Install 100 MVAR reactor at Border 345 kV substation Install 175 MVAR reactor at Crawfish Draw 345 kV substation Install 375 MVAR reactor at Crawfish Draw 765 kV substation Install 300 MVAR reactor at Phantom 765 kV substation Install new 345/765 Ckt 1 transformer at Crawfish Draw Install new 345/765 Ckt 2 transformer at Crawfish Draw Install new 345/765 Ckt 3 transformer at Crawfish Draw | SPS | 4780500% | 1366342009.8205
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Dunjee - Reno 138 kV Ckt 1 Rebuild | 503211 | Rebuild 7.32-mile Ckt 1 line from Dunjee 138 kV substation to Reno 138 kV substation | OKGE | 4690500% | 16661900
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Multi - Horseshoe Lake Reconfiguration | TBD | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | OKGE | 4727000% | 61120000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Multi - Horseshoe Lake Reconfiguration | TBD | Upgrade terminal equipment for Ckt 1 from Memorial 138 kV substation to Bryant 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Horseshoe Lake 138 kV substation Upgrade terminal equipment for Ckt 1 from Jones Tap 138 kV substation to Acorn 138 kV substation Switch out 138 kV Ckt 1 line from Remington Tap to Remington Convert the existing Remington - NE 30th Ckt 1 line to 138 kV Switch out 69 kV Ckt 1 line from NE 30th to Deep Fork Tap Convert the existing NE 30th - Reno Ckt 1 line from 69 kV to 138 kV Switch out 69 kV Ckt 1 line from Deep Fork Tap to Green Pastures Switch out 69 kV Ckt 1 line from Deep Fork Tap to Deep Fork Switch out Remington Tap 138 substation Convert the 69 kV NE 30th substation to 138 kV Switch out Deep Fork Tap 69 substation Convert the 69 kV Green Pastures substation to 138 kV Switch out Deep Fork 69 substation. | OKGE | 4727000% | 61120000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | NE 10th - Reno 138 kV Line Rebuild | 501015 | Rebuild 4.16-mile Ckt 1 line from NE 10th 138 kV substation to Reno 138 kV substation | OKGE | 4727000% | 8392000
Contingent | ERAS-2025-001 CF | Steady State | 04 SOUTHEAST | 2025 ITP | NRIS | Trosper - Reno 138 kV Line Rebuild | 500003 | Rebuild 2.62-mile Ckt 1 line from Trosper 138 kV substation to Reno 138 kV substation | OKGE | 4727000% | 6178000
6649063889.231