# Provisional Load PRocess Study

# PLP-2026-March-0017-H Quindaro

By SPP Engineering, Transmission Services

Published on 7/31/2026

Version 1

# Revision History

| Date or version number | Author | Change Description | Comments |
| --- | --- | --- | --- |
| 7/15/2026 | SPP/EPE | Original |  |
| 7/31/2026 | SPP/EPE | Updated Table 3-4 | Included the conceptual cost for the Nearman – Quindaro 161kV line. |

Contents

Revision History	i

Section 1: INtroduction	1

Section 2: Study Methodology	2

Objective	2

Study Process	2

Section 3: Results of analysis	6

Potential Thermal and Voltage Violations	6

Short Circuit	7

Stability	9

EMT Screening	10

Transmission Solutions	10

Section 4: Conclusion	13

Appendix	14

Appendix A	14

Appendix B	14

Appendix C	14

Appendix D	14

# Section 1: INtroduction

This report outlines the results of an evaluation of regional transmission impacts from delivery point request PLP-2026-March-0017. The requesting entity plans to add load to a new delivery point called Quindaro with an in-service date of 7/1/2027. The Quindaro delivery point is in the Kansas City Board of Public Utilities (KCBPU) Transmission System.

The load flow models used for the evaluation were 2026 Integrated Transmission Planning (ITP) base reliability models. Southwest Power Pool (SPP) performed an Alternating Current (AC) contingency analysis on these models using TARA.

# Section 2: Study Methodology

## Objective

The purpose of this study was to determine the regional transmission system impacts within the SPP footprint associated with the addition of the new load at the Quindaro delivery point. The study modeled an initial 300 MW load, consisting of three 99.2 MW load additions, behind the Quindaro 161 kV delivery point in the 2027, 2028, 2030, and 2035 model years. The load was interconnected at the proposed 161 kV Substation Quindaro station (Bus #546652).

The new delivery point and associated facilities are intended to support a phased data center development near Kansas City.

To accommodate the proposed Quindaro load addition, additional generation resources were added in the surrounding area to support system performance and reliability. The details regarding the generation additions are provided in the following section.

## Study Process

- Model Assumptions

  - 2026 ITP Base Reliability Model Series

    - Model years 2027, 2028, 2030, and 2035

    - Summer Peak (2027S, 2028S, 2030S, and 2035S), Winter Peak (2027W, 2028W, 2030W, and 2035W), and Summer Shoulder (2030H)

  - 2026 ITP Short Circuit Model Series

    - 2030 Summer Max Fault

  - 2026 Transmission System Planning (TPL) Dynamic Model Series

    - 2030 Summer Peak Base and Change Cases

  - Planned Generation

    - Ninnescah Flats Solar – 96.4 MW

    - Ninnescah Flats BESS – 96.4 MW

    - Nearman BESS – 170 MW

Table 2-1. Study Cases

| Case Name | Study Year | Season | Scenario | Load (MW/MVAR) |
| --- | --- | --- | --- | --- |
| 2026ITPFinal-27S.sav | 2027 | Summer Peak | Base Reliability | Base Case |
| 2026ITPFinal-27W.sav | 2027 | Winter Peak | Base Reliability | Base Case |
| 2026ITPFinal-28S.sav | 2028 | Summer Peak | Base Reliability | Base Case |
| 2026ITPFinal-28W.sav | 2028 | Winter Peak | Base Reliability | Base Case |
| 2026ITPFinal-30S.sav | 2030 | Summer Peak | Base Reliability | Base Case |
| 2026ITPFinal-30W.sav | 2030 | Winter Peak | Base Reliability | Base Case |
| 2026ITPFinal-30H.sav | 2030 | Summer Shoulder | Base Reliability | Base Case |
| 2026ITPFinal-35S.sav | 2035 | Summer Peak | Base Reliability | Base Case |
| 2026ITPFinal-35W.sav | 2035 | Winter Peak | Base Reliability | Base Case |
| 2026ITPFinal-27S_Study.sav | 2027 | Summer Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-27W_Study.sav | 2027 | Winter Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-28S_Study.sav | 2028 | Summer Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-28W_Study.sav | 2028 | Winter Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-30S_Study.sav | 2030 | Summer Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-30W_Study.sav | 2030 | Winter Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-30H_Study.sav | 2030 | Summer Shoulder | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-35S_Study.sav | 2035 | Summer Peak | Base Reliability | Quindaro = 300/63.26 |
| 2026ITPFinal-35W_Study.sav | 2035 | Winter Peak | Base Reliability | Quindaro = 300/63.26 |

- Steady State Analysis

  - Assumptions (consistent with the ITP analysis)

    - AC contingency analysis on all load flow models using PSS®E and TARA

    - Monitored Elements

      - SPP facilities 69 kV and above

      - First-tier companies 100 kV and above

    - Contingencies (consistent with the ITP analysis)

      - Provided for the ITP by SPP members and first-tier companies

      - Autogenerated contingencies capturing P1s that were missed in the SPP members provided contingencies.

    - Apply SPP Criteria and National American Electric Reliability Corporation (NERC) reliability standards

  - The study focused only on violations caused by the addition of the proposed Quindaro load. The study case results were compared against the corresponding base cases and any violations that already existed in the base cases were excluded from the analysis. Only the new violations created by the proposed load addition were considered in the evaluation and development of mitigation upgrades.

- Short Circuit Analysis

  - Assumptions

    - Used 2026 Final ITP Short Circuit models (Max Fault)

      - Placed all available facilities in service

        - Generation

        - Transmission lines

        - Transformers

        - Buses

      - Short Circuit Output

        - Physical

      - Short Circuit Coordinates

        - Polar

      - Short Circuit Parameters

        - 3 Phase

      - FLAT – classical fault analysis conditions

  - Analyses

    - Three-phase fault

- Dynamics Analysis

  - Assumptions

    - The 2026 Series TPL 2030 Summer Peak Model was modified to include the 300 MW load at the proposed 161 kV Quindaro station (Bus #546652).

    - The dynamic model for the 300 MW load was added as detailed in Appendix A.

    - The following generators and their associated dynamic models were added to the 2030 Summer Peak Model:

        - Ninnescah Flats Solar I

        - Ninnescah Flats Solar II

        - Ninnescah BESS

  - Dynamic Stability analysis was performed using PSS®E.

    - Monitored Elements

      - The active power (PELEC), reactive power (QELEC), and terminal voltage (ETERM) of all conventional and renewable generation interconnecting within 5 levels of POI. The machine rotor angle of conventional generators was also monitored.

      - The voltage and frequency of all transmission buses 69 kV and above within the study area were monitored.

      - The active and reactive power of the 300 MW load at Quindaro was monitored.

    - 2030 Summer Peak Model - Dispatch

      - To balance the swing after adding the study load, following generators were switched on and/or dispatched up:

        - Ninnescah Flats Solar I

        - Ninnescah Flats Solar II

        - Ninnescah BESS

        - Nearman BESS

    - Fault Definitions

      - EPE developed and simulated a revised set of fault events for PLP-2026-March-0017 using modified study models. The updated fault set was executed to assess system performance under the revised modelling assumptions.

      - The fault models included both three-phase faults and single-line-to-ground (SLG) stuck breaker faults. SLG faults were represented using an equivalent fault impedance approach, adjusted such that the faulted bus positive-sequence voltage is reduced to approximately 0.6 pu.

      - In addition, P3 contingency events were constructed by combining the tripping of a generating unit within the study area followed by the outage of a transmission element within three voltage levels of the Point of Interconnection (POI). The following generating units were included in the P3 contingency definition:

        - Ninnescah Flats Solar I

        - Ninnescah Flats Solar II

        - Ninnescah BESS

        - Nearman BESS

      - A separate study load drop contingency was also simulated to evaluate potential frequency excursions and high-voltage conditions resulting from sudden load rejection within the study area.

- A complete list and detailed description of all simulated fault events are provided in Appendix C.

# Section 3: Results of analysis

## Potential Thermal and Voltage Violations

The analysis identified potential thermal violations resulting from the new load at the Quindaro delivery point. No voltage violations were observed in the analyzed study cases. The identified thermal violations are summarized in Table 3-1.

Table 3-1. Potential Thermal Violations

| Year | Facility Name | Contingency Name | Rate A, Rate B (MVA) | Max Flow (MVA) | Study Model Max Loading (%) | Transfer Limit (MW) | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2027W | 546200 MILLST TAP 5 - 546222 ROSEDALE 5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 406.8 | 127.94% | 202.85 | Resolved with 546652 QUINDARO5 to 546653 NEARMAN CKT2, which will be in-service Jun 2028. The ability to serve Quindaro load will be dependent on this future in-service line |
| 2027W | 546200 MILLST TAP 5 - 546661 ARMDALE5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 400.1 | 125.81% | 209.51 |  |
| 2027W | 546222 ROSEDALE 5 - 546651 BARBER 5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 433.3 | 129.36% | 193.92 |  |
| 2027W | 546659 CTR CTY5 - 546667 FAIRFX-5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 366.5 | 115.25% | 248.15 |  |
| 2027W | 546659 CTR CTY5 - 546750 MUNCIE 5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 385.4 | 121.21 % | 229.12 |  |
| 2027W | 546661 ARMDALE5- 546750 MUNCIE 5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 387.8 | 121.95% | 222.86 |  |
| 2027W | 546667 FAIRFX-5 - 546684 FIBGLAS5 | P12:161:KACY:QUIND-NEARMAN::QUINDARO-NEARMAN OPEN OPEN LINE FROM BUS 546652 TO BUS 546653 CIRCUIT 1 | 318/318 | 356 | 111.94% | 258.74 |  |
| 2035S | 542987 GRAND 5 - 542989 NAVY 5 | P12:161:KCPL:NRTHST-GRANDAVE-NTHEASTCAP:::HV:' OPEN LINE FROM BUS 542985 TO BUS 542988 CKT 1 REMOVE SWSHUNT FROM BUS 542948 | 259/259 | 260.1 | 100.42% | 286.53 |  |
| 2035S | 542987 GRAND 5 - 543666 NEASTN5 | P12:161:KCPL:NRTHST-GRANDAVE-NTHEASTCAP:::HV:' OPEN LINE FROM BUS 542985 TO BUS 542988 CKT 1 REMOVE SWSHUNT FROM BUS 542948 | 259/259 | 260.3 | 100.5% | 284.30 |  |

## Short Circuit

SPP performed short circuit analysis for the 2030 Summer Peak with the new load addition. The analysis identified the currents listed in Table 3-2.

Table 3-2. Short Circuit Results

| Season | Model | Fault | Bus | Current (Amps) |
| --- | --- | --- | --- | --- |
| 30S | Max Fault | Three Phase | LOAD 2 34.500 | 10,402 |
| 30S | Max Fault | Three Phase | LOAD 3 34.500 | 10,402 |
| 30S | Max Fault | Three Phase | LOAD 1 34.500 | 10,402 |
| 30S | Max Fault | Three Phase | SUB_P1 161.00 | 51,756 |
| 30S | Max Fault | Three Phase | SUB_S11 34.500 | 15,039 |
| 30S | Max Fault | Three Phase | SUB_S12 34.500 | 15,039 |
| 30S | Max Fault | Three Phase | SUB_S13 34.500 | 15,039 |
| 30S | Max Fault | Three Phase | EDWRDVL5 161.00 | 24,010 |
| 30S | Max Fault | Three Phase | WETHRBY5 161.00 | 17,072 |
| 30S | Max Fault | Three Phase | SHWNMSN5 161.00 | 39,871 |
| 30S | Max Fault | Three Phase | WALDRON5 161.00 | 16,481 |
| 30S | Max Fault | Three Phase | BARBER 5 161.00 | 35,525 |
| 30S | Max Fault | Three Phase | QUINDARO5 161.00 | 53,388 |
| 30S | Max Fault | Three Phase | NEARMAN5 161.00 | 41,289 |
| 30S | Max Fault | Three Phase | SUNSET 5 161.00 | 25,830 |
| 30S | Max Fault | Three Phase | KAW W 5 161.00 | 27,755 |
| 30S | Max Fault | Three Phase | MAYWOOD5 161.00 | 27,200 |
| 30S | Max Fault | Three Phase | GIBBS 5 161.00 | 26,277 |
| 30S | Max Fault | Three Phase | CTR CTY5 161.00 | 19,893 |
| 30S | Max Fault | Three Phase | GM PLT 5 161.00 | 25,827 |
| 30S | Max Fault | Three Phase | TURNER 5 161.00 | 25,727 |
| 30S | Max Fault | Three Phase | FAIRFX-5 161.00 | 21,274 |
| 30S | Max Fault | Three Phase | PIPER 5 161.00 | 17,715 |
| 30S | Max Fault | Three Phase | WOLCOTT5 161.00 | 20,317 |
| 30S | Max Fault | Three Phase | OAK KNOL 69.000 | 10,926 |
| 30S | Max Fault | Three Phase | MORRIS 2 69.000 | 10,506 |
| 30S | Max Fault | Three Phase | SPEAKER2 69.000 | 10,111 |
| 30S | Max Fault | Three Phase | GW TAP 1 69.000 | 12,548 |
| 30S | Max Fault | Three Phase | GW TAP 2 69.000 | 11,710 |
| 30S | Max Fault | Three Phase | MAYWOOD2 69.000 | 12,184 |
| 30S | Max Fault | Three Phase | MAYWOOD12.4712.470 | 22,647 |
| 30S | Max Fault | Three Phase | MUNCIE 2 69.000 | 9,237 |
| 30S | Max Fault | Three Phase | EVERETT2 69.000 | 9,994 |
| 30S | Max Fault | Three Phase | FIBGLAS5 161.00 | 22,158 |
| 30S | Max Fault | Three Phase | COL PAL2 69.000 | 9,165 |
| 30S | Max Fault | Three Phase | KAW WEST13 13.800 | 11,081 |
| 30S | Max Fault | Three Phase | BARBER13 13.800 | 20,806 |
| 30S | Max Fault | Three Phase | KAW WST2 69.000 | 13,310 |
| 30S | Max Fault | Three Phase | BARBER 2 69.000 | 9,392 |
| 30S | Max Fault | Three Phase | QUINDA 2 69.000 | 14,939 |
| 30S | Max Fault | Three Phase | V WEST2 69.000 | 10,462 |
| 30S | Max Fault | Three Phase | QUINDB 2 69.000 | 14,812 |
| 30S | Max Fault | Three Phase | QUINDC 2 69.000 | 14,589 |
| 30S | Max Fault | Three Phase | QUINDARO13 13.800 | 16,602 |
| 30S | Max Fault | Three Phase | QCT2 1 13.800 | 24,593 |
| 30S | Max Fault | Three Phase | QCT3 1 13.800 | 31,936 |
| 30S | Max Fault | Three Phase | NMGEN N1 20.000 | 69,102 |
| 30S | Max Fault | Three Phase | NMISOBUS 20.000 | 69,151 |
| 30S | Max Fault | Three Phase | MAYSOTH5 161.00 | 27,144 |
| 30S | Max Fault | Three Phase | NM CT4 1 13.200 | 47,104 |
| 30S | Max Fault | Three Phase | METRO 5 161.00 | 30,723 |
| 30S | Max Fault | Three Phase | MUNCIE 5 161.00 | 19,507 |
| 30S | Max Fault | Three Phase | NM4 BUS 161.00 | 37,931 |

## Stability

EPE performed a dynamic stability analysis to assess the impact of the proposed load addition on system stability, based on the assumptions outlined in Section 2. The analysis was conducted in accordance with SPP’s Disturbance Performance Requirements.

Simulated fault events included three-phase faults and single-line-to-ground stuck breaker faults. Single-line-to-ground faults were approximated by applying a fault impedance to reduce the faulted bus positive sequence voltage to 0.60 pu. A full list and description of the simulated faults is provided in Appendix C.

Appendix B presents the results for all fault events simulated in the modified study model. Prior to the addition of the project, Ralph Green natural gas 69 kV unit was observed to trip due to undervoltage protection during select contingency definitions. This behavior was identified as a pre-existing model issue and was not caused by the interconnection of the 300 MW Quindaro load model. Disabling the LOEXR1T relay model or increasing the relay’s self-trip breaker timer allowed the affected contingencies to ride through the contingency disturbance and complete the dynamic simulations successfully without any adverse impact to system stability.

Additionally, under select P4 contingencies, Nearman coal unit exhibited loss of synchronism. This instability was also present prior to the addition of the 300 MW Quindaro Load and therefore represents a pre-existing system characteristic. A critical clearing time analysis was performed for the troublesome P4 contingencies, identifying 10, 12, and 14 cycles as the maximum clearing times prior to loss of synchronism. Clearing times beyond these limits resulted in loss of synchronism for the Nearman coal unit. These results were below the typical 16-cycle fault clearing time observed for the remaining P4 contingencies, where stable system response was maintained. The observed instability is therefore associated with specific existing system conditions rather than the addition of the Project load.

Based on the study results, the analysis indicates that the addition of the 300 MW Quindaro Load did not worsen any pre-existing stability issues or introduce any new stability concerns under the simulated contingency conditions. No damping or voltage recovery violations attributable to the Project were identified under the simulated contingencies. Accordingly, the dynamic simulations demonstrate that the addition of the 300 MW Quindaro load does not adversely impact the transient stability performance of the system under the evaluated contingency conditions.

A separate study load-drop contingency was also simulated to evaluate potential frequency excursions and high-voltage conditions resulting from the sudden rejection of the Project load within the study area. The contingency was successfully completed, and the results demonstrated acceptable system performance. No frequency or voltage recovery violations were observed, indicating that the loss of the Project load does not result in adverse dynamic performance under the evaluated conditions.

## EMT Screening

EMT screening was performed for the 300 MW Quindaro load using the GSAT tool and the stability model, based on the Short Circuit Ratio (SCR) calculated at the Quindaro 161 kV substation. SCR is defined as the ratio of the three-phase short circuit MVA at a given location to the MW rating of the load at that location.

The SCR threshold for identification of an electrically weak location used by SPP is any value below 3.0, which indicates an elevated risk of voltage or control instability requiring further assessment using EMT analysis. It must be noted that the SCR value does not necessarily eliminate the need for further assessment in EMT studies and is only provided as an indicator for this study. Additional assessment may be required at SPP's discretion.

The study found that the SCR at Quindaro 161 kV substation does not fall below 3 under any of the system conditions. The results of the SCR Screening are included in Appendix D.

Table 3-3: Short Circuit Ratio Results

| Load | Min SCR | SCR Pass/Fail | EMT Analysis Requirement based on SCR? |
| --- | --- | --- | --- |
| Quindaro Load | 14.42 | Pass | No |

## Transmission Solutions

The addition of the new load at the Quindaro delivery point resulted in potential thermal overloads on the 161 kV transmission system near the load. Portfolio 1 consists of rebuilding the overloaded transmission lines identified in Table 3-1.  Portfolio 2 includes a new Nearman – Quindaro 2nd circuit 161kV line.

Portfolio #1: Total cost $10.3 M

- Reconductor Grand - Navy 161kV line (0.18 miles)

- Reconductor Grand - Northeastern 161kV line (1.67 miles)

- Reconductor Mill St Tap - Rosedale 161kV line (1.65 miles)

- Reconductor Mill St Tap - Armdale 161kV line (1.16 miles)

- Reconductor Rosedale - Barber 161kV line (2.1 miles)

- Reconductor Center City - Fairfax 161kV line (2.1 miles)

- Reconductor Center City - Muncie 161kV line (2.35 miles)

- Reconductor Armdale - Muncie 161kV line (1.86 miles)

- Reconductor Fairfax - Fiberglass 161kV line (0.71 miles)

Portfolio #2: Total cost $8.9 M

- Reconductor Grand - Navy 161kV line (0.18 miles)

- Reconductor Grand - Northeastern 161kV line (1.67 miles)

- New Nearman – Quindaro 161kV line ckt 2 (3.57 miles)

SPP chose to move forward with Portfolio #2.  This solution solves all issues identified in Table 3-1 in the most cost-effective manner.

Table 3-4:  Recommended Upgrade Portfolio #2

| New Upgrade Description* | Mileage | Required Flow (MVA) | Date Needed** | Host Transmission Owner | Estimated Cost*** |
| --- | --- | --- | --- | --- | --- |
| Reconductor Grand - Navy 161kV line | 0.18 | 313 | 6/1/2035 | KCPL | $135,000 |
| Reconductor Grand - Northeastern 161kV line | 1.67 | 313 | 6/1/2035 | KCPL | $1,252,500 |
| New Nearman – Quindaro 161kV line ckt 2 | 3.57 | 318 | 7/1/2027 | KACY | $7,497,000 |
| TOTAL NEW UPGRADE COST |  |  |  |  | $8,884,500 |

*Pursuant to Attachment AX of the Tariff, the Transmission Provider is responsible for assessing the impacts on the Transmission System caused by modifying an existing delivery point or establishing the new delivery point through the Provisional Load Process Study (“PLPS”). The PLPS may determine the need for a Network Upgrade(s) necessary for the modification of an existing delivery point or the establishment of a new delivery point. A Network Upgrade(s) that the Transmission Customer or Host Transmission Owner desires that exceeds the needed Network Upgrade(s) identified in the PLPS will need to be studied through the Transmission Provider’s Sponsored Upgrade study process to evaluate the impacts of the desired changes on the Transmission System.

**If the project need date specified in this study cannot be met, the Transmission Owner will be required to submit mitigations pursuant to the SPP Project Tracking process. All upgrades or mitigations must be in place prior to the dates shown in Table 3-4.

***Note that the estimated new upgrade cost provided in this report is an SPP Conceptual Cost Estimate only; this is preliminary, and a more refined Study Cost Estimate will be developed after issuance of this report through a Standardized Cost Estimate Reporting Template (SCERT).

# Section 4: Conclusion

The AC analysis revealed potential thermal violations associated with the Quindaro load addition.  Among the evaluated options, Portfolio 2 provides the most cost-effective upgrade approach, reducing the overall scope of system upgrades while maintaining reliable system performance within the SPP transmission network.

The study shows that the following upgrades are required to reliably serve the load addition:

- Reconductor Grand - Navy 161kV line (0.18 miles)

- Reconductor Grand - Northeastern 161kV line (1.67 miles)

- New Nearman – Quindaro 161kV line ckt 2 (3.57 miles)

Furthermore, the dynamic stability assessment demonstrates that the addition of the 300 MW Quindaro load does not adversely impact the transient performance of the transmission system under the evaluated contingency conditions. No project-related damping, voltage recovery, or frequency response violations were identified. Although pre-existing dynamic model issues were observed during select contingencies, they were not caused or worsened by the project. Overall, the project satisfies the dynamic performance requirements for the simulated conditions.

A SCR screening study was performed to assess the strength of the grid at the Quindaro 161 kV substation. The study did not determine any system conditions under which the SCR falls below the threshold.

# Appendix

## Appendix A

## Appendix B

## Appendix C

## Appendix D

SPP Disturbance Performance Requirements: https://www.spp.org/documents/28859/spp%20disturbance%20performance%20requirements%20(twg%20approved).pdf