# Provisional Load Process Study

# PLP-2026-JANuary-0004

By SPP Engineering, Transmission Services

Published on 7/16/2026

# Revision History

| Date or version number | Author | Change Description | Comments |
| --- | --- | --- | --- |
| 6/26/2026 | EPE/SPP | Original |  |
| 7/16/2026 | EPE/SPP | Restudy with updated load modeling |  |

Contents

Revision History	i

Section 1: Introduction	1

Section 2: Study Methodology	2

Objective	2

Study Process	2

Section 3: Results of analysis	6

Potential Thermal and Voltage Violations	6

Short Circuit	8

Stability	9

EMT Screening	10

Transmission Solutions	10

Section 4: Conclusion	13

Appendix	14

Appendix A	14

Appendix B	14

Appendix C	14

Appendix D	14

# Section 1: Introduction

This report outlines the results of an evaluation of regional transmission impacts from delivery point request PLP-2026-January-004 Project Aether. The requesting entity plans to add load to a new delivery point called Alpha with an in-service date of 12/1/2027. The delivery point is in the Southwestern Power Administration (SPA) Transmission System.

The load flow models used for the evaluation were 2025 Integrated Transmission Planning (ITP) base reliability models. Southwest Power Pool (SPP) performed an Alternating Current (AC) contingency analysis on these models using TARA.

# Section 2: Study Methodology

## Objective

The purpose of this study was to determine the regional transmission system impacts within the SPP footprint associated with the addition of a new, 816 MW data center load in the Clarksville area served by Clarksville Connected Utilities (CCU). The study modeled an initial 18 MW load and an expanded load of 798 MW (total 816 MW) in the 2029 and 2034 model years. The load was interconnected at the existing 69 kV CLRKSVL2 station (Bus 505511) and the proposed 161 kV Substation Alpha - Clarksville Bravo station (Bus 505996).

The new delivery point and associated facilities are intended to support a phased data center development near Clarksville, Arkansas. In the 2029 Light Load model, the modeled expanded load was reduced to 667 MW instead of 798 MW to reflect the expected loading conditions for that seasonal scenario.

To accommodate the proposed Clarksville load addition, additional generation resources were added in the surrounding area to support system performance and reliability. The details regarding the generation additions are provided below.

## Study Process

- Model Assumptions

  - 2025 ITP Base Reliability Model Series

    - Model years 2029 and 2034

    - Summer Peak (2029S and 2034S), Winter Peak (2029W and 2034W), and Light Load (2029L and 2034L)

  - 2025 ITP Short Circuit Model Series

    - 2029 Summer Max Fault

  - 2025 Transmission System Planning (TPL) Dynamic Model Series

    - 2034 Summer Peak Base and Change Models

  - Planned Generation

    - Petit Jean Solar – 150 MW

    - Pinnacle Solar (GEN-2023-132) – 150 MW

    - Muleshoe Battery (GEN-2019-011) – 207 MW

    - Evergy PPA – 18 MW

    - Clarksville BESS – 100 MW

    - Clarksville Gas – 200 MW

    - Clarksville Gas – 160 MW

Table 2-1. Study Models

| Model Name | Study Year | Season | Scenario | Load (MW/MVAR) |
| --- | --- | --- | --- | --- |
| 2025ITPFinal-29L.sav | 2029 | Light Load | Base Reliability | Base Model |
| 2025ITPFinal-29S.sav | 2029 | Summer Peak | Base Reliability | Base Model |
| 2025ITPFinal-29W.sav | 2029 | Winter Peak | Base Reliability | Base Model |
| 2025ITPFinal-34L.sav | 2034 | Light Load | Base Reliability | Base Model |
| 2025ITPFinal-34S.sav | 2034 | Summer Peak | Base Reliability | Base Model |
| 2025ITPFinal-34W.sav | 2034 | Winter Peak | Base Reliability | Base Model |
| 2025ITPFinal-29L_Study.sav | 2029 | Light Load | Base Reliability | CLRKSVL2 (69 kV) – 18/4.51 Clarksville Bravo (161 kV) – 667/166.75 |
| 2025ITPFinal-29S_Study.sav | 2029 | Summer Peak | Base Reliability | CLRKSVL2 (69 kV) – 18/4.51 Clarksville Bravo (161 kV) – 798/199.99 |
| 2025ITPFinal-29W_Study.sav | 2029 | Winter Peak | Base Reliability | CLRKSVL2 (69 kV) – 18/4.51 Clarksville Bravo (161 kV) – 798/199.99 |
| 2025ITPFinal-34L_Study.sav | 2034 | Light Load | Base Reliability | CLRKSVL2 (69 kV) – 18/4.51 Clarksville Bravo (161 kV) – 798/199.99 |
| 2025ITPFinal-34S_Study.sav | 2034 | Summer Peak | Base Reliability | CLRKSVL2 (69 kV) – 18/4.51 Clarksville Bravo (161 kV) – 798/199.99 |
| 2025ITPFinal-34W_Study.sav | 2034 | Winter Peak | Base Reliability | CLRKSVL2 (69 kV) – 18/4.51 Clarksville Bravo (161 kV) – 798/199.99 |

- Steady State Analysis

  - Assumptions (consistent with the ITP analysis)

    - AC contingency analysis on all load flow models using PSS®E and TARA

    - Monitored Elements

      - SPP facilities 69 kV and above

      - First-tier companies 100 kV and above

    - Contingencies (consistent with the ITP analysis)

      - Provided by SPP members and first-tier companies

      - Autogenerated contingencies capturing P1s that were missing in the SPP members provided contingencies.

    - Apply SPP Criteria and National American Electric Reliability Corporation (NERC) reliability standards

  - The study focused only on violations caused by the addition of the proposed Clarksville load. The study model results were compared against the corresponding base models and any violations that already existed in the base models were excluded from the analysis. Only the new violations created by the proposed load addition were considered in the evaluation and development of mitigation upgrades.

- Short Circuit Analysis

  - Assumptions

    - Used 2025 Final ITP Short Circuit models (Max Fault)

      - Placed all available facilities in service

        - Generation

        - Transmission lines

        - Transformers

        - Buses

      - Short Circuit Output

        - Physical

      - Short Circuit Coordinates

        - Polar

      - Short Circuit Parameters

        - 3 Phase

      - FLAT – classical fault analysis conditions

  - Analyses

    - Three-phase fault

- Dynamics Analysis

  - Assumptions

    - The 2026 Series TPL 2030 Summer Peak Models were modified to include the 816 MW load at the proposed 161 kV Substation Alpha - Clarksville Bravo station (Bus 505996).

    - The dynamic model for the 816 MW load was added as detailed in Appendix A.

    - The following generators and their associated dynamic models were added to the model:

        - Clarksville Gas Power Station (370 MW)

        - Clarksville BESS (103.45 MW)

        - Petite Jean Solar and BESS (151.1 MW)

        - Pinnacle Solar (152 MW)

        - Muleshoe BESS (211.31 MW)

  - Dynamic Stability analysis was performed using PSS®E.

    - Monitored Elements

      - The active power (PELEC), reactive power (QELEC), and terminal voltage (ETERM) of all conventional and renewable generation interconnecting within 5 levels of POI. The machine rotor angle of conventional generators was also monitored.

      - The voltage and frequency of all transmission buses 69 kV and above within the study area were monitored.

      - The active and reactive power of the 816 MW load at Clarksville was monitored.

    - Model Dispatch

      - To balance the swing after adding the study load, following generators were switched on and/or dispatched up:

        - Clarksville Gas Power Station (6 units)

        - Clarksville BESS

        - Petite Jean Solar

        - Pinnacle Solar

        - Muleshoe BESS

        - PARAGLD2

    - Fault Definitions

      - EPE developed and simulated a revised set of fault events for DPA-2026-February-2281 using modified study models. The updated fault set was executed to assess system performance under the revised modelling assumptions.

      - The fault models included both three-phase faults and single-line-to-ground (SLG) stuck breaker faults. SLG faults were represented using an equivalent fault impedance approach, adjusted such that the faulted bus positive-sequence voltage is reduced to approximately 0.6 pu.

      - In addition, P3 contingency events were constructed by combining the tripping of a generating unit within the study area followed by the outage of a transmission element within three voltage levels of the Point of Interconnection (POI). The following generating units were included in the P3 contingency definition:

        - Clarksville Gas Power Station (370 MW)

        - Clarksville BESS (103.45 MW)

        - Dardanelle 1 & 2 (67 MW)

        - Ozark 3, 4, and 5 (60 MW)

      - A separate study load drop contingency was also simulated to evaluate potential frequency excursions and high-voltage conditions resulting from sudden load rejection within the study area.

      - A complete list and detailed description of all simulated fault events are provided in Appendix B.

# Section 3: Results of analysis

## Potential Thermal and Voltage Violations

The analysis identified potential thermal violations resulting from the new load at the Clarksville delivery point. The identified thermal violations are summarized in Table 3-1. No voltage violations were observed in the assessed study models.

Table 3-1. Potential Thermal Violations

| Year | Season | Facility Name | Contingency Name | Rate A, Rate B (MVA) | Max Flow (MVA) | Study Model Max Loading (%) |
| --- | --- | --- | --- | --- | --- | --- |
| 2029S | Summer | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505514 TO BUS 515319 CKT 1 | 189/189 | 231.2 | 122.35 |
| 2029S | Summer | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 515319 TO BUS 515355 CKT 1 | 189/189 | 219.1 | 115.93 |
| 2029S | Summer | 505514 CLARKSV5 505516 OZARK H5 | P12:161:OKGE-AEPW:BKRBKR3550:::HV: | 189/189 | 193.2 | 102.23 |
| 2029S | Summer | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 189/189 | 198.3 | 104.91 |
| 2029S | Summer | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 223/223 | 249.7 | 111.95 |
| 2029S | Summer | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505514 TO BUS 505516 CKT 1 | 223/223 | 243.4 | 109.15 |
| 2029S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 148/167 | 205.4 | 122.97 |
| 2029S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | TRIP LINE FROM BUS 337909 TO BUS 515305 CKT 1 | 148/167 | 202.8 | 121.45 |
| 2029S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | OPEN BRANCH FROM BUS 337909 TO BUS 515305 CKT 1 | 148/167 | 202.8 | 121.45 |
| 2029S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | OPEN BRANCH FROM BUS 337909 TO BUS 515305 CKT 1 | 148/167 | 202.8 | 121.45 |
| 2029S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 148/167 | 191.4 | 114.63 |
| 2029W | Winter | 504172 BOONEVIL 2 507198 WBOONVL2 | OPEN BRANCH FROM BUS 507190 TO BUS 515316 CKT 1 | 48/48 | 53.9 | 112.32 |
| 2029W | Winter | 504172 BOONEVIL 2 507198 WBOONVL2 | OPEN BRANCH FROM BUS 507190 TO BUS 515316 CKT 1 | 48/48 | 53.9 | 112.32 |
| 2029W | Winter | 504172 BOONEVIL 2 507198 WBOONVL2 | OPEN BRANCH FROM BUS 507190 TO BUS 515316 CKT 1 | 48/48 | 53.9 | 112.32 |
| 2029W | Winter | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505514 TO BUS 515319 CKT 1 | 223/223 | 242.2 | 108.59 |
| 2029W | Winter | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 515319 TO BUS 515355 CKT 1 | 223/223 | 232.4 | 104.22 |
| 2029W | Winter | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 223/223 | 239.4 | 107.36 |
| 2029W | Winter | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505514 TO BUS 505516 CKT 1 | 223/223 | 254.3 | 114.02 |
| 2034L | Light Load | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505514 TO BUS 515319 CKT 1 | 218/218 | 238.4 | 109.38 |
| 2034L | Light Load | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 515319 TO BUS 515355 CKT 1 | 218/218 | 220.0 | 100.91 |
| 2034L | Light Load | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505514 TO BUS 505516 CKT 1 | 223/223 | 263.2 | 118.05 |
| 2034L | Light Load | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 223/223 | 233.1 | 104.54 |
| 2034S | Summer | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505514 TO BUS 515319 CKT 1 | 189/189 | 235.5 | 124.6 |
| 2034S | Summer | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 515319 TO BUS 515355 CKT 1 | 189/189 | 223.7 | 118.35 |
| 2034S | Summer | 505514 CLARKSV5 505516 OZARK H5 | P12:161:OKGE-AEPW:BKRBKR3550:::HV: | 189/189 | 197.2 | 104.32 |
| 2034S | Summer | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 189/189 | 200.7 | 106.19 |
| 2034S | Summer | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505514 TO BUS 505516 CKT 1 | 223/223 | 247.3 | 110.91 |
| 2034S | Summer | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 223/223 | 252.3 | 113.12 |
| 2034S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | 148/167 | 214.1 | 128.22 |
| 2034S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | TRIP LINE FROM BUS 337909 TO BUS 515305 CKT 1 | 148/167 | 211.1 | 126.43 |
| 2034S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | OPEN BRANCH FROM BUS 337909 TO BUS 515305 CKT 1 | 148/167 | 211.1 | 126.43 |
| 2034S | Summer | 515300 FTSMTHE5 515345 COLONY 5 | OPEN BRANCH FROM BUS 515300 TO BUS 515310 CKT 1 | 340/404 | 461.1 | 114.14 |
| 2034S | Summer | 515311 BARLING5 515343 MASSARD5 | OPEN BRANCH FROM BUS 515300 TO BUS 515345 CKT 1 | 230/271 | 290.8 | 107.31 |
| 2034S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | OPEN BRANCH FROM BUS 337909 TO BUS 515305 CKT 1 | 148/167 | 211.1 | 126.43 |
| 2034S | Summer | 507190 NMAGZIN5 515316 BRANCH 5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 148/167 | 200.6 | 120.13 |
| 2034W | Winter | 504172 BOONEVIL 2 507198 WBOONVL2 | OPEN BRANCH FROM BUS 507190 TO BUS 515316 CKT 1 | 48/48 | 56.5 | 117.73 |
| 2034W | Winter | 504172 BOONEVIL 2 507198 WBOONVL2 | OPEN BRANCH FROM BUS 507190 TO BUS 515316 CKT 1 | 48/48 | 56.5 | 117.73 |
| 2034W | Winter | 504172 BOONEVIL 2 507198 WBOONVL2 | OPEN BRANCH FROM BUS 507190 TO BUS 515316 CKT 1 | 48/48 | 56.5 | 117.73 |
| 2034W | Winter | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 505514 TO BUS 515319 CKT 1 | 223/223 | 246.0 | 110.30 |
| 2034W | Winter | 505514 CLARKSV5 505516 OZARK H5 | OPEN BRANCH FROM BUS 515319 TO BUS 515355 CKT 1 | 223/223 | 237.2 | 106.39 |
| 2034W | Winter | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505514 TO BUS 505516 CKT 1 | 223/223 | 257.9 | 115.66 |
| 2034W | Winter | 505514 CLARKSV5 515319 LSPADRA5 | OPEN BRANCH FROM BUS 505508 TO BUS 505514 CKT 1 | 223/223 | 238.3 | 106.84 |
| 2034W | Winter | 515345 COLONY 5 515349 BATTLEF5 | OPEN BRANCH FROM BUS 515300 TO BUS 515310 CKT 1 | 294/328 | 349.2 | 106.47 |

## Short Circuit

SPP performed a short circuit analysis for the 2029 Summer Peak with the new load addition. The analysis identified the currents listed in Table 3-2.

Table 3-2. Short Circuit Results

| Season | Model | Fault | Bus | Current (Amps) |
| --- | --- | --- | --- | --- |
| 29S | Max Fault | Three Phase | POI_BUS 161.00 | 13,963 |
| 29S | Max Fault | Three Phase | GSU11 13.800 | 39,030 |
| 29S | Max Fault | Three Phase | GSU12 13.800 | 39,030 |
| 29S | Max Fault | Three Phase | GSU13 13.800 | 39,030 |
| 29S | Max Fault | Three Phase | GSU21 13.800 | 34,132 |
| 29S | Max Fault | Three Phase | GSU22 13.800 | 34,132 |
| 29S | Max Fault | Three Phase | GSU23 13.800 | 34,132 |
| 29S | Max Fault | Three Phase | GSU24 13.800 | 34,132 |
| 29S | Max Fault | Three Phase | GSU25 13.800 | 34,132 |
| 29S | Max Fault | Three Phase | DARDAN.APL 161.00 | 12,042 |
| 29S | Max Fault | Three Phase | RUSSELVL S 161.00 | 13,255 |
| 29S | Max Fault | Three Phase | HILLTOP 161.00 | 9,397 |
| 29S | Max Fault | Three Phase | FITZHUGH 5 161.00 | 13,196 |
| 29S | Max Fault | Three Phase | SWPINEY5 161.00 | 6,306 |
| 29S | Max Fault | Three Phase | DARDANE5 161.00 | 13,749 |
| 29S | Max Fault | Three Phase | DAR1&2 1 13.800 | 36,012 |
| 29S | Max Fault | Three Phase | CLRKSVL2 69.000 | 7,824 |
| 29S | Max Fault | Three Phase | DAR3&4 1 13.800 | 35,931 |
| 29S | Max Fault | Three Phase | CLK X1 1 12.470 | 6,886 |
| 29S | Max Fault | Three Phase | CLARKSV5 161.00 | 14,007 |
| 29S | Max Fault | Three Phase | CLK X2 1 12.470 | 6,886 |
| 29S | Max Fault | Three Phase | OZARK H5 161.00 | 12,862 |
| 29S | Max Fault | Three Phase | OZK1&2 1 13.800 | 25,232 |
| 29S | Max Fault | Three Phase | OZK345 1 13.800 | 29,672 |
| 29S | Max Fault | Three Phase | VAN BUR5 161.00 | 18,513 |
| 29S | Max Fault | Three Phase | CLK ALPHA 161.00 | 13,971 |
| 29S | Max Fault | Three Phase | CLK BRAVO 161.00 | 11,484 |
| 29S | Max Fault | Three Phase | CLK BXMR 1 113.800 | 6,787 |
| 29S | Max Fault | Three Phase | CLK BXMR 2 113.800 | 6,787 |
| 29S | Max Fault | Three Phase | CLK BXMR 3 113.800 | 6,787 |
| 29S | Max Fault | Three Phase | CLK BXMR 4 113.800 | 6,787 |
| 29S | Max Fault | Three Phase | CLK BXMR 5 113.800 | 6,787 |
| 29S | Max Fault | Three Phase | CLK BRAVO 34.500 | 26,250 |
| 29S | Max Fault | Three Phase | LSPADRA5 161.00 | 11,145 |
| 29S | Max Fault | Three Phase | LSPADRA2 69.000 | 8,390 |
| 29S | Max Fault | Three Phase | IGO 5 161.00 | 10,531 |
| 29S | Max Fault | Three Phase | LSPADR41 13.800 | 2,615 |

## Stability

SPP performed a dynamic stability analysis to assess the impact of the proposed load addition on system stability, based on the assumptions outlined in Section 2. The analysis was conducted in accordance with SPP’s Disturbance Performance Requirements.

Simulated fault events included three-phase faults and single-line-to-ground stuck breaker faults. Single-line-to-ground faults were approximated by applying a fault impedance to reduce the faulted bus positive sequence voltage to 0.60 pu. A full list and description of the simulated faults is provided in Appendix B.

Appendix C presents the results for all fault events simulated in the modified study model. The analysis indicates that no pre-existing or newly identified stability issues were observed under the simulated contingencies. No damping or voltage recovery violations attributable to the addition of the 816 MW Clarksville load were identified during the simulated faults.

Load ride-through performance was evaluated across all simulated events. The study identified that a significant portion of the electrical load trips during a majority of events, driven by the dynamic load model's trip threshold of 0.92 pu and the model's inability to account for the proposed 4-second time delay. To assess the potential impact on system stability under a scenario where protection does not operate instantaneously, a sensitivity analysis was conducted. This involved adjusting the composite load model's electrical load trip setpoint and enabling load reconnection following voltage recovery. No damping or voltage recovery violations were observed in the sensitivity model.

## EMT Screening

EMT screening was performed for the 816 MW Clarksville load using the GSAT tool and the stability model, based on the Short Circuit Ratio (SCR) calculated at the Clarksville 161 kV substation. SCR is defined as the ratio of the three-phase short circuit MVA at a given location to the MW rating of the load at that location.

The SCR threshold for identification of an electrically weak location used by SPP is any value below 3.0, which indicates an elevated risk of voltage or control instability requiring further assessment using EMT analysis. It must be noted that the SCR value does not necessarily eliminate the need for further assessment in EMT studies and is only provided as an indicator for this study. Additional assessment may be required at SPP's discretion.

The study found that the SCR at the Clarksville 161 kV substation does not fall below 3 under any system conditions. The results of the SCR Screening are included in Appendix D.

Table 3-3: Short Circuit Ratio Results

| Load | Min SCR | SCR Pass/Fail | EMT Analysis Requirement based on SCR? |
| --- | --- | --- | --- |
| Clarksville Load | 3.813 | Pass | No |

## Transmission Solutions

The addition of the new load at the Clarksville delivery point resulted in potential thermal overloads on the 69 kV and 161 kV transmission systems. To mitigate these violations, SPP identified the following upgrade portfolios.

Portfolio #1: Total cost $33.6 M

- Reconductor Clarksville – Ozark 161kV line (26.1 miles)

- Reconductor N Magazine – Branch 161kV line (8.8 miles)

- Rebuild Clarksville – Little Spadra 161kV line (5.95 miles)

- Reconductor Booneville – W Booneville 69kV line (0.56 miles)

- Reconductor Ft Smith – Colony 161kV line (2.22 miles)

- Reconductor Barlington – Massard 161kV line (2.8 miles)

- Reconductor Colony - Battlefield 161kV line (1.12 miles)

Portfolio #2: Total cost $54.1 M

- New Clarksville – ANO 161kV line (23 miles)

SPP chose to move forward with Portfolio #1.  This solution solves all issues identified in Table 3-1 in the most cost-effective manner.

Table 3-4:  Recommended Upgrade Portfolio #1

| New Upgrade Description* | Mileage | Required Flow (MVA) | Date Needed** | Host Transmission Owner | Estimated Cost*** |
| --- | --- | --- | --- | --- | --- |
| Reconductor Clarksville – Ozark 161kV line | 26.1 | 291 | 12/1/2027 | SWPA | $15,921,000 |
| Reconductor N Magazine – Branch 161kV line | 8.8 | 225 | 12/1/2027 | AEPW / OKGE | $5,368,000 |
| Rebuild Clarksville – Little Spadra 161kV line | 5.95 | 369 | 12/1/2027 | OKGE | $8,327,025 |
| Reconductor Booneville – W Booneville 69kV line | 0.56 | 63 | 12/1/2029 | AEPW | $247,520 |
| Reconductor Ft Smith – Colony 161kV line | 2.22 | 520 | 6/1/2032 | OKGE | $1,354,200 |
| Reconductor Barlington – Massard 161kV line | 2.8 | 339 | 6/1/2033 | OKGE | $1,708,000 |
| Reconductor Colony - Battlefield 161kV line | 1.12 | 412 | 12/1/2033 | OKGE | $683,200 |
| TOTAL NEW UPGRADE COST |  |  |  |  | $33,608,945 |

*Pursuant to Attachment AX of the Tariff, the Transmission Provider is responsible for assessing the impacts on the Transmission System caused by modifying an existing delivery point or establishing the new delivery point through the Provisional Load Process Study (“PLPS”). The PLPS may determine the need for a Network Upgrade(s) necessary for the modification of an existing delivery point or the establishment of a new delivery point. A Network Upgrade(s) that the Transmission Customer or Host Transmission Owner desires that exceeds the needed Network Upgrade(s) identified in the PLPS will need to be studied through the Transmission Provider’s Sponsored Upgrade study process to evaluate the impacts of the desired changes on the Transmission System.

**If the project need date specified in this study cannot be met, the Transmission Owner will be required to submit mitigations pursuant to the SPP Project Tracking process. All upgrades or mitigations must be in place prior to the dates shown in Table 3-4.

***Note that the estimated new upgrade cost provided in this report is an SPP Conceptual Cost Estimate only; this is preliminary, and a more refined Study Cost Estimate will be developed after issuance of this report through a Standardized Cost Estimate Reporting Template (SCERT).

# Section 4: Conclusion

The steady state analysis revealed potential thermal violations associated with the new load addition.  The study shows the following upgrades are required to reliably serve the new load:

- Reconductor Clarksville – Ozark 161kV line (26.1 miles)

- Reconductor N Magazine – Branch 161kV line (8.8 miles)

- Rebuild Clarksville – Little Spadra 161kV line (5.95 miles)

- Reconductor Booneville – W Booneville 69kV line (0.56 miles)

- Reconductor Ft Smith – Colony 161kV line (2.22 miles)

- Reconductor Barlington – Massard 161kV line (2.8 miles)

- Reconductor Colony - Battlefield 161kV line (1.12 miles)

Based on the study results, Portfolio 1 provides an effective solution for the load addition while maintaining reliable system performance within the SPP transmission network.

Furthermore, dynamic studies were performed to assess the impact of the addition of the load on transient stability of the network which did not demonstrate any damping or voltage recovery violations.

A SCR screening study was performed to assess the strength of the grid at the Clarksville 161 kV substation. The study did not determine any system conditions under which the SCR falls below the threshold.

# Appendix

## Appendix A

## Appendix B

## Appendix C

## Appendix D

SPP Disturbance Performance Requirements: https://www.spp.org/documents/28859/spp%20disturbance%20performance%20requirements%20(twg%20approved).pdf