## Executive Summary
Executive Summary: ESR-LA for GEN-2026-SR3 Group 4 Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Electric Storage Resource Load Assessment (ESR-LA) for Electric Storage Resource (ESR) generation interconnection requests that are near their Commercial Operation Date (COD). The primary objective of this ESR-LA is to evaluate the impacts of an ESR withdrawing energy from the Transmission System. The study will identify the steady state system constraints associated with connecting the ESR to the area transmission system. The study is designed to identify the maximum allowed withdraw of the interconnecting Generating Facility without requiring additional Network Upgrades. The study analysis for the generation interconnection requests included in this ESR-LA are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. In addition, the ESR-LA projects under study and their co-located Electrically Equivalent (EE) units are listed in the Request Tab along with their MW dispatch amount for this analysis. The steady state analysis for the ESR-LA was performed consistent with Section 5 DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen. This manual contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual and ESR-LA study methodology, or contact gistudies@spp.org for more information about the study process. This ESR-LA study includes the following surplus study requests in the following cluster groups: GEN-2025-SR3 (04- SOUTHEAST)
DISIS Manual Version 4.4
https://spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
-100 MW
Models Used in Steady State Study
2022 ITP Series, DISIS-2022-001 Restudy Steady State BC Models
ERIS HVER Light: 2027
By: SPP Generator Interconnection Department
Published: August 31, 2026
The Requests tab has a Study Assumptions column that lists whether the project was under study (ESR-LA) or if it was dispatched as a co-located electrically equivalent (EE) project per the modeling methodology. Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2. Note that because the units under study are withdrawing power and have a negative MW dispatch, the TDF will also be negative. This means that the relevant TDFs for impacts will be negative instead of positive (i.e. -3% TDF for base case thermal violations). The topology is reflective of what is currently in-service from the 2024 ITP portfolio

## Revision History
Revision History
Date | Author | Change Description
2026-08-31 | SPP | ESR-LA For GEN-2026-SR3 Group 4 Posting

## Requests
Gen Number | Group | Queue | Study Assumptions | Fuel Type | Dispatch Amount (MW) | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2026-SR3 | 04 SOUTHEAST | Surplus | ESR-LA | Battery/Storage | -100 | -100 | None | ER | AEPW | Sweetwater 230kV | SPECIAL STUDY
GEN-2006-002 | 04 SOUTHEAST | ICS-2008-001 Prior Queued | EE | Wind | 0 | 0 | None | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | ICS-2008-001 Prior Queued | EE | Wind | 0 | 0 | None | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | ICS-2008-001 Prior Queued | EE | Wind | 0 | 0 | None | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | DISIS-2016-002-1 | EE | Wind | 0 | 0 | None | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Season | Most Severe Contingency | Rating Type | Rating (MVA) | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | ESR-LA-2026-SR3 | ERIS | Non-Converged | None | 27L | None
04ALL | ESR-LA-2026-SR3 | ERIS | Thermal | None | 27L | None
04ALL | ESR-LA-2026-SR3 | ERIS | Voltage | None | 27L | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Length (miles) | Upgrade Rating (MVA) | Allocated Cost | %Allocated | Total Upgrade Cost | PTDF
None

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade length (miles) | Upgrade Rating (MVA) | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
None

## All Thermal
SOLUTIONTYPE | Group | Scenario | Season | Source | Direction | MONTCOMMONNAME | Rating Type | Rating (MVA) | TDF | TC Loading % | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converged | 04ALL | 0 | 27L | N/A | N/A | None |  |  |  |  | None
Thermal | 04ALL | 1 | 27L | N/A | N/A | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | Group | Scenario | Season | Source | MONTCOMMONNAME | BC Voltage | TC Voltage | Voltage Diff | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | 04ALL | 2 | 27L | N/A | None | [7 empty] | None