## Executive Summary
Executive Summary: ESR-LA GEN-2026-SR11 Group 4 Power Flow
Pursuant to the SPP Open Access Transmission Tariff (OATT), SPP has conducted this Electric Storage Resource Load Assessment (ESR-LA) for Electric Storage Resource (ESR) generation interconnection requests. Aneden Consulting was retained by SPP to perform this ESR-LA analysis. The primary objective of this ESR-LA is to evaluate the impacts of an ESR withdrawing energy from the Transmission System. The study will identify the steady state system constraints associated with connecting the ESR to the area transmission system. The study is designed to identify the maximum allowed withdraw of the interconnecting Generating Facility without requiring additional Network Upgrades. The study analysis for the generation interconnection requests included in this ESR-LA are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The ESR-LA analysis is an approved Revision Request (RR): “RR676 Electric Storage Resource Load Assessment.” These sections can be found in Attachment V of SPP OATT and throughout BP7250, Section 5, Interconnection Service For Electric Energy Storage Resources. In addition, the ESR-LA projects under study and their co-located Electrically Equivalent (EE) units are listed in the Request Tab along with their MW dispatch amount for this analysis. The steady state analysis for the ESR-LA was performed consistent with the DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen. This manual contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual and SPP OATT, or contact specialstudies@spp.org for more information about the study process. This ESR-LA GEN-2026-SR11 study includes study requests in the following cluster groups: (04 - SOUTHEAST)
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Group 4 ESR-LA GEN-2026-SR11 analyzes the impact of interconnecting ESRs for total of:
-258 MW
Model Used in Steady State Study
2022 ITP Series, DISIS-2022-001-1 Restudy Steady State TC Models
ERIS HVER Light: 2027
By: SPP Generator Interconnection Department
Published: August 27, 2026
The Requests tab has a Study Assumptions column that lists whether the project was under study (ESR-LA) or if it was dispatched as a co-located electrically equivalent (EE) project per the modeling methodology.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Note that because the units under study are withdrawing power and have a negative MW dispatch, the TDF will also be negative. This means that the relevant TDFs for impacts will be negative instead of positive (i.e. -3% TDF for base case thermal violations).

## Revision History
Revision History
Date | Author | Change Description
2026-08-27 | SPP | ESR-LA GEN-2026-SR11 Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue | Study Assumptions | Fuel Type | Dispatch Amount (MW) | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2026-SR11 | 04 SOUTHEAST | Surplus | ESR-LA GEN-2026-SR11 | Battery/Storage | -258 | -258 | None | ER/NR | OKGE | Johnson County 345kV Substation | SPECIAL STUDY
GEN-2017-149 | 04 SOUTHEAST | DIS-17-2 | EE | Wind | 0 | N/A | N/A | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 04 SOUTHEAST | DIS-16-1 | EE | Wind | 0 | N/A | N/A | ER | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX
04ALL | ESR-LA GEN-2026-SR11 | ERIS | Thermal | None | 27L | None
04ALL | ESR-LA GEN-2026-SR11 | ERIS | Non-Converged | None | 27L | None
04ALL | ESR-LA GEN-2026-SR11 | ERIS | Voltage | None | 27L | None

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria
Non-Converged | ESR-LA GEN-2026-SR11 | 04ALL | 27L | N/A | " | None |  |  |  |  | None
Thermal | ESR-LA GEN-2026-SR11 | 04ALL | 27L | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | ESR-LA GEN-2026-SR11 | 04ALL | 27L | N/A | None | [7 empty] | None