## Executive Summary
Executive Summary: GEN-2026-PR2 Priority Process Study
Interconnection Customer GEN-2026-PR2 (Group 04) has requested a Priority System Impact Study persuant to Section 3.11 of the GIP under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new generation for a total of:
41.89 MW
The minimum cost of interconnecting GEN-2026-PR2 included in this Priority Process is estimated at:
Total Network Upgrade $0 Steady State Network Upgrade $0 Stability Network Upgrade $0 Steady State/Stability Network Upgrade $0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR2 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 05/19/2026
Costs for Wind Requests were allocated using the 27L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4616100% | SPP | Final Report Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.58436 | ER | OG&E | Tatonga 345 kV Substation | None
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | None
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | None
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | None
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | None
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | None
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | None
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | None
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | None
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | None
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | None
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation | None
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | IA PENDING
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | IA PENDING
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
ASGI-2017-013 | 01 NORTH | 23.5 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV | None
ASGI-2018-003 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV | None
ASGI-2018-006 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV | None
ASGI-2018-007 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV | None
ASGI-2018-010 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV | None
ASGI-2018-011 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV | None
GEN-2018-003 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 23.5 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 23.5 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 23.5 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | WITHDRAWN
GEN-2018-015 | 05 SOUTHWEST | 23.5 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 23.5 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-026 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 23.5 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 23.5 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 23.5 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-049 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 23.5 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 23.5 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL |  | None
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW |  | None
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW |  | None
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL |  | None
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW |  | None
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE |  | None
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW |  | None
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL |  | None
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL |  | None
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW |  | None
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP |  | None
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL |  | None
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP |  | None
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL |  | None
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW |  | None
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW |  | None
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP |  | None
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC |  | None
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC |  | None
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP |  | None
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW |  | None
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP |  | None
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | None
MPC04500 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 250 | [9 empty] | ER/NR | OTP |  | None
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0 | None
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0 | None
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | [9 empty] | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | WITHDRAWN
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | [9 empty] | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | WITHDRAWN
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | WITHDRAWN
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | NPPD | Antelope 345kV substation | WITHDRAWN
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER/NR | MIDW | ITC Post Rock 345 kV Substation | WITHDRAWN
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0 | None
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0 | None
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Patent Gate Substation 345 kV | WITHDRAWN
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP |  | None
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP |  | None
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP |  | None
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP |  | None
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP |  | None
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | WITHDRAWN
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE |  | None
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE |  | None
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW |  | None
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW |  | None
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC |  | None
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | WITHDRAWN
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC | Neset 230 kV Substation | TERMINATED
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE |  | None
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC |  | None
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC |  | None
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC |  | None
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC |  | None
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD |  | None
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS |  | None
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA |  | None
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA |  | None
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA |  | None
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation | None
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE |  | None
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS |  | None
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW |  | None
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC |  | None
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE |  | None
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0 | None
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0 | None
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0 | None
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line | None
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0 | None
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0 | None
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0 | None
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445 | None
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | None
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV | None
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation | None
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA |  | None
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA |  | None
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW |  | None
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC |  | None
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC |  | None
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA |  | None
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW |  | None
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC |  | None
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA |  | None
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC |  | None
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC |  | None
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA |  | None
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC |  | None
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC |  | None
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE |  | None
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD |  | None
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA |  | None
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC |  | None
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC |  | None
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC |  | None
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE |  | None
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE |  | None
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE |  | None
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE |  | None
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC |  | None
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC |  | None
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL |  | None
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL |  | None
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD |  | None
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD |  | None
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC |  | None
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP |  | None
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP |  | None
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP |  | None
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP |  | None
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE |  | None
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP |  | None
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP |  | None
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP |  | None
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS |  | None
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE |  | None
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | 0 | None
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0 | None
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE |  | None
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC |  | None
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC |  | None
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC |  | None
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS |  | None
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD |  | None
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS |  | None
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE |  | None
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW |  | None
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS |  | None
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS |  | None
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD |  | None
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD |  | None
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS |  | None
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS |  | None
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS |  | None
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS |  | None
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS |  | None
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA |  | None
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA |  | None
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0 | None
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD |  | None
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD |  | None
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD |  | None
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0 | None
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0 | None
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL |  | None
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS |  | None
GEN-2011-056 | 02 NEBRASKA | 6 | DIS-11-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0 | None
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0 | None
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0 | None
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE |  | None
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0 | None
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 4 | DIS-10-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE |  | None
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC |  | None
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL |  | None
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL |  | Surplus | Solar | 175 | [9 empty] | ER | SUNC |  | None
GEN-2006-044N | 02 NEBRASKA |  | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-GR1 | 04 SOUTHEAST |  | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR1 | 04 SOUTHEAST |  | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR2 | 04 SOUTHEAST |  | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR3 | 05 SOUTHWEST |  | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST |  | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR5 | 05 SOUTHWEST |  | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
HAWCT_GEN-2021-SR9 | 03 CENTRAL |  | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL |  | None

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR2 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 41.89 | 0 | Non-Convergence | Minco - Seminole 765 kV Ckt 1 New Line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 41.89 | 41.89
GEN-2026-PR2 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 41.89 | 0 | Non-Convergence | Minco - Seminole 765 kV Ckt 1 New Line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 41.89 | 41.89
GEN-2026-PR2 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 41.89 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 41.89 | N/A
GEN-2026-PR2 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 41.89 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 41.89 | N/A
GEN-2026-PR2 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 41.89 | 0 | Non-Convergence | Minco - Seminole 765 kV Ckt 1 New Line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 41.89 | 41.89
GEN-2026-PR2 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 41.89 | 0 | Non-Convergence | Minco - Seminole 765 kV Ckt 1 New Line | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 41.89 | 41.89
GEN-2026-PR2 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 41.89 | 0 | Non-Convergence | Minco - Seminole 765 kV Ckt 1 New Line | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 41.89
GEN-2026-PR2 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 41.89 | 0 | Non-Convergence | Minco - Seminole 765 kV Ckt 1 New Line | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 41.89

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR2 PSIS | ERIS | Non-Converged | None | 26SP, 29SP,29WP,29L | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS | ERIS | Thermal | None | 29WP, 29L | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 123.14 | 123.49 |  |  |  | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
04ALL | GEN-2026-PR2 PSIS | ERIS | Voltage | None | 26SP, 29SP,29WP,29L | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS CF | ERIS | Non-Converged | Non-Converged | 29WP, 29L | P23:345:OKGE:IF_MICO7302:::EHV: | [7 empty] | Minco - Seminole 765 kV Ckt 1 New Line
04ALL | GEN-2026-PR2 PSIS CF | ERIS | Thermal | None | 26SP, 29SP,29WP,29L | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS CF | ERIS | Voltage | None | 26SP, 29SP,29WP,29L | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS | ERIS | Stability | None | 29SP,29WP | [8 empty] | None
04ALL | GEN-2026-PR2 PSIS CF | ERIS | Stability | None | 29SP,29WP | [8 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR2 | GEN-2026-PR2 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 kV line 1 (37.04 miles) to a minimum rating of 2390 MVA | 0 | 0% | 81488001.7662 | 0.03716
GEN-2026-PR2 | GEN-2026-PR2 PSIS CF | 04 SOUTHEAST | 530689 | ERIS | Minco - Seminole 765 kV Ckt 1 New Line | Contingent | Build a 100-mile 765 kV Ckt 1 line from Minco to Seminole | 0 | 0% | 580000000 | N/A
GEN-2026-PR2 | GEN-2026-PR2 PSIS | 04 SOUTHEAST | TBD | ERIS | Tatonga 345 kV Substation GEN-2026-PR2 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR2 (41.89/Wind), into Tatonga 345 kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR2 | GEN-2026-PR2 PSIS | 04 SOUTHEAST | TBD | ERIS | Tatonga 345 kV Substation GEN-2026-PR2 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR2 (41.89/Wind), into Tatonga 345 kV Substation | TBD | 100% | TBD | 1
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR2 PSIS | Steady Steate | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 kV line 1 (37.04 miles) to a minimum rating of 2390 MVA | WERE | TBD | 81488001.7662
Contingent | GEN-2026-PR2 PSIS CF | Steady Steate | 04 SOUTHEAST | 2025 ITP | ERIS | Minco - Seminole 765 kV Ckt 1 New Line | 530689 | Build a 100-mile 765 kV Ckt 1 line from Minco to Seminole | TBD | 4821400% | 580000000
Interconnection | GEN-2026-PR2 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR2 PSIS | ERIS | Tatonga 345 kV Substation GEN-2026-PR2 Interconnection (TOIF) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR2 (41.89/Wind), into Tatonga 345 kV Substation | OGE | TBD | TBD
Interconnection | GEN-2026-PR2 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR2 PSIS | ERIS | Tatonga 345 kV Substation GEN-2026-PR2 Interconnection (Non-Shared NU) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR2 (41.89/Wind), into Tatonga 345 kV Substation | OGE | TBD | TBD
661488001.7662

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 503689 | Minco - Seminole 765 kV New Line | Minco - Seminole 765 kV Ckt 1 New Line | Build a 100-mile 765 kV Ckt 1 line from Minco to Seminole | 2025 ITP | Yes | N/A | 0.06207 | 4821400% | 580000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504182 | Minco 765 kV New Reactor | Minco 765 kV Reactor | Install 150 MVAR reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | 0.06207 | 4821400% | 15000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504257 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Reactor | Install 150 MVAR reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | 0.03315 | 4780500% | 15000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 503075 | Anthem - Seminole 765 kV New Line | Anthem - Seminole 765 kV Ckt 1 New Line | Build a 131.4-mile 765 kV Ckt 1 line from Anthem to Seminole | 2025 ITP | Yes | N/A | 0.03324 | 4821400% | 762120000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504180 | Anthem 765 kV New Reactor | Anthem 765 kV Reactor | Install 150 MVAR reactor at Anthem 765 kV substation | 2025 ITP | Yes | N/A | 0.03324 | 4821400% | 15000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 503353 | Southwest Shreveport - Seminole 765 kV New Line | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.2-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | 0.03315 | 4780500% | 1822360000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504255 | Line - Seminole - Southwest Shreveport 765 kV | Southwest Shreveport 765 kV Reactor | Install 150 MVAR reactor at Southwest Shreveport 765 kV substation | 2025 ITP | Yes | N/A | 0.03315 | 4780500% | 15000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 503095 | Woodward - Viola 765 kV New Line | Woodward - Viola 765 kV Ckt 1 New Line | Build a 152.4-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.09644 | 4821400% | 883920000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 502153 | Woodward 345/765 kV New Transformer | Woodward 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Woodward | 2025 ITP | Yes | N/A | 0.07361 | 4821400% | 61500000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 502156 | Woodward 345/765 kV New Transformer | Woodward 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Woodward | 2025 ITP | Yes | N/A | 0.07361 | 4821400% | 61500000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 502193 | Hitchland - Potter Co 345 kV New Line | Hitchland 345 kV Reactor | Install 52.36 MVAR reactor at Hitchland 345 kV substation | 2025 ITP | Yes | N/A | 0.03715 | 4821400% | 5236000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 500753 | Carpenter 345 kV New Capacitor | Carpenter 345 kV Capacitor | Install 90 MVAR capacitor at Carpenter 345 kV substation | 2025 ITP | Yes | N/A | 0.03715 | 4727000% | 5121041.84
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504245 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | 0.07361 | 4821400% | 13000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504243 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.07361 | 4821400% | 30000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | TBD | 504302 | Viola 765 kV New Reactor | Viola 765 kV Reactor | Install 150 MVAR reactor at Viola 765 kV substation | 2025 ITP | Yes | N/A | 0.09644 | 4821400% | 15000000
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | N/A | 0.03586 | 4600200% | 19687412
GEN-2026-PR2 | 04 SOUTHEAST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation. | DISIS-2016-002 | Yes | N/A | 0.03586 | TBD | 968409

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR2 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00182 | -0.07624 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00493 | -0.25947 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00147 | -0.025137 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00147 | -0.0441 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00027 | -0.021546 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640600 S3771 345 1 | -0.00898 | -0.898 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640600 S3771 345 1 | 0.00314 | 0.15069 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -9e-05 | -0.00774 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -9e-05 | -0.011842 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00064 | 0.0768 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00063 | 0.04977 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00247 | 0.25243 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00134 | 0.1072 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00057 | -0.28272 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00057 | -0.1596 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00818 | -2.454 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640600 S3771 345 1 | -0.00244 | -0.15128 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | -0.00013 | -0.00403 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00013 | 0.00806 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00021 | 0.0819 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00028 | 0.1512 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00024 | 0.0936 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00026 | 0.0702 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.003 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.0015 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.0015 | No
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.0025 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR2 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converged | GEN-2026-PR2 PSIS | 04ALL | 0 | 26SP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR2 PSIS | 04ALL | 0 | 29SP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR2 PSIS | 04ALL | 0 | 29WP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR2 PSIS | 04ALL | 0 | 29L | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR2 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR2 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.0566 | 111.13 | Base Case | TDF Impact | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
Thermal | GEN-2026-PR2 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR2 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.05523 | 123.14 | Base Case | TDF Impact | Rebuild line 532796 WICHITA7 345 532798 VIOLA 7 345 1
Thermal | GEN-2026-PR2 PSIS | 04ALL | 1 | 29WP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR2 PSIS | 04ALL | 1 | 29L | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR2 PSIS CF | 04ALL | 0 | 26SP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR2 PSIS CF | 04ALL | 0 | 29SP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR2 PSIS CF | 04ALL | 0 | 29WP | GEN-2026-PR2 | " | Non-Converged |  |  | 0.06559 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Non-Converged | GEN-2026-PR2 PSIS CF | 04ALL | 0 | 29L | GEN-2026-PR2 | " | Non-Converged |  |  | 0.06063 |  | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Minco - Seminole 765 kV Ckt 1 New Line
Thermal | GEN-2026-PR2 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR2 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR2 PSIS CF | 04ALL | 1 | 29WP | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR2 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR2 | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR2 PSIS | 04ALL | 2 | 26SP |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS | 04ALL | 2 | 29SP |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS | 04ALL | 2 | 29WP |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS | 04ALL | 2 | 29L |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS CF | 04ALL | 2 | 26SP |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS CF | 04ALL | 2 | 29SP |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS CF | 04ALL | 2 | 29WP |  | None | [7 empty] | None | None
Voltage | GEN-2026-PR2 PSIS CF | 04ALL | 2 | 29L |  | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles allows the controller to converge and issue is resolved.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on TANGRTP2 69.000 (514775) 69 kV Bus a. Apply fault at the TANGRTP2 69.000 (514775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TANGIER2 (514771) 69.0 kV to TANGRTP2 (514775) 69.0 kV Transmission Circuit #1 b.2. TANGRTP2 (514775) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. TANGRTP2 (514775) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 b.4. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWMAN 2 (514773) 69.0 kV to NEWGRTP2 (514776) 69.0 kV Transmission Circuit #1 b.2. NEWGRTP2 (514776) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on YUKON 2 69.000 (514816) 69 kV Bus a. Apply fault at the YUKON 2 69.000 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 (514816) 69.0 kV to SVCELRN2 (514817) 69.0 kV Transmission Circuit #1 b.2. YUKON 2 (514816) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 b.3. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on EASTERN4 138.00 (514832) 138 kV Bus a. Apply fault at the EASTERN4 138.00 (514832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 (514832) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 b.2. EASTERN4 (514832) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 b.3. DANFRTH4 (514833) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on DANFRTH4 138.00 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 138.00 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 (514833) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on BURGETT4 138.00 (514510) 138 kV Bus a. Apply fault at the BURGETT4 138.00 (514510) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 (514510) 138.0 kV to DANFRTH4 (514833) 138.0 kV Transmission Circuit #1 b.2. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on FAIRFLD4 138.00 (515468) 138 kV Bus a. Apply fault at the FAIRFLD4 138.00 (515468) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 (514834) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 b.2. SKYLINE4 (514850) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 b.3. CHISHOM4 (515374) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on TENESTP4 138.00 (514837) 138 kV Bus a. Apply fault at the TENESTP4 138.00 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to TENESTP4 (514837) 138.0 kV Transmission Circuit #1 b.2. WILSHIR4 (514836) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.3. WILSHIR4 (514836) 138.0 kV to HEFNER 4 (514848) 138.0 kV Transmission Circuit #1 b.4. TENESTP4 (514837) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.5. TENESTP4 (514837) 138.0 kV to 84TH ST4 (514843) 138.0 kV Transmission Circuit #1 b.6. 84TH ST4 (514843) 138.0 kV to BELISLE4 (514844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029GEN1 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CHTWOOD4 138.00 (514842) 138 kV Bus a. Apply fault at the CHTWOOD4 138.00 (514842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONESTP4 (514840) 138.0 kV to CHTWOOD4 (514842) 138.0 kV Transmission Circuit #1 b.2. CHTWOOD4 (514842) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on BRYANT 4 138.00 (514839) 138 kV Bus a. Apply fault at the BRYANT 4 138.00 (514839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to BRYANT 4 (514839) 138.0 kV Transmission Circuit #1 b.2. BRYANT 4 (514839) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 b.3. JONESTP4 (514840) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to SKYLINE4 (514850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to 38TH ST4 (514846) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029GEN1 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to WESTERN4 (514869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029GEN1 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 (514845) 69.0 kV to BETHANY2 (514914) 69.0 kV Transmission Circuit #1 b.2. MSTANG 2 (514860) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.3. BETHANY2 (514914) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the HSL 8G (514939), G24-252 (784534), G24-254 (784594), HSL 14G (515986), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on SKYLINE4 138.00 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 138.00 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 (514850) 138.0 kV to QUAILCK4 (514851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029GEN1 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to LNEOAK 4 (514873) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029GEN1 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to WILROGR2 (514916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the HSL 8G (514939), G24-252 (784534), G24-254 (784594), HSL 14G (515986), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relays trip G18-029GEN1 (762650) and G21-088 (766112) units. After disabling protection relays, oscillatory responses are observed in the power output of the HSL 8G (514939), G24-252 (784534), G24-254 (784594), HSL 14G (515986), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on COUNCIL4 138.00 (514865) 138 kV Bus a. Apply fault at the COUNCIL4 138.00 (514865) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to WESTOAK4 (514866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on BLOCK4 138.00 (516031) 138 kV Bus a. Apply fault at the BLOCK4 138.00 (516031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to BLOCK4 (516031) 138.0 kV Transmission Circuit #1 b.2. BLOCK4 (516031) 138.0 kV to CHAIN4 (516038) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relays trip G18-029GEN1 (762650) and G21-088 (766112) units. After disabling protection relays, oscillatory responses are observed in the power output of the HSL 8G (514939), G24-252 (784534), G24-254 (784594), HSL 14G (515986), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.2. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.3. KELLYAV4 (514501) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029GEN1 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on HOBBYLO4 138.00 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 138.00 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 (514892) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.2. HOBBYLO4 (515338) 138.0 kV to CHEMTRN4 (515367) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-088 (766112) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-120 (780574) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-088 (766112) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-088 (766112) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 4 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 4 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 (514920) 138.0 kV to CLASSEN4 (514922) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relays trip G18-029GEN1 (762650) and G21-088 (766112) units. After disabling protection relays, oscillatory responses are observed in the power output of the HSL 8G (514939), G24-252 (784534), G24-254 (784594), HSL 14G (515986), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 4 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and FRQTPAT (516071, 516088, 516089, 516090) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and FRQTPAT (516071, 516088, 516089, 516090) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650), G24-239GEN1 (784144) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650), G24-239GEN1 (784144) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Rotor angle violations is identified in G10-055 (560391). The issue is also observed in base case and is not impacted by the CQ unit. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650), REDBDPLNW0 (511974) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 (514919) 69.0 kV to SW 5TH 4 (514920) 138.0 kV to SW 5TH 1 (515763) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (764511), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (764511), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (764511), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G18-029 (762650) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MCARTHR2 (514917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the HSL 8G (514939), G24-252 (784534), G24-254 (784594), HSL 14G (515986), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_161 | 3 Phase fault on STNWAL 4 138.00 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 138.00 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_162 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_163 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to NE30TH 2 (514969) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_164 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to GRNPAST4 (514971) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_165 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips G24-154GEN1 (781594) unit. After disabling protection relay, oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_166 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_167 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_168 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_169 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_170 | 3 Phase fault on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_171 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_172 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_173 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips CNTRPL-WTG1 (531601) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_174 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips CNTRPL-WTG1 (531601) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_175 | 3 Phase fault on G24-340-TAP 345.00 (787170) 345 kV Bus a. Apply fault at the G24-340-TAP 345.00 (787170) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-340-TAP (787170) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_176 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_177 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_178 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_179 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_180 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_181 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_182 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip CNTRPL-WTG1 (531601) and SSWIND 1 (539100) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_183 | 3 Phase fault on G16133G16146345.00 (511877) 345 kV Bus a. Apply fault at the G16133G16146345.00 (511877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 (511877) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_184 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip CNTRPL-WTG1 (531601), G24-154GEN1 (781594) and SSWIND 1 (539100) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and G17-141 (760412) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 3 cycles resolves the issue. Base case was found to require the same clearing time.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and FRQTPAT (516071, 516088, 516089, 516090) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and FRQTPAT (516071, 516088, 516089, 516090) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.4. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.5. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.4. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.2. TALOGA 4 (521065) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CENT 4 138.00 (515363) 138 kV Bus a. Apply Fault at the CENT 4 138.00 (515363) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.2. CENT 4 (515363) 138.0 kV to CENT 21 (515365) 34.5 kV to CENT 11 (515364) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of G19-045 (763722). The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on OUSPRT 4 138.00 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 138.00 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.3. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G22-145 (769844) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.5. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.6. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.7. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.9. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of OUSPRTG1 (515399). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.12. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Simulation crashes following the fault. After applying steady-state mitigation measures, voltage violations are observed at POTTER_CO (523966), CROSSROADS (527669), and several nearby substations around POTTER_CO. This issue is also present in the base case, and CQ units were not found to have any impact on it. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply Fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to CHISHOLM6 (511557) 230.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IODINE-4 138.00 (514796) 138 kV Bus a. Apply Fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-145 (769884) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-145 (769884) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-145 (769884) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to WAGNWL11 (516193) 34.5 kV Two Winding #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GEN-2022-016345.00 (767301) 345 kV Bus a. Apply Fault at the GEN-2022-016345.00 (767301) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR1 (767302) 34.5 kV Two Winding #1 b.2. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR2 (767305) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply Fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on BOBCAT 7 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-145 (769884) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. FPLWNDG1 (515895) 0.7 kV to Generator # b.4. WINDFRM4 (515785) 138.0 kV to remove bus # b.5. FPLWIND4 (515786) 138.0 kV to remove bus # b.6. FPLWND11 (515787) 34.5 kV to remove bus # b.7. FLPWND21 (515790) 13.8 kV to remove bus # b.8. FPLWNDG1 (515895) 0.7 kV to remove bus # b.9. FPLWNDC1 (515896) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-145 (769884) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.3. WODWRD 2 (514782) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_OKGE_FAULT_007 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 1388 kV Bus a. Apply Fault at the WINDFRM4 (515785) 1388 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP3_P4_AEP_FAULT_001 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ST FRANC (345773) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.4. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.11. MUSKOGE7 (515224) 345.0 kV to GEN-2024-293 (785761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-111 (769204) and G23-059 (773167, 773166) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of G19-045 (763722). The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. FRNT2WD7 (516066) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of GRNTWDG1 (515660, 515661). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-111 (769204) and G23-059 (773167, 773166) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of GRNTWDG1 (515660, 515661). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.3. # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output are observed in G17-141 (760412) and G24-334 (786997, 786994) units. This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles resolved the G17-141 oscillations and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves other issues.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output are observed in G17-141 (760412) and G24-334 (786997, 786994) units. This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles resolved the G17-141 oscillations and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves other issues.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output are observed in G17-141 (760412) and G24-334 (786997, 786994) units. This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles resolved the G17-141 oscillations and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves other issues.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output are observed in G17-141 (760412) and G24-334 (786997, 786994) units. This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles resolved the G17-141 oscillations and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves other issues.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output are observed in G17-141 (760412) and G24-334 (786997, 786994) units. This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles resolved the G17-141 oscillations and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves other issues.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output are observed in G17-141 (760412) and G24-334 (786997, 786994) units. This behavior was also observed in the base case. | Reduction of simulation time step to 1/8 cycles resolved the G17-141 oscillations and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves other issues.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory reactive power is observed in G24-334 (786997, 786994) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on TANGRTP2 69.000 (514775) 69 kV Bus a. Apply fault at the TANGRTP2 69.000 (514775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TANGIER2 (514771) 69.0 kV to TANGRTP2 (514775) 69.0 kV Transmission Circuit #1 b.2. TANGRTP2 (514775) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. TANGRTP2 (514775) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 b.4. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWMAN 2 (514773) 69.0 kV to NEWGRTP2 (514776) 69.0 kV Transmission Circuit #1 b.2. NEWGRTP2 (514776) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on YUKON 2 69.000 (514816) 69 kV Bus a. Apply fault at the YUKON 2 69.000 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 (514816) 69.0 kV to SVCELRN2 (514817) 69.0 kV Transmission Circuit #1 b.2. YUKON 2 (514816) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 b.3. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on EASTERN4 138.00 (514832) 138 kV Bus a. Apply fault at the EASTERN4 138.00 (514832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 (514832) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 b.2. EASTERN4 (514832) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 b.3. DANFRTH4 (514833) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on DANFRTH4 138.00 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 138.00 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 (514833) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on BURGETT4 138.00 (514510) 138 kV Bus a. Apply fault at the BURGETT4 138.00 (514510) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 (514510) 138.0 kV to DANFRTH4 (514833) 138.0 kV Transmission Circuit #1 b.2. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on FAIRFLD4 138.00 (515468) 138 kV Bus a. Apply fault at the FAIRFLD4 138.00 (515468) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 (514834) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 b.2. SKYLINE4 (514850) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 b.3. CHISHOM4 (515374) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on TENESTP4 138.00 (514837) 138 kV Bus a. Apply fault at the TENESTP4 138.00 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to TENESTP4 (514837) 138.0 kV Transmission Circuit #1 b.2. WILSHIR4 (514836) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.3. WILSHIR4 (514836) 138.0 kV to HEFNER 4 (514848) 138.0 kV Transmission Circuit #1 b.4. TENESTP4 (514837) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.5. TENESTP4 (514837) 138.0 kV to 84TH ST4 (514843) 138.0 kV Transmission Circuit #1 b.6. 84TH ST4 (514843) 138.0 kV to BELISLE4 (514844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CHTWOOD4 138.00 (514842) 138 kV Bus a. Apply fault at the CHTWOOD4 138.00 (514842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONESTP4 (514840) 138.0 kV to CHTWOOD4 (514842) 138.0 kV Transmission Circuit #1 b.2. CHTWOOD4 (514842) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on BRYANT 4 138.00 (514839) 138 kV Bus a. Apply fault at the BRYANT 4 138.00 (514839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to BRYANT 4 (514839) 138.0 kV Transmission Circuit #1 b.2. BRYANT 4 (514839) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 b.3. JONESTP4 (514840) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to SKYLINE4 (514850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to 38TH ST4 (514846) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to WESTERN4 (514869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 (514845) 69.0 kV to BETHANY2 (514914) 69.0 kV Transmission Circuit #1 b.2. MSTANG 2 (514860) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.3. BETHANY2 (514914) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the G24-254 (784594), G24-252 (784534), G24-255 (784624), G24-254 (784594), SEMINL1G (515040), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on SKYLINE4 138.00 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 138.00 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 (514850) 138.0 kV to QUAILCK4 (514851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to LNEOAK 4 (514873) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to WILROGR2 (514916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the G24-254 (784594), G24-252 (784534), G24-255 (784624), G24-254 (784594), SEMINL1G (515040), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. After disabling protection relay, Oscillatory responses are observed in the power output of the G24-254 (784594), G24-252 (784534), G24-255 (784624), G24-254 (784594), SEMINL1G (515040), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on COUNCIL4 138.00 (514865) 138 kV Bus a. Apply fault at the COUNCIL4 138.00 (514865) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to WESTOAK4 (514866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on BLOCK4 138.00 (516031) 138 kV Bus a. Apply fault at the BLOCK4 138.00 (516031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to BLOCK4 (516031) 138.0 kV Transmission Circuit #1 b.2. BLOCK4 (516031) 138.0 kV to CHAIN4 (516038) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. After disabling protection relay, Oscillatory responses are observed in the power output of the G24-254 (784594), G24-252 (784534), G24-255 (784624), G24-254 (784594), SEMINL1G (515040), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing resolves the issue. Removal of reclosing was also required in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.2. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.3. KELLYAV4 (514501) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on HOBBYLO4 138.00 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 138.00 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 (514892) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.2. HOBBYLO4 (515338) 138.0 kV to CHEMTRN4 (515367) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-088 (766112) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-120 (780574) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-088 (766112) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-088 (766112) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 (514920) 138.0 kV to CLASSEN4 (514922) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. After disabling protection relay, Oscillatory responses are observed in the power output of the G24-254 (784594), G24-252 (784534), G24-255 (784624), G24-254 (784594), SEMINL1G (515040), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and GOODWELL (523171) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and GOODWELL (523171) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650), G24-239 (784144) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650), G24-239 (784144) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in G10-055 (560391). The issue is observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650), REDBDPLNW0 (511974) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 (514919) 69.0 kV to SW 5TH 4 (514920) 138.0 kV to SW 5TH 1 (515763) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (764511), G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (764511), G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (764511), G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and GOODWELL (523170, 523171) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MCARTHR2 (514917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the G24-254 (784594), G24-252 (784534), G24-255 (784624), G24-254 (784594), SEMINL1G (515040), SEMINL3G (515042) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_161 | 3 Phase fault on STNWAL 4 138.00 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 138.00 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_162 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_163 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to NE30TH 2 (514969) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_164 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to GRNPAST4 (514971) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_165 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips G18-029 (762650) unit. After disabling protection relay, oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_166 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_167 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_168 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_169 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_170 | 3 Phase fault on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_171 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_172 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_173 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips CNTRPL-WTG1 (531601) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_174 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips CNTRPL-WTG1 (531601) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_175 | 3 Phase fault on G24-340-TAP 345.00 (787170) 345 kV Bus a. Apply fault at the G24-340-TAP 345.00 (787170) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-340-TAP (787170) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_176 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_177 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_178 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_179 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_180 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_181 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_182 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip FLTRDG1 (539114) and SSWIND 1 (539100) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_183 | 3 Phase fault on G16133G16146345.00 (511877) 345 kV Bus a. Apply fault at the G16133G16146345.00 (511877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 (511877) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_184 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips SSWIND 1 (539100) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), SOONER2G (514806) and G17-141 (760412) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and GOODWELL (523171) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and GOODWELL (523171) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594), G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.4. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.5. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.4. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.2. TALOGA 4 (521065) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CENT 4 138.00 (515363) 138 kV Bus a. Apply Fault at the CENT 4 138.00 (515363) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.2. CENT 4 (515363) 138.0 kV to CENT 21 (515365) 34.5 kV to CENT 11 (515364) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154GEN1 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-136 (769704) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-136 (769704) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on OUSPRT 4 138.00 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 138.00 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.3. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G22-143 (769844) and G20-020 (764511) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.5. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.6. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.7. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.9. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of OUSPRTG1 (515399). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.12. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. After disabling the protection, the transient voltages at POTTER_CO (523966) and CROSSROADS (527669) exceed 1.2 p.u. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply Fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to CHISHOLM6 (511557) 230.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IODINE-4 138.00 (514796) 138 kV Bus a. Apply Fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-136 (769704) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and G22-145 (769884) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to WAGNWL11 (516193) 34.5 kV Two Winding #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GEN-2022-016345.00 (767301) 345 kV Bus a. Apply Fault at the GEN-2022-016345.00 (767301) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR1 (767302) 34.5 kV Two Winding #1 b.2. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR2 (767305) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply Fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on BOBCAT 7 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. FPLWNDG1 (515895) 0.7 kV to Generator # b.4. WINDFRM4 (515785) 138.0 kV to remove bus # b.5. FPLWIND4 (515786) 138.0 kV to remove bus # b.6. FPLWND11 (515787) 34.5 kV to remove bus # b.7. FLPWND21 (515790) 13.8 kV to remove bus # b.8. FPLWNDG1 (515895) 0.7 kV to remove bus # b.9. FPLWNDC1 (515896) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.3. WODWRD 2 (514782) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_OKGE_FAULT_007 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 1388 kV Bus a. Apply Fault at the WINDFRM4 (515785) 1388 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP3_P4_AEP_FAULT_001 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ST FRANC (345773) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.4. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.11. MUSKOGE7 (515224) 345.0 kV to GEN-2024-293 (785761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-111 (769204, 769206) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999).The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. FRNT2WD7 (516066) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-111 (769204, 769206) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.3. # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P1_LOCAL_FAULT_165 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips G24-154GEN1 (781594) unit. After disabling protection relay, oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P1_LOCAL_FAULT_175 | 3 Phase fault on G24-340-TAP 345.00 (787170) 345 kV Bus a. Apply fault at the G24-340-TAP 345.00 (787170) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-340-TAP (787170) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of G19-045 (763722). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.12. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Simulation crashes following the fault. After applying steady-state mitigation measures, voltage violations are observed at POTTER_CO (523966), CROSSROADS (527669), and several nearby substations around POTTER_CO. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP3_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29S | Base | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of G19-045 (763722). | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_165 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips G18-029 (762650) unit. After disabling protection relay, oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_175 | 3 Phase fault on G24-340-TAP 345.00 (787170) 345 kV Bus a. Apply fault at the G24-340-TAP 345.00 (787170) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-340-TAP (787170) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), SOONER2G (514806) and G17-141 (760412) units. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduction of clearing time to 2 cycles and removal of reclosing resolves the issue. Similar requirements are also observed in the base case.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP3_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999) | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. FRNT2WD7 (516066) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G24-334 (786994, 786999). | No mitigation required.
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on TANGRTP2 69.000 (514775) 69 kV Bus a. Apply fault at the TANGRTP2 69.000 (514775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TANGIER2 (514771) 69.0 kV to TANGRTP2 (514775) 69.0 kV Transmission Circuit #1 b.2. TANGRTP2 (514775) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. TANGRTP2 (514775) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 b.4. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWMAN 2 (514773) 69.0 kV to NEWGRTP2 (514776) 69.0 kV Transmission Circuit #1 b.2. NEWGRTP2 (514776) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on YUKON 2 69.000 (514816) 69 kV Bus a. Apply fault at the YUKON 2 69.000 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 (514816) 69.0 kV to SVCELRN2 (514817) 69.0 kV Transmission Circuit #1 b.2. YUKON 2 (514816) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 b.3. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on EASTERN4 138.00 (514832) 138 kV Bus a. Apply fault at the EASTERN4 138.00 (514832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 (514832) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 b.2. EASTERN4 (514832) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 b.3. DANFRTH4 (514833) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on DANFRTH4 138.00 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 138.00 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 (514833) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on BURGETT4 138.00 (514510) 138 kV Bus a. Apply fault at the BURGETT4 138.00 (514510) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 (514510) 138.0 kV to DANFRTH4 (514833) 138.0 kV Transmission Circuit #1 b.2. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on FAIRFLD4 138.00 (515468) 138 kV Bus a. Apply fault at the FAIRFLD4 138.00 (515468) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 (514834) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 b.2. SKYLINE4 (514850) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 b.3. CHISHOM4 (515374) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on TENESTP4 138.00 (514837) 138 kV Bus a. Apply fault at the TENESTP4 138.00 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to TENESTP4 (514837) 138.0 kV Transmission Circuit #1 b.2. WILSHIR4 (514836) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.3. WILSHIR4 (514836) 138.0 kV to HEFNER 4 (514848) 138.0 kV Transmission Circuit #1 b.4. TENESTP4 (514837) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.5. TENESTP4 (514837) 138.0 kV to 84TH ST4 (514843) 138.0 kV Transmission Circuit #1 b.6. 84TH ST4 (514843) 138.0 kV to BELISLE4 (514844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CHTWOOD4 138.00 (514842) 138 kV Bus a. Apply fault at the CHTWOOD4 138.00 (514842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONESTP4 (514840) 138.0 kV to CHTWOOD4 (514842) 138.0 kV Transmission Circuit #1 b.2. CHTWOOD4 (514842) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on BRYANT 4 138.00 (514839) 138 kV Bus a. Apply fault at the BRYANT 4 138.00 (514839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to BRYANT 4 (514839) 138.0 kV Transmission Circuit #1 b.2. BRYANT 4 (514839) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 b.3. JONESTP4 (514840) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to SKYLINE4 (514850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to 38TH ST4 (514846) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to WESTERN4 (514869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 (514845) 69.0 kV to BETHANY2 (514914) 69.0 kV Transmission Circuit #1 b.2. MSTANG 2 (514860) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.3. BETHANY2 (514914) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on SKYLINE4 138.00 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 138.00 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 (514850) 138.0 kV to QUAILCK4 (514851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to LNEOAK 4 (514873) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to WILROGR2 (514916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on COUNCIL4 138.00 (514865) 138 kV Bus a. Apply fault at the COUNCIL4 138.00 (514865) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to WESTOAK4 (514866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on BLOCK4 138.00 (516031) 138 kV Bus a. Apply fault at the BLOCK4 138.00 (516031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to BLOCK4 (516031) 138.0 kV Transmission Circuit #1 b.2. BLOCK4 (516031) 138.0 kV to CHAIN4 (516038) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.2. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.3. KELLYAV4 (514501) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on HOBBYLO4 138.00 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 138.00 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 (514892) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.2. HOBBYLO4 (515338) 138.0 kV to CHEMTRN4 (515367) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 (514920) 138.0 kV to CLASSEN4 (514922) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 (514919) 69.0 kV to SW 5TH 4 (514920) 138.0 kV to SW 5TH 1 (515763) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MCARTHR2 (514917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_161 | 3 Phase fault on STNWAL 4 138.00 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 138.00 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_162 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_163 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to NE30TH 2 (514969) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_164 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to GRNPAST4 (514971) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_165 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_166 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_167 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_168 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_169 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_170 | 3 Phase fault on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_171 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_172 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_173 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_174 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_175 | 3 Phase fault on G24-340-TAP 345.00 (787170) 345 kV Bus a. Apply fault at the G24-340-TAP 345.00 (787170) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-340-TAP (787170) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_176 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_177 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_178 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_179 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_180 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_181 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_182 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_183 | 3 Phase fault on G16133G16146345.00 (511877) 345 kV Bus a. Apply fault at the G16133G16146345.00 (511877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 (511877) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_184 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.4. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.5. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.4. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.2. TALOGA 4 (521065) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CENT 4 138.00 (515363) 138 kV Bus a. Apply Fault at the CENT 4 138.00 (515363) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.2. CENT 4 (515363) 138.0 kV to CENT 21 (515365) 34.5 kV to CENT 11 (515364) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on OUSPRT 4 138.00 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 138.00 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.3. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.5. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.6. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.7. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.9. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.12. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply Fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to CHISHOLM6 (511557) 230.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IODINE-4 138.00 (514796) 138 kV Bus a. Apply Fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to WAGNWL11 (516193) 34.5 kV Two Winding #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GEN-2022-016345.00 (767301) 345 kV Bus a. Apply Fault at the GEN-2022-016345.00 (767301) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR1 (767302) 34.5 kV Two Winding #1 b.2. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR2 (767305) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply Fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on BOBCAT 7 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. FPLWNDG1 (515895) 0.7 kV to Generator # b.4. WINDFRM4 (515785) 138.0 kV to remove bus # b.5. FPLWIND4 (515786) 138.0 kV to remove bus # b.6. FPLWND11 (515787) 34.5 kV to remove bus # b.7. FLPWND21 (515790) 13.8 kV to remove bus # b.8. FPLWNDG1 (515895) 0.7 kV to remove bus # b.9. FPLWNDC1 (515896) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.3. WODWRD 2 (514782) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_OKGE_FAULT_007 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 1388 kV Bus a. Apply Fault at the WINDFRM4 (515785) 1388 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP3_P4_AEP_FAULT_001 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ST FRANC (345773) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.4. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.11. MUSKOGE7 (515224) 345.0 kV to GEN-2024-293 (785761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. FRNT2WD7 (516066) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.3. # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on TANGRTP2 69.000 (514775) 69 kV Bus a. Apply fault at the TANGRTP2 69.000 (514775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TANGIER2 (514771) 69.0 kV to TANGRTP2 (514775) 69.0 kV Transmission Circuit #1 b.2. TANGRTP2 (514775) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. TANGRTP2 (514775) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 b.4. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWMAN 2 (514773) 69.0 kV to NEWGRTP2 (514776) 69.0 kV Transmission Circuit #1 b.2. NEWGRTP2 (514776) 69.0 kV to WDNITRO2 (514779) 69.0 kV Transmission Circuit #1 b.3. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on YUKON 2 69.000 (514816) 69 kV Bus a. Apply fault at the YUKON 2 69.000 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 (514816) 69.0 kV to SVCELRN2 (514817) 69.0 kV Transmission Circuit #1 b.2. YUKON 2 (514816) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 b.3. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV to REFLEK 2 (516209) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on EASTERN4 138.00 (514832) 138 kV Bus a. Apply fault at the EASTERN4 138.00 (514832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 (514832) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 b.2. EASTERN4 (514832) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 b.3. DANFRTH4 (514833) 138.0 kV to HAFERSB4 (515469) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on DANFRTH4 138.00 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 138.00 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 (514833) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on BURGETT4 138.00 (514510) 138 kV Bus a. Apply fault at the BURGETT4 138.00 (514510) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 (514510) 138.0 kV to DANFRTH4 (514833) 138.0 kV Transmission Circuit #1 b.2. BURGETT4 (514510) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to RNDBARN4 (515461) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on FAIRFLD4 138.00 (515468) 138 kV Bus a. Apply fault at the FAIRFLD4 138.00 (515468) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 (514834) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 b.2. SKYLINE4 (514850) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 b.3. CHISHOM4 (515374) 138.0 kV to FAIRFLD4 (515468) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on TENESTP4 138.00 (514837) 138 kV Bus a. Apply fault at the TENESTP4 138.00 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to TENESTP4 (514837) 138.0 kV Transmission Circuit #1 b.2. WILSHIR4 (514836) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.3. WILSHIR4 (514836) 138.0 kV to HEFNER 4 (514848) 138.0 kV Transmission Circuit #1 b.4. TENESTP4 (514837) 138.0 kV to TENNESE4 (514838) 138.0 kV Transmission Circuit #1 b.5. TENESTP4 (514837) 138.0 kV to 84TH ST4 (514843) 138.0 kV Transmission Circuit #1 b.6. 84TH ST4 (514843) 138.0 kV to BELISLE4 (514844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CHTWOOD4 138.00 (514842) 138 kV Bus a. Apply fault at the CHTWOOD4 138.00 (514842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONESTP4 (514840) 138.0 kV to CHTWOOD4 (514842) 138.0 kV Transmission Circuit #1 b.2. CHTWOOD4 (514842) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 b.3. ARCADIA4 (514907) 138.0 kV to LGARBER4 (515465) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on BRYANT 4 138.00 (514839) 138 kV Bus a. Apply fault at the BRYANT 4 138.00 (514839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to BRYANT 4 (514839) 138.0 kV Transmission Circuit #1 b.2. BRYANT 4 (514839) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 b.3. JONESTP4 (514840) 138.0 kV to ACORN 4 (515459) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV to SKYLINE4 (514850) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to 38TH ST4 (514846) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV to WESTERN4 (514869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 (514845) 69.0 kV to BETHANY2 (514914) 69.0 kV Transmission Circuit #1 b.2. MSTANG 2 (514860) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.3. BETHANY2 (514914) 69.0 kV to WODLAWN2 (514915) 69.0 kV Transmission Circuit #1 b.4. MSTANG 2 (514860) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on SKYLINE4 138.00 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 138.00 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 (514850) 138.0 kV to QUAILCK4 (514851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to LNEOAK 4 (514873) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to WILROGR2 (514916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on COUNCIL4 138.00 (514865) 138 kV Bus a. Apply fault at the COUNCIL4 138.00 (514865) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to WESTOAK4 (514866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on BLOCK4 138.00 (516031) 138 kV Bus a. Apply fault at the BLOCK4 138.00 (516031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COUNCIL4 (514865) 138.0 kV to BLOCK4 (516031) 138.0 kV Transmission Circuit #1 b.2. BLOCK4 (516031) 138.0 kV to CHAIN4 (516038) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.2. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 b.3. KELLYAV4 (514501) 138.0 kV to MEMRIAL4 (514835) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on HOBBYLO4 138.00 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 138.00 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 (514892) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.2. HOBBYLO4 (515338) 138.0 kV to CHEMTRN4 (515367) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on JNSKAMO4 138.00 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 138.00 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 (514906) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 (514920) 138.0 kV to CLASSEN4 (514922) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on SW 5TH 4 138.00 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 138.00 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 (514919) 69.0 kV to SW 5TH 4 (514920) 138.0 kV to SW 5TH 1 (515763) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on MEMRIAL4 138.00 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 138.00 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 (514835) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BELISLE4 138.00 (514844) 138 kV Bus a. Apply fault at the BELISLE4 138.00 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 (514844) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on KELLYAV4 138.00 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 138.00 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 (514501) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on MSTANG 2 69.000 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 69.000 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MCARTHR2 (514917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_161 | 3 Phase fault on STNWAL 4 138.00 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 138.00 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 (514870) 138.0 kV to REMNGPK4 (514874) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_162 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to CHISHOM4 (515374) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_163 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to NE30TH 2 (514969) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_164 | 3 Phase fault on REMNGPK4 138.00 (514874) 138 kV Bus a. Apply fault at the REMNGPK4 138.00 (514874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMNGPK4 (514874) 138.0 kV to GRNPAST4 (514971) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_165 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_166 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_167 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_168 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_169 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_170 | 3 Phase fault on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_171 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_172 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_173 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_174 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_175 | 3 Phase fault on G24-340-TAP 345.00 (787170) 345 kV Bus a. Apply fault at the G24-340-TAP 345.00 (787170) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G24-340-TAP (787170) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_176 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_177 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_178 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_179 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_180 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_181 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_182 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_183 | 3 Phase fault on G16133G16146345.00 (511877) 345 kV Bus a. Apply fault at the G16133G16146345.00 (511877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 (511877) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_184 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WODWRD 2 69.000 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 69.000 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.5. WODWRD 2 (514782) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.4. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.5. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to G23-104-TAP (774060) 138.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.4. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.2. TALOGA 4 (521065) 138.0 kV to G20-010-TAP (765215) 138.0 kV Transmission Circuit #1 b.3. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.4. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 b.2. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CENT 4 138.00 (515363) 138 kV Bus a. Apply Fault at the CENT 4 138.00 (515363) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.2. CENT 4 (515363) 138.0 kV to CENT 21 (515365) 34.5 kV to CENT 11 (515364) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on OUSPRT 4 138.00 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 138.00 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.3. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD1S (514899) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD1G (514910) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. REDBUD3S (514905) 18.0 kV to REDBUD 7 (514909) 345.0 kV to REDBUD3G (514912) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.2. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.5. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.6. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.7. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.9. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515795) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.12. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply Fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to CHISHOLM6 (511557) 230.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IODINE-4 138.00 (514796) 138 kV Bus a. Apply Fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515799) 13.8 kV Three Winding #3 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BOBCAT 7 (516106) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to WAGNWL11 (516193) 34.5 kV Two Winding #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GEN-2022-016345.00 (767301) 345 kV Bus a. Apply Fault at the GEN-2022-016345.00 (767301) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR1 (767302) 34.5 kV Two Winding #1 b.2. GEN-2022-016 (767301) 345.0 kV to G22-016XFMR2 (767305) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply Fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDPST 4 (515425) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on BOBCAT 7 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. FPLWNDG1 (515895) 0.7 kV to Generator # b.4. WINDFRM4 (515785) 138.0 kV to remove bus # b.5. FPLWIND4 (515786) 138.0 kV to remove bus # b.6. FPLWND11 (515787) 34.5 kV to remove bus # b.7. FLPWND21 (515790) 13.8 kV to remove bus # b.8. FPLWNDG1 (515895) 0.7 kV to remove bus # b.9. FPLWNDC1 (515896) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. G24-344-TAP (787290) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #2 b.3. WODWRD 2 (514782) 69.0 kV to CEDARAV2 (514781) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_OKGE_FAULT_007 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 1388 kV Bus a. Apply Fault at the WINDFRM4 (515785) 1388 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.3. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP3_P4_AEP_FAULT_001 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to G24-340-TAP (787170) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ST FRANC (345773) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.4. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.11. MUSKOGE7 (515224) 345.0 kV to GEN-2024-293 (785761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.3. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.3. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. FRNT2WD7 (516066) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.3. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR2 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.3. # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR2 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.6018 | 14.6929 | 0.0911
GEN-2026-PR2 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 19.0806 | 19.1704 | 0.0898
GEN-2026-PR2 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.9952 | 13.0359 | 0.0407
GEN-2026-PR2 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 43.8199 | 43.8515 | 0.0316
GEN-2026-PR2 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 23.7221 | 23.7535 | 0.0314
GEN-2026-PR2 | 04 SOUTHEAST | 767221 | GEN-2022-012 | 345 | 23.3431 | 23.3735 | 0.0304
GEN-2026-PR2 | 04 SOUTHEAST | 767301 | GEN-2022-016 | 345 | 23.3653 | 23.3957 | 0.0304
GEN-2026-PR2 | 04 SOUTHEAST | 767321 | GEN-2022-017 | 345 | 23.001 | 23.0305 | 0.0295
GEN-2026-PR2 | 04 SOUTHEAST | 784591 | GEN-2024-254 | 345 | 39.0224 | 39.047 | 0.0246
GEN-2026-PR2 | 04 SOUTHEAST | 784590 | GEN-2024-254 | 345 | 38.4913 | 38.5156 | 0.0243
GEN-2026-PR2 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 20.508 | 20.5314 | 0.0234
GEN-2026-PR2 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 9.0284 | 9.0472 | 0.0188
GEN-2026-PR2 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 43.6219 | 43.6385 | 0.0166
GEN-2026-PR2 | 04 SOUTHEAST | 784141 | GEN-2024-239 | 345 | 42.9111 | 42.9271 | 0.016
GEN-2026-PR2 | 04 SOUTHEAST | 784531 | GEN-2024-252 | 345 | 38.8648 | 38.8777 | 0.0129
GEN-2026-PR2 | 04 SOUTHEAST | 784530 | GEN-2024-252 | 345 | 38.3357 | 38.3485 | 0.0128
GEN-2026-PR2 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 39.9382 | 39.9508 | 0.0126
GEN-2026-PR2 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.4558 | 16.4672 | 0.0114
GEN-2026-PR2 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 16.4253 | 16.4367 | 0.0114
GEN-2026-PR2 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 16.3956 | 16.4069 | 0.0113
GEN-2026-PR2 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.7307 | 14.7416 | 0.0109
GEN-2026-PR2 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.4601 | 26.4709 | 0.0108
GEN-2026-PR2 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 12.8482 | 12.8564 | 0.0082
GEN-2026-PR2 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 13.1693 | 13.1766 | 0.0073
GEN-2026-PR2 | 04 SOUTHEAST | 562020 | PRSCRKII 7 | 345 | 11.6697 | 11.6764 | 0.0067
GEN-2026-PR2 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 16.3395 | 16.3458 | 0.0063
GEN-2026-PR2 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 51.0863 | 51.0919 | 0.0056
GEN-2026-PR2 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 10.6951 | 10.7005 | 0.0054
GEN-2026-PR2 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.1119 | 19.1165 | 0.0046
GEN-2026-PR2 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 28.1974 | 28.2019 | 0.0045
GEN-2026-PR2 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 49.2644 | 49.2689 | 0.0045
GEN-2026-PR2 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 35.528 | 35.5322 | 0.0042
GEN-2026-PR2 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 34.9816 | 34.9857 | 0.0041
GEN-2026-PR2 | 04 SOUTHEAST | 784621 | GEN-2024-255 | 345 | 26.253 | 26.2569 | 0.0039
GEN-2026-PR2 | 04 SOUTHEAST | 784620 | GEN-2024-255 | 345 | 25.8887 | 25.8925 | 0.0038
GEN-2026-PR2 | 04 SOUTHEAST | 780991 | GEN-2024-134 | 345 | 12.1299 | 12.1333 | 0.0034
GEN-2026-PR2 | 04 SOUTHEAST | 781021 | GEN-2024-135 | 345 | 12.1299 | 12.1333 | 0.0034
GEN-2026-PR2 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 12.5569 | 12.5602 | 0.0033
GEN-2026-PR2 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 33.316 | 33.3192 | 0.0032
GEN-2026-PR2 | 04 SOUTHEAST | 776821 | GEN-2023-102 | 345 | 11.5852 | 11.5884 | 0.0032
GEN-2026-PR2 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 19.0494 | 19.0524 | 0.003
GEN-2026-PR2 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 19.0444 | 19.0474 | 0.003
GEN-2026-PR2 | 04 SOUTHEAST | 585420 | SUBST HS | 345 | 8.1934 | 8.1964 | 0.003
GEN-2026-PR2 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 26.7156 | 26.7184 | 0.0028
GEN-2026-PR2 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 11.3655 | 11.3683 | 0.0028
GEN-2026-PR2 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 26.5968 | 26.5996 | 0.0028
GEN-2026-PR2 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.3066 | 18.3093 | 0.0027
GEN-2026-PR2 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 25.7503 | 25.7529 | 0.0026
GEN-2026-PR2 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 25.6952 | 25.6977 | 0.0025
GEN-2026-PR2 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 40.2875 | 40.29 | 0.0025
GEN-2026-PR2 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 12.5357 | 12.5381 | 0.0024
GEN-2026-PR2 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 35.1633 | 35.1657 | 0.0024
GEN-2026-PR2 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 36.5555 | 36.5578 | 0.0023
GEN-2026-PR2 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 44.3677 | 44.37 | 0.0023
GEN-2026-PR2 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 35.0715 | 35.0737 | 0.0022
GEN-2026-PR2 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 16.6085 | 16.6107 | 0.0022
GEN-2026-PR2 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 31.0194 | 31.0215 | 0.0021
GEN-2026-PR2 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 42.1751 | 42.1772 | 0.0021
GEN-2026-PR2 | 04 SOUTHEAST | 539871 | PIXLEY-SOLAR | 345 | 15.8701 | 15.8722 | 0.0021
GEN-2026-PR2 | 04 SOUTHEAST | 516074 | PONDRSA7 | 345 | 9.9129 | 9.9149 | 0.002
GEN-2026-PR2 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 48.9984 | 49.0003 | 0.0019
GEN-2026-PR2 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 47.6127 | 47.6146 | 0.0019
GEN-2026-PR2 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 10.7535 | 10.7553 | 0.0018
GEN-2026-PR2 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 32.7667 | 32.7684 | 0.0017
GEN-2026-PR2 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 16.1328 | 16.1345 | 0.0017
GEN-2026-PR2 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 16.1328 | 16.1345 | 0.0017
GEN-2026-PR2 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 44.3163 | 44.318 | 0.0017
GEN-2026-PR2 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 14.4342 | 14.4358 | 0.0016
GEN-2026-PR2 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 12.8321 | 12.8337 | 0.0016
GEN-2026-PR2 | 04 SOUTHEAST | 515374 | CHISHOM4 | 138 | 32.0212 | 32.0228 | 0.0016
GEN-2026-PR2 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 14.3478 | 14.3493 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.3235 | 20.325 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 14.7287 | 14.7302 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 31.288 | 31.2895 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 9.9965 | 9.998 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 523040 | OLYMPIA7 | 345 | 12.6112 | 12.6127 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 781591 | GEN-2024-154 | 345 | 14.2939 | 14.2954 | 0.0015
GEN-2026-PR2 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 30.3521 | 30.3535 | 0.0014
GEN-2026-PR2 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.9373 | 28.9387 | 0.0014
GEN-2026-PR2 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 12.8964 | 12.8977 | 0.0013
GEN-2026-PR2 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 9.3557 | 9.357 | 0.0013
GEN-2026-PR2 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 32.6607 | 32.6619 | 0.0012
GEN-2026-PR2 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 24.5754 | 24.5766 | 0.0012
GEN-2026-PR2 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 31.1057 | 31.1069 | 0.0012
GEN-2026-PR2 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.313 | 9.3142 | 0.0012
GEN-2026-PR2 | 04 SOUTHEAST | 777361 | GEN-2024-013 | 345 | 22.6387 | 22.6399 | 0.0012
GEN-2026-PR2 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 22.6847 | 22.6858 | 0.0011
GEN-2026-PR2 | 04 SOUTHEAST | 523041 | FRWLN7 | 345 | 10.4283 | 10.4294 | 0.0011
GEN-2026-PR2 | 04 SOUTHEAST | 515800 | GEN-2021-048 | 115 | 23.3561 | 23.3572 | 0.0011
GEN-2026-PR2 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 11.5552 | 11.5562 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 21.8246 | 21.8256 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 777368 | GEN-2024-C1 | 345 | 20.4179 | 20.4189 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 777369 | GEN-2024-C2 | 345 | 20.4179 | 20.4189 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 35.753 | 35.754 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 21.9661 | 21.9671 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 786601 | GEN-2024-321 | 345 | 34.3007 | 34.3017 | 0.001
GEN-2026-PR2 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 31.5082 | 31.5091 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 23.7366 | 23.7375 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 32.039 | 32.0399 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 20.7883 | 20.7892 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 20.6728 | 20.6737 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 11.8948 | 11.8957 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.6076 | 15.6085 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 12.0687 | 12.0696 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 13.4404 | 13.4413 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.7554 | 23.7563 | 0.0009
GEN-2026-PR2 | 04 SOUTHEAST | 533069 | BUFFALO4 | 138 | 32.0453 | 32.0461 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 523019 | OSLO-SYLVIE7 | 345 | 9.148 | 9.1488 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 523020 | SYLVIE 7 | 345 | 9.148 | 9.1488 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 523030 | OLSO 7 | 345 | 9.148 | 9.1488 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 774060 | G23-104-TAP | 138 | 11.3356 | 11.3364 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 774061 | GEN-2023-104 | 138 | 11.2491 | 11.2499 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 23.9738 | 23.9746 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 539804 | GEN-2021-043 | 115 | 18.149 | 18.1498 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 33.4404 | 33.4412 | 0.0008
GEN-2026-PR2 | 04 SOUTHEAST | 516192 | WAGNWTIE7 | 345 | 16.4304 | 16.4311 | 0.0007
GEN-2026-PR2 | 04 SOUTHEAST | 516198 | WAGNWL7 | 345 | 16.4304 | 16.4311 | 0.0007
GEN-2026-PR2 | 04 SOUTHEAST | 516207 | GADWALL7 | 345 | 16.4304 | 16.4311 | 0.0007
GEN-2026-PR2 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.4188 | 17.4195 | 0.0007
GEN-2026-PR2 | 04 SOUTHEAST | 765530 | GEN-2021-025 | 138 | 17.9431 | 17.9438 | 0.0007
GEN-2026-PR2 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.6117 | 19.6123 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 13.2876 | 13.2882 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.3386 | 10.3392 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9561 | 11.9567 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.8428 | 7.8434 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 516036 | TRAV3WD7 | 345 | 7.4923 | 7.4929 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.9662 | 17.9668 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 50.2064 | 50.207 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.3505 | 22.3511 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.3537 | 17.3543 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 16.1521 | 16.1527 | 0.0006
GEN-2026-PR2 | 04 SOUTHEAST | 511587 | MATO 7 | 345 | 10.7153 | 10.7158 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.2699 | 10.2704 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.6297 | 13.6302 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 516086 | TRAV3WZ7 | 345 | 6.9604 | 6.9609 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 511592 | SEVEN7A_HV | 345 | 10.1826 | 10.1831 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 511599 | SEVEN7AB2 | 345 | 10.1826 | 10.1831 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 511608 | SEVEN7AB3 | 345 | 10.1826 | 10.1831 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.4023 | 20.4028 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.6529 | 13.6534 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 515481 | STHLAKE4 | 138 | 23.1381 | 23.1386 | 0.0005
GEN-2026-PR2 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 18.2321 | 18.2325 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 24.0675 | 24.0679 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 11.6237 | 11.6241 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 10.9865 | 10.9869 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 7.1529 | 7.1533 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 7.1372 | 7.1376 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 20.7116 | 20.712 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 16.7632 | 16.7636 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.7959 | 18.7963 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 22.0445 | 22.0449 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.6667 | 12.6671 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 515802 | GEN-2021-108 | 345 | 35.8801 | 35.8805 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.7255 | 10.7259 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 18.5514 | 18.5518 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.9551 | 6.9555 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 10.7932 | 10.7936 | 0.0004
GEN-2026-PR2 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.3084 | 19.3087 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 16.6806 | 16.6809 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 515646 | GRNTWD 7 | 345 | 11.0941 | 11.0944 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 523103 | NOBLE_WND 3 | 115 | 9.8684 | 9.8687 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.8548 | 10.8551 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 539813 | GEN-2021-048 | 115 | 9.4784 | 9.4787 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.3318 | 8.3321 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 516045 | TRAV2WD7 | 345 | 5.9797 | 5.98 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 516087 | TRAV22Z7 | 345 | 5.6457 | 5.646 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 516107 | TRAV21Z7 | 345 | 5.646 | 5.6463 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 516109 | TRAV12Z7 | 345 | 5.2469 | 5.2472 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 7.8473 | 7.8476 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 8.2827 | 8.283 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 12.0557 | 12.056 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 523959 | POTTER_CO 6 | 230 | 27.3358 | 27.3361 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 539823 | IRONSTAR7 | 345 | 8.655 | 8.6553 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 9.1397 | 9.14 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 780571 | GEN-2024-120 | 138 | 20.9233 | 20.9236 | 0.0003
GEN-2026-PR2 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6793 | 10.6795 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 511541 | DEMPSEYR POI | 230 | 9.3708 | 9.371 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 7.7976 | 7.7978 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 765480 | GEN-2021-019 | 345 | 13.5186 | 13.5188 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.8354 | 6.8356 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.5089 | 6.5091 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 764980 | GEN-2020-008 | 345 | 6.5089 | 6.5091 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 8.0043 | 8.0045 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 511920 | CDW-SUB | 345 | 12.1561 | 12.1563 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 511992 | HVBUS | 345 | 14.0233 | 14.0235 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 9.1898 | 9.19 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 516054 | TRAV1WD7 | 345 | 5.5303 | 5.5305 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.4808 | 10.481 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 523131 | GRPLNS-HV2-3 | 115 | 9.0737 | 9.0739 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 523966 | POTTER_CO 9 | 765 | 8.1391 | 8.1393 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 523979 | HARRNG_EST 6 | 230 | 30.0246 | 30.0248 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 524010 | ROLLHILLS 6 | 230 | 22.874 | 22.8742 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 16.8654 | 16.8656 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 539824 | IRS7 115 KV | 115 | 12.6363 | 12.6365 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 7.3018 | 7.302 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 763670 | GEN-2019-030 | 345 | 8.2232 | 8.2234 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 765490 | GEN-2021-021 | 345 | 6.1496 | 6.1498 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.6968 | 7.697 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 516108 | TRAV11Z7 | 345 | 5.2471 | 5.2473 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 7.5676 | 7.5678 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 539816 | GEN-2021-108 | 345 | 9.8411 | 9.8413 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 763677 | G19-030-TAP | 345 | 9.8592 | 9.8594 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 782641 | GEN-2024-189 | 345 | 8.5796 | 8.5798 | 0.0002
GEN-2026-PR2 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 54.79 | 54.7901 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 66.1755 | 66.1756 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 32.1967 | 32.1968 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.894 | 30.8941 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 55.7716 | 55.7717 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 527656 | CROSSROAD | 345 | 16.8178 | 16.8179 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.3724 | 8.3725 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.3724 | 8.3725 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 527598 | SAGA_NDCOL 7 | 345 | 11.5026 | 11.5027 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 527601 | SAGA_NCOL 7 | 345 | 11.5026 | 11.5027 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 523130 | GRPLNS-HV4-3 | 115 | 6.8562 | 6.8563 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 527669 | CROSSROADS 9 | 765 | 7.2499 | 7.25 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.9235 | 5.9236 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.1696 | 23.1697 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 31.0035 | 31.0036 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 24.14 | 24.1401 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 17.3715 | 17.3716 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 7.0404 | 7.0405 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4947 | 10.4948 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 6.784 | 6.7841 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 511544 | DEMPSEYR_HV | 230 | 5.4287 | 5.4288 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 10.2813 | 10.2814 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 5.772 | 5.7721 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 514779 | WDNITRO2 | 69 | 5.0377 | 5.0378 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 6.0309 | 6.031 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.4238 | 5.4239 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 515786 | GEN-2021-043 | 115 | 6.6134 | 6.6135 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.6693 | 13.6694 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 6.1483 | 6.1484 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 8.3003 | 8.3004 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 9.0509 | 9.051 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 523323 | MCDWL_CREEK6 | 230 | 9.9178 | 9.9179 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 525549 | TOLK 7 | 345 | 13.7913 | 13.7914 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 525839 | G17-151TAP | 345 | 10.158 | 10.1581 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 16.7088 | 16.7089 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 525851 | ELK_CT3 7 | 345 | 16.677 | 16.6771 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 532785 | PRATTWF7 | 345 | 4.9373 | 4.9374 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 18.3294 | 18.3295 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 784050 | G24-236-TAP | 345 | 12.329 | 12.3291 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 784051 | GEN-2024-236 | 345 | 10.3139 | 10.314 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 784471 | GEN-2024-250 | 345 | 20.655 | 20.6551 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 787200 | GEN-2024-341 | 345 | 19.9785 | 19.9786 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 5.2051 | 5.2052 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 521127 | BOILSPR4 | 138 | 8.1078 | 8.1079 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 34.9553 | 34.9554 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 53.0163 | 53.0164 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 511877 | G16133G16146 | 345 | 34.9553 | 34.9554 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 35.2668 | 35.2669 | 0.0001
GEN-2026-PR2 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 22.42 | 22.42 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.6387 | 34.6387 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 21.6504 | 21.6504 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 21.0787 | 21.0787 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 5.0492 | 5.0492 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 7.0813 | 7.0813 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511726 | ZONE-5 SUB | 345 | 7.0314 | 7.0314 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511878 | G16133_765TN | 765 | 9.4823 | 9.4823 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511879 | G16133_765R1 | 765 | 9.4823 | 9.4823 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511880 | G16133_765R2 | 765 | 4.5954 | 4.5954 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511881 | G16133_765R3 | 765 | 3.661 | 3.661 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511882 | G16133_765CS | 765 | 3.661 | 3.661 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511883 | G16133_345CS | 345 | 7.9598 | 7.9598 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511884 | ZONE-1 SUB | 345 | 7.0643 | 7.0643 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511893 | ZONE-2 SUB | 345 | 7.0461 | 7.0461 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511902 | ZONE-3 SUB | 345 | 6.9858 | 6.9858 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511911 | ZONE-4 SUB | 345 | 6.5223 | 6.5223 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 511929 | ZONE-6 SUB | 345 | 7.0721 | 7.0721 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 514771 | TANGIER2 | 69 | 3.878 | 3.878 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 514773 | NEWMAN 2 | 69 | 1.6272 | 1.6272 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 514775 | TANGRTP2 | 69 | 5.0507 | 5.0507 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.8794 | 7.8794 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515233 | PECANCK4 | 138 | 14.6506 | 14.6506 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 22.0791 | 22.0791 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 25.7652 | 25.7652 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.2844 | 3.2844 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 3.8745 | 3.8745 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515694 | ARMFTWD4 | 138 | 10.2477 | 10.2477 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515778 | GRIFFIN7 | 345 | 24.6718 | 24.6718 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.8792 | 6.8792 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 523869 | CHAN+TASCOS6 | 230 | 5.5829 | 5.5829 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 524267 | BUSHLAND 6 | 230 | 10.8311 | 10.8311 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 524276 | WILDOR_WND 6 | 230 | 5.4778 | 5.4778 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 524290 | WILDOR2_JUS6 | 230 | 7.34 | 7.34 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 524296 | SPNSPUR_WND7 | 345 | 6.4323 | 6.4323 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 524299 | SPNSPUR_COL7 | 345 | 6.4323 | 6.4323 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 525461 | NEWHART 6 | 230 | 10.878 | 10.878 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 28.7801 | 28.7801 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 525750 | G18-015-TAP | 345 | 5.4313 | 5.4313 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527599 | SAGA_SDCOL 7 | 345 | 14.0244 | 14.0244 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527600 | SAGA_SMEAS 7 | 345 | 14.0244 | 14.0244 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527610 | SAGA_SCOL 7 | 345 | 14.0244 | 14.0244 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527640 | MILO_WIND 7 | 345 | 13.6432 | 13.6432 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527654 | RSVLT_CC_W 7 | 345 | 11.2988 | 11.2988 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527655 | RSVLT_CC_E 7 | 345 | 13.6432 | 13.6432 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527666 | RSVLT_COL1 7 | 345 | 11.2988 | 11.2988 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 527667 | RSVLT_COL2 7 | 345 | 11.2988 | 11.2988 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.0968 | 7.0968 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 534109 | GEN-2016-073 | 345 | 5.5582 | 5.5582 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.9501 | 4.9501 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.4021 | 5.4021 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.9361 | 1.9361 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.9227 | 1.9227 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 762132 | GEN-2017-158 | 230 | 12.5001 | 12.5001 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 6.7926 | 6.7926 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 762460 | GEN-2018-015 | 345 | 5.4193 | 5.4193 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 12.129 | 12.129 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 763186 | GEN-2018-089 | 230 | 10.5676 | 10.5676 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 765470 | GEN-2021-018 | 345 | 7.723 | 7.723 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 779941 | GEN-2024-099 | 230 | 10.8354 | 10.8354 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 781561 | GEN-2024-153 | 230 | 10.749 | 10.749 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 785761 | GEN-2024-293 | 345 | 31.193 | 31.193 | 0
GEN-2026-PR2 | 04 SOUTHEAST | 786061 | GEN-2024-303 | 345 | 12.6869 | 12.6869 | 0

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR2 | 8.6493 | PASS | 0.79965 | PASS | None | PASS | No

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | base | 11.4406 | PASS | 0.84026 | PASS | 740.2624 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 11.3022 | PASS | 0.85591 | PASS | 755.9118 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.2622 | PASS | 0.85209 | PASS | 752.0931 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 781591 [GEN-2024-154 345.00] CKT 1 | 11.4401 | PASS | 0.84105 | PASS | 741.0486 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 11.252 | PASS | 0.84955 | PASS | 749.5472 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 515425 [WWDPST 4 138.00] CKT 8 | 11.1827 | PASS | 0.84268 | PASS | 742.6828 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514796 [IODINE-4 138.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 1 | 11.3949 | PASS | 0.84047 | PASS | 740.4673 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 11.3655 | PASS | 0.83913 | PASS | 739.1307 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 11.4235 | PASS | 0.84041 | PASS | 740.4105 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 11.2383 | PASS | 0.84144 | PASS | 741.436 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 11.4355 | PASS | 0.84055 | PASS | 740.5543 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 11.3666 | PASS | 0.84159 | PASS | 741.5857 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.1193 | PASS | 0.83965 | PASS | 739.6472 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.3017 | PASS | 0.83958 | PASS | 739.579 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 11.3023 | PASS | 0.83959 | PASS | 739.5851 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 11.4544 | PASS | 0.83779 | PASS | 737.7913 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 11.2986 | PASS | 0.83991 | PASS | 739.9129 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784141 [GEN-2024-239 345.00] CKT 1 | 11.4516 | PASS | 0.83787 | PASS | 737.8704 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784530 [GEN-2024-252 345.00] CKT 3 | 11.4461 | PASS | 0.83905 | PASS | 739.0541 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784531 [GEN-2024-252 345.00] CKT 1 | 11.3602 | PASS | 0.83837 | PASS | 738.3743 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 11.4402 | PASS | 0.84031 | PASS | 740.3087 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 11.4401 | PASS | 0.84031 | PASS | 740.3125 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 11.4401 | PASS | 0.84033 | PASS | 740.3336 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.2116 | PASS | 0.84201 | PASS | 742.0071 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 10.0907 | PASS | 0.8399 | PASS | 739.9011 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 10.0659 | PASS | 0.83971 | PASS | 739.7141 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 11.2549 | PASS | 0.8344 | PASS | 734.397 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 11.2548 | PASS | 0.83442 | PASS | 734.4163 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.4046 | PASS | 0.85284 | PASS | 752.8376 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 10.7646 | PASS | 0.84732 | PASS | 747.319 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 11.3627 | PASS | 0.83366 | PASS | 733.6618 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 11.3731 | PASS | 0.83856 | PASS | 738.5648 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 11.448 | PASS | 0.83862 | PASS | 738.6185 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 11.4361 | PASS | 0.84119 | PASS | 741.1891 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 11.4125 | PASS | 0.84644 | PASS | 746.4353 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515376 [WWRDEHV4 138.00] TO BUS 515394 [KEENAN 4 138.00] CKT 1 | 11.4378 | PASS | 0.84109 | PASS | 741.0917 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515376 [WWRDEHV4 138.00] TO BUS 515398 [OUSPRT 4 138.00] CKT 1 | 11.4388 | PASS | 0.84081 | PASS | 740.806 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515376 [WWRDEHV4 138.00] TO BUS 515425 [WWDPST 4 138.00] CKT 1 | 11.1828 | PASS | 0.84274 | PASS | 742.7374 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 11.4696 | PASS | 0.8371 | PASS | 737.0967 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 8.6626 | PASS | 0.85385 | PASS | 753.8525 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 8.6553 | PASS | 0.85386 | PASS | 753.864 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 11.5054 | PASS | 0.83613 | PASS | 736.131 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.4326 | PASS | 0.84088 | PASS | 740.8827 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 2 | 11.4326 | PASS | 0.84088 | PASS | 740.8827 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 11.2613 | PASS | 0.84847 | PASS | 748.4747 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 11.4456 | PASS | 0.84174 | PASS | 741.7445 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 11.4476 | PASS | 0.83869 | PASS | 738.6943 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 11.2945 | PASS | 0.83847 | PASS | 738.4663 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 11.3147 | PASS | 0.84285 | PASS | 742.8459 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 11.3146 | PASS | 0.84284 | PASS | 742.8441 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.4217 | PASS | 0.84705 | PASS | 747.0498 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 11.2887 | PASS | 0.83737 | PASS | 737.3724 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 11.2887 | PASS | 0.83737 | PASS | 737.3709 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 776821 [GEN-2023-102 345.00] CKT 1 | 11.4109 | PASS | 0.84678 | PASS | 746.7811 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 780991 [GEN-2024-134 345.00] CKT 1 | 11.4192 | PASS | 0.84519 | PASS | 745.1897 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 781021 [GEN-2024-135 345.00] CKT 1 | 11.4192 | PASS | 0.84519 | PASS | 745.1897 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 11.4433 | PASS | 0.83985 | PASS | 739.8527 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515951 [PERSIMN7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.4247 | PASS | 0.84519 | PASS | 745.1879 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 11.4457 | PASS | 0.8404 | PASS | 740.4039 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 11.4415 | PASS | 0.84017 | PASS | 740.1682 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 2 | 11.3597 | PASS | 0.84883 | PASS | 748.825 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 516146 [25MILE 7 345.00] CKT 1 | 11.4309 | PASS | 0.84293 | PASS | 742.9255 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 588560 [GEN-2017-011 345.00] CKT 1 | 11.4363 | PASS | 0.84146 | PASS | 741.4624 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511557 [CHISHOLM6 230.00] TO BUS 511558 [CHISHOLM1 13.2] CKT 1 | 11.4114 | PASS | 0.83908 | PASS | 739.0763 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511490 [ELKCITY6 230.00] CKT 1 | 11.4194 | PASS | 0.84306 | PASS | 743.0605 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511541 [DEMPSEYR POI 230.00] CKT 1 | 11.3963 | PASS | 0.84444 | PASS | 744.4358 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 511592 [SEVEN7A_HV 345.00] CKT 1 | 11.4283 | PASS | 0.84031 | PASS | 740.3121 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 11.3356 | PASS | 0.85341 | PASS | 753.4067 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 11.3624 | PASS | 0.85658 | PASS | 756.5799 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 11.445 | PASS | 0.83954 | PASS | 739.5406 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 11.3485 | PASS | 0.84086 | PASS | 740.8637 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 11.4458 | PASS | 0.83934 | PASS | 739.3437 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 514714 [WOODRNG4 138.00] TO BUS 515770 [WOODRNG1 13.8] CKT 2 | 11.4363 | PASS | 0.84026 | PASS | 740.2634 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 515363 [CENT 4 138.00] CKT 1 | 11.4419 | PASS | 0.84016 | PASS | 740.1625 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 515785 [WINDFRM4 138.00] CKT 1 | 11.2513 | PASS | 0.84199 | PASS | 741.9932 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 514782 [WODWRD 2 69.00] TO BUS 515771 [WOODWR21 13.2] CKT 2 | 11.4241 | PASS | 0.84025 | PASS | 740.2521 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514796 [IODINE-4 138.00] TO BUS 515533 [REDCLFT4 138.00] CKT 1 | 11.3949 | PASS | 0.84058 | PASS | 740.5778 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515444 [MCNOWND7 345.00] CKT 1 | 11.4503 | PASS | 0.83815 | PASS | 738.1453 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515549 [MNCWND37 345.00] CKT 1 | 11.4485 | PASS | 0.83897 | PASS | 738.9732 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 11.3971 | PASS | 0.84064 | PASS | 740.6445 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 761250 [GEN-2017-233 345.00] CKT 1 | 11.4497 | PASS | 0.83854 | PASS | 738.5402 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514828 [KETCHTP4 138.00] CKT 1 | 11.4363 | PASS | 0.84023 | PASS | 740.2318 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514854 [BRADEN 4 138.00] CKT 1 | 11.4351 | PASS | 0.84021 | PASS | 740.2149 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514864 [PIEDMNT4 138.00] CKT 1 | 11.4381 | PASS | 0.84025 | PASS | 740.2485 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514873 [LNEOAK 4 138.00] CKT 1 | 11.4327 | PASS | 0.84019 | PASS | 740.187 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] TO BUS 515742 [NORTWS21 13.8] CKT 2 | 11.4324 | PASS | 0.84033 | PASS | 740.3258 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] TO BUS 515743 [NORTWS31 13.8] CKT 3 | 11.4327 | PASS | 0.84033 | PASS | 740.3273 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] TO BUS 514885 [NORTWS41 13.8] CKT 4 | 11.4327 | PASS | 0.84033 | PASS | 740.3267 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514882 [SPGCK1&2 13.8.00] CKT 1 | 11.417 | PASS | 0.83982 | PASS | 739.8196 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514883 [SPGCK3&4 13.8.00] CKT 1 | 11.4171 | PASS | 0.83982 | PASS | 739.8194 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 11.3593 | PASS | 0.84738 | PASS | 747.3813 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784620 [GEN-2024-255 345.00] CKT 3 | 11.4453 | PASS | 0.83919 | PASS | 739.1917 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784621 [GEN-2024-255 345.00] CKT 1 | 11.3893 | PASS | 0.83814 | PASS | 738.1368 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 511425 [TUTCONT4 138.00] CKT 1 | 11.4343 | PASS | 0.84015 | PASS | 740.1455 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514819 [EL-RENO4 138.00] CKT 1 | 11.4409 | PASS | 0.84021 | PASS | 740.2093 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514820 [JENSENT4 138.00] CKT 1 | 11.4408 | PASS | 0.84017 | PASS | 740.1741 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514863 [HAYMAKR4 138.00] CKT 1 | 11.4388 | PASS | 0.84032 | PASS | 740.3243 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514894 [CZECHAL4 138.00] CKT 1 | 11.4256 | PASS | 0.84013 | PASS | 740.1258 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514895 [SARA 4 138.00] CKT 1 | 11.4285 | PASS | 0.84033 | PASS | 740.3292 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] TO BUS 515714 [CIMARO11 13.8] CKT 1 | 11.422 | PASS | 0.84105 | PASS | 741.0497 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] TO BUS 515715 [CIMARO21 13.8] CKT 2 | 11.419 | PASS | 0.83942 | PASS | 739.4235 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 11.4172 | PASS | 0.84006 | PASS | 740.0628 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 | 11.438 | PASS | 0.84155 | PASS | 741.5529 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 | 11.438 | PASS | 0.84155 | PASS | 741.5529 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 3 | 11.438 | PASS | 0.84155 | PASS | 741.5529 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515703 [ARCADI21 13.8] CKT 2 | 11.4402 | PASS | 0.84032 | PASS | 740.3192 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515704 [ARCADI31 13.8] CKT 3 | 11.4396 | PASS | 0.84042 | PASS | 740.4189 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515700 [ARCADI41 13.8] CKT 4 | 11.4396 | PASS | 0.84043 | PASS | 740.4309 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 787290 [G24-344-TAP 345.00] CKT 1 | 11.3799 | PASS | 0.83684 | PASS | 736.8395 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514899 [REDBUD1S 18.00] TO BUS 514910 [REDBUD1G 18] CKT 1 | 11.4116 | PASS | 0.83917 | PASS | 739.1742 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514900 [REDBUD2S 18.00] TO BUS 514911 [REDBUD2G 18] CKT 1 | 11.4116 | PASS | 0.83919 | PASS | 739.1893 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514905 [REDBUD3S 18.00] TO BUS 514912 [REDBUD3G 18] CKT 1 | 11.4115 | PASS | 0.83921 | PASS | 739.2078 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514940 [REDBUD4S 18.00] TO BUS 514942 [REDBUD4G 18] CKT 1 | 11.4116 | PASS | 0.83919 | PASS | 739.1897 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515795 [WWDEHV21 13.8] CKT 2 | 11.3873 | PASS | 0.84122 | PASS | 741.2242 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515799 [WWDEHV31 13.8] CKT 3 | 11.3847 | PASS | 0.84128 | PASS | 741.276 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515394 [KEENAN 4 138.00] TO BUS 515393 [KEENAN 1 34.5.00] TO BUS 515392 [KEENAN T 10] CKT 1 | 11.4377 | PASS | 0.84103 | PASS | 741.0327 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515398 [OUSPRT 4 138.00] TO BUS 515397 [OUSPRT 1 34.5.00] TO BUS 515396 [OUSPRT T 10] CKT 1 | 11.4387 | PASS | 0.84076 | PASS | 740.7623 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515450 [CRSRDW21 34.5.00] TO BUS 515452 [CRSRDWT2 13.8] CKT 2 | 11.4556 | PASS | 0.83731 | PASS | 737.3116 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515449 [CRSRDW11 34.5.00] TO BUS 515451 [CRSRDWT1 13.8] CKT 1 | 11.4513 | PASS | 0.83818 | PASS | 738.1834 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 525832 [TUCO_INT 7 345.00] CKT 1 | 11.3967 | PASS | 0.84247 | PASS | 742.4719 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 525839 [G17-151TAP 345.00] CKT 1 | 11.3852 | PASS | 0.84181 | PASS | 741.8081 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515583 [SLINGW11 34.5.00] TO BUS 515584 [SILNGWT1 13.8] CKT 1 | 11.4746 | PASS | 0.83534 | PASS | 735.3429 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515632 [SILNGW21 34.5.00] TO BUS 515633 [SILNGWT2 13.8] CKT 2 | 11.467 | PASS | 0.8364 | PASS | 736.3972 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515610 [FSHRTAP7 345.00] TO BUS 515600 [KNGFSHR7 345.00] CKT 1 | 11.4519 | PASS | 0.83805 | PASS | 738.0457 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515610 [FSHRTAP7 345.00] TO BUS 515605 [CANADN7 345.00] CKT 1 | 11.4444 | PASS | 0.83953 | PASS | 739.5324 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515554 [BVRCNTY7 345.00] CKT 1 | 11.3821 | PASS | 0.83845 | PASS | 738.448 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515554 [BVRCNTY7 345.00] CKT 2 | 11.382 | PASS | 0.83845 | PASS | 738.448 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515686 [BLUWND 7 345.00] CKT 1 | 11.4411 | PASS | 0.84052 | PASS | 740.5218 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516074 [PONDRSA7 345.00] CKT 1 | 11.4335 | PASS | 0.84251 | PASS | 742.5058 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 585420 [SUBST HS 345.00] CKT 1 | 11.4325 | PASS | 0.8432 | PASS | 743.1957 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 515820 [GRTWSL11 34.5.00] TO BUS 515860 [GRTWST11 13.8] CKT 1 | 11.435 | PASS | 0.84187 | PASS | 741.8692 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 515823 [GRTWSL21 34.5.00] TO BUS 515824 [GRTWST21 13.8] CKT 1 | 11.4351 | PASS | 0.84192 | PASS | 741.9174 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 515853 [DGRASSE4 138.00] TO BUS 515854 [DGRASSE1 13.8] CKT 3 | 11.3685 | PASS | 0.84499 | PASS | 744.9856 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 514795 [KNOBHIL4 138.00] CKT 1 | 11.4374 | PASS | 0.84027 | PASS | 740.267 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 520436 [ROSEVLY4 138.00] CKT 1 | 11.4359 | PASS | 0.84048 | PASS | 740.482 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 520999 [MOORLND4 138.00] CKT 1 | 11.4196 | PASS | 0.84246 | PASS | 742.4648 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 763769 [GEN-2019-045 138.00] CKT 1 | 11.4374 | PASS | 0.84128 | PASS | 741.276 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] TO BUS 515884 [RDDRTT11 13.2] CKT 1 | 11.4425 | PASS | 0.83995 | PASS | 739.9473 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] TO BUS 515885 [RDDRTT21 13.2] CKT 1 | 11.4428 | PASS | 0.83989 | PASS | 739.8901 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515951 [PERSIMN7 345.00] TO BUS 562020 [PRSCRKII 7 345.00] CKT 1 | 11.4345 | PASS | 0.84197 | PASS | 741.9728 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515951 [PERSIMN7 345.00] TO BUS 515953 [PRSMNL11 34.5.00] TO BUS 515952 [PRSMNT11 13.8] CKT 1 | 11.4311 | PASS | 0.84323 | PASS | 743.2253 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516054 [TRAV1WD7 345.00] CKT 1 | 11.4429 | PASS | 0.84024 | PASS | 740.2442 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516087 [TRAV22Z7 345.00] CKT 1 | 11.4433 | PASS | 0.8398 | PASS | 739.7996 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516107 [TRAV21Z7 345.00] CKT 1 | 11.4416 | PASS | 0.84011 | PASS | 740.1115 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516086 [TRAV3WZ7 345.00] TO BUS 516035 [TRAV3L11 34.5.00] TO BUS 516037 [TRAV3T11 13.8] CKT 1 | 11.4415 | PASS | 0.84017 | PASS | 740.1682 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 | 11.43 | PASS | 0.84037 | PASS | 740.3743 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 11.4293 | PASS | 0.84039 | PASS | 740.392 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 777361 [GEN-2024-013 345.00] CKT 1 | 11.4173 | PASS | 0.83535 | PASS | 735.3495 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] TO BUS 516099 [NORMHL21 13.8] CKT 2 | 11.4382 | PASS | 0.84031 | PASS | 740.3088 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] TO BUS 516098 [NORMHL11 13.8] CKT 1 | 11.4382 | PASS | 0.84031 | PASS | 740.3085 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516146 [25MILE 7 345.00] TO BUS 516159 [25MILZ 7 345.00] CKT 1 | 11.4309 | PASS | 0.84291 | PASS | 742.9121 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 11.3128 | PASS | 0.8419 | PASS | 741.8978 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 524296 [SPNSPUR_WND7 345.00] CKT 1 | 11.4353 | PASS | 0.84156 | PASS | 741.5603 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 525549 [TOLK 7 345.00] CKT 1 | 11.432 | PASS | 0.84031 | PASS | 740.3102 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523967 [POTTER_TR3 3 13.2] CKT 1 | 11.4403 | PASS | 0.84029 | PASS | 740.2855 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523964 [POTTER_TR3 1 13.2] CKT 1 | 11.4403 | PASS | 0.84029 | PASS | 740.2855 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523965 [POTTER_TR3 2 13.2] CKT 1 | 11.4403 | PASS | 0.84029 | PASS | 740.2855 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] TO BUS 523958 [POTTER_TR2 1 13.2] CKT 2 | 11.4398 | PASS | 0.83912 | PASS | 739.1232 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] TO BUS 523957 [POTTER_TR 1 13.2] CKT 1 | 11.4378 | PASS | 0.83954 | PASS | 739.5376 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 11.377 | PASS | 0.835 | PASS | 734.9971 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 2 | 11.3768 | PASS | 0.83513 | PASS | 735.1346 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539800 [CLARKCOUNTY7 345.00] CKT 1 | 11.4168 | PASS | 0.8421 | PASS | 742.0959 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539800 [CLARKCOUNTY7 345.00] CKT 2 | 11.4167 | PASS | 0.84179 | PASS | 741.7882 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539871 [PIXLEY-SOLAR 345.00] CKT 1 | 11.4409 | PASS | 0.84034 | PASS | 740.3382 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 762834 [GEN-2018-049 345.00] CKT 1 | 11.4412 | PASS | 0.84082 | PASS | 740.8212 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.8] CKT 1 | 11.4203 | PASS | 0.83977 | PASS | 739.7726 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 588560 [GEN-2017-011 345.00] TO BUS 588561 [G17-011XFMR1 34.5.00] CKT 1 | 11.4359 | PASS | 0.8412 | PASS | 741.2008 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 763527 [GEN-2019-012 345.00] TO BUS 763528 [G19-012-XFM1 34.5.00] CKT 1 | 11.448 | PASS | 0.83862 | PASS | 738.6174 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767221 [GEN-2022-012 345.00] TO BUS 767222 [G22-012XFMR1 34.5.00] CKT 1 | 11.4361 | PASS | 0.84118 | PASS | 741.176 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767301 [GEN-2022-016 345.00] TO BUS 767302 [G22-016XFMR1 34.5.00] CKT 1 | 11.4323 | PASS | 0.84209 | PASS | 742.0898 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767301 [GEN-2022-016 345.00] TO BUS 767305 [G22-016XFMR2 34.5.00] CKT 1 | 11.4323 | PASS | 0.84209 | PASS | 742.0898 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767301 [GEN-2022-016 345.00] TO BUS 767321 [GEN-2022-017 345.00] CKT 1 | 11.4308 | PASS | 0.8423 | PASS | 742.3016 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776822 [G23-102XFMR1 34.5.00] CKT 1 | 11.434 | PASS | 0.84168 | PASS | 741.6774 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776823 [G23-102XFMR2 34.5.00] CKT 1 | 11.4341 | PASS | 0.84166 | PASS | 741.6602 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776824 [G23-102XFMR3 34.5.00] CKT 1 | 11.4341 | PASS | 0.84166 | PASS | 741.6567 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776825 [G23-102XFMR4 34.5.00] CKT 1 | 11.4343 | PASS | 0.84162 | PASS | 741.6237 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 780991 [GEN-2024-134 345.00] TO BUS 780992 [G24-134XFMR1 34.5.00] TO BUS 781007 [G24-134TER1 13.8] CKT 1 | 11.4304 | PASS | 0.84244 | PASS | 742.4447 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 780991 [GEN-2024-134 345.00] TO BUS 780995 [G24-134XFMR2 34.5.00] TO BUS 781008 [G24-134TER2 13.8] CKT 1 | 11.4305 | PASS | 0.84242 | PASS | 742.4215 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 781021 [GEN-2024-135 345.00] TO BUS 781022 [G24-135XFMR1 34.5.00] TO BUS 781037 [G24-135TER1 13.8] CKT 1 | 11.4304 | PASS | 0.84244 | PASS | 742.4447 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 781021 [GEN-2024-135 345.00] TO BUS 781025 [G24-135XFMR2 34.5.00] TO BUS 781038 [G24-135TER2 13.8] CKT 1 | 11.4305 | PASS | 0.84242 | PASS | 742.4215 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 781591 [GEN-2024-154 345.00] TO BUS 781592 [G24-154XFMR1 34.5.00] TO BUS 781607 [G24-154TER1 13.8] CKT 1 | 11.4401 | PASS | 0.84105 | PASS | 741.0466 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784141 [GEN-2024-239 345.00] TO BUS 784142 [G24-239XFMR1 34.5.00] TO BUS 784157 [G24-239TER1 13.8] CKT 1 | 11.4516 | PASS | 0.83787 | PASS | 737.8692 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784530 [GEN-2024-252 345.00] TO BUS 784535 [G24-252XFMR2 34.5.00] TO BUS 784548 [G24-252TER2 13.8] CKT 2 | 11.4461 | PASS | 0.83904 | PASS | 739.0446 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 784534 [G24-252GEN1 13.8.00] CKT 1 | 11.3602 | PASS | 0.83836 | PASS | 738.3642 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 784595 [G24-254XFMR2 34.5.00] TO BUS 784608 [G24-254TER2 13.8] CKT 2 | 11.4476 | PASS | 0.83867 | PASS | 738.6747 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 784594 [G24-254GEN1 13.8.00] CKT 1 | 11.2945 | PASS | 0.83845 | PASS | 738.4452 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT1 & 2 | 11.4369 | PASS | 0.84251 | PASS | 742.5117 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT1 & 3 | 11.4369 | PASS | 0.84251 | PASS | 742.5117 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT2 & 3 | 11.4369 | PASS | 0.84251 | PASS | 742.5117 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515554 [BVRCNTY7 345.00] CKT1 & 2 | 10.6613 | PASS | 0.8393 | PASS | 739.2972 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT1 & 2 | 11.3638 | PASS | 0.84086 | PASS | 740.8592 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT1 & 2 | 11.1727 | PASS | 0.82405 | PASS | 724.0499 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539800 [CLARKCOUNTY7 345.00] CKT1 & 2 | 11.1431 | PASS | Non-converged | PASS | 0 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | base | 11.3872 | PASS | 0.80522 | PASS | 705.2218 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 11.3156 | PASS | 0.81122 | PASS | 711.219 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.2798 | PASS | 0.80903 | PASS | 709.0279 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 781591 [GEN-2024-154 345.00] CKT 1 | 11.3875 | PASS | 0.80517 | PASS | 705.1694 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 11.2282 | PASS | 0.80873 | PASS | 708.7305 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 515425 [WWDPST 4 138.00] CKT 8 | 11.1533 | PASS | 0.80626 | PASS | 706.2553 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514796 [IODINE-4 138.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 1 | 11.3429 | PASS | 0.8055 | PASS | 705.499 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 11.3059 | PASS | 0.80529 | PASS | 705.2858 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 11.3705 | PASS | 0.80542 | PASS | 705.4177 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 11.1822 | PASS | 0.80465 | PASS | 704.6525 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 11.3831 | PASS | 0.80531 | PASS | 705.3123 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 11.3145 | PASS | 0.80605 | PASS | 706.0476 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.0812 | PASS | 0.803 | PASS | 702.9996 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.253 | PASS | 0.80452 | PASS | 704.5186 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 11.2535 | PASS | 0.80452 | PASS | 704.5234 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 11.3917 | PASS | 0.80485 | PASS | 704.8508 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 11.2466 | PASS | 0.80498 | PASS | 704.9837 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784141 [GEN-2024-239 345.00] CKT 1 | 11.3931 | PASS | 0.80416 | PASS | 704.1571 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784530 [GEN-2024-252 345.00] CKT 3 | 11.39 | PASS | 0.80466 | PASS | 704.6571 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784531 [GEN-2024-252 345.00] CKT 1 | 11.2944 | PASS | 0.80444 | PASS | 704.4393 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 11.3867 | PASS | 0.80527 | PASS | 705.2656 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 11.3866 | PASS | 0.80527 | PASS | 705.2689 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 11.3866 | PASS | 0.80529 | PASS | 705.2912 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.1576 | PASS | 0.80709 | PASS | 707.0948 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 10.0364 | PASS | 0.80682 | PASS | 706.8224 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 10.0115 | PASS | 0.80672 | PASS | 706.7162 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 11.1833 | PASS | 0.80387 | PASS | 703.868 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 11.1833 | PASS | 0.80388 | PASS | 703.8765 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.3781 | PASS | 0.81191 | PASS | 711.9112 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 10.6994 | PASS | 0.80957 | PASS | 709.5716 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 11.3009 | PASS | 0.80186 | PASS | 701.8626 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 11.3217 | PASS | 0.8045 | PASS | 704.5025 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 11.3905 | PASS | 0.80455 | PASS | 704.5455 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 11.3866 | PASS | 0.80535 | PASS | 705.3455 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 11.3831 | PASS | 0.80631 | PASS | 706.3061 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515376 [WWRDEHV4 138.00] TO BUS 515394 [KEENAN 4 138.00] CKT 1 | 11.3863 | PASS | 0.80572 | PASS | 705.7192 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515376 [WWRDEHV4 138.00] TO BUS 515398 [OUSPRT 4 138.00] CKT 1 | 11.3866 | PASS | 0.80559 | PASS | 705.5906 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515376 [WWRDEHV4 138.00] TO BUS 515425 [WWDPST 4 138.00] CKT 1 | 11.1535 | PASS | 0.80629 | PASS | 706.2853 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 11.4214 | PASS | 0.80121 | PASS | 701.2109 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 8.6565 | PASS | 0.81685 | PASS | 716.8548 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 8.6493 | PASS | 0.81686 | PASS | 716.8564 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 11.4554 | PASS | 0.8006 | PASS | 700.6043 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.3814 | PASS | 0.80545 | PASS | 705.4479 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 2 | 11.3814 | PASS | 0.80545 | PASS | 705.4479 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 11.2322 | PASS | 0.80871 | PASS | 708.7105 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 11.3852 | PASS | 0.80832 | PASS | 708.3211 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 11.3908 | PASS | 0.80449 | PASS | 704.4944 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 11.2299 | PASS | 0.80403 | PASS | 704.0307 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 11.2809 | PASS | 0.80625 | PASS | 706.2467 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 11.2808 | PASS | 0.80625 | PASS | 706.246 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.393 | PASS | 0.8068 | PASS | 706.7962 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 11.23 | PASS | 0.80508 | PASS | 705.0764 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 11.23 | PASS | 0.80508 | PASS | 705.0755 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 776821 [GEN-2023-102 345.00] CKT 1 | 11.38 | PASS | 0.80697 | PASS | 706.9713 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 780991 [GEN-2024-134 345.00] CKT 1 | 11.384 | PASS | 0.80641 | PASS | 706.4112 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 781021 [GEN-2024-135 345.00] CKT 1 | 11.384 | PASS | 0.80641 | PASS | 706.4112 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 11.3862 | PASS | 0.80566 | PASS | 705.6604 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515951 [PERSIMN7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.3882 | PASS | 0.80661 | PASS | 706.6051 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 11.3861 | PASS | 0.80681 | PASS | 706.8094 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 11.387 | PASS | 0.80538 | PASS | 705.384 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 1 | 11.358 | PASS | 0.80698 | PASS | 706.9768 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 2 | 11.3579 | PASS | 0.80698 | PASS | 706.9774 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 516146 [25MILE 7 345.00] CKT 1 | 11.3856 | PASS | 0.80628 | PASS | 706.2762 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 588560 [GEN-2017-011 345.00] CKT 1 | 11.3861 | PASS | 0.80582 | PASS | 705.8191 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511553 [CHISHOLM7 345.00] TO BUS 511557 [CHISHOLM6 230.00] TO BUS 511558 [CHISHOLM1 13.2] CKT 1 | 11.3643 | PASS | 0.80457 | PASS | 704.5674 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511490 [ELKCITY6 230.00] CKT 1 | 11.3805 | PASS | 0.80601 | PASS | 706.0109 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511541 [DEMPSEYR POI 230.00] CKT 1 | 11.3631 | PASS | 0.80566 | PASS | 705.6643 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 511592 [SEVEN7A_HV 345.00] CKT 1 | 11.376 | PASS | 0.80517 | PASS | 705.1655 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 511587 [MATO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 11.3383 | PASS | 0.80933 | PASS | 709.3261 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 11.3674 | PASS | 0.80903 | PASS | 709.0255 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 11.3884 | PASS | 0.80532 | PASS | 705.3241 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 11.2975 | PASS | 0.80531 | PASS | 705.3101 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 11.3879 | PASS | 0.80532 | PASS | 705.3155 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 514714 [WOODRNG4 138.00] TO BUS 515770 [WOODRNG1 13.8] CKT 2 | 11.3837 | PASS | 0.80511 | PASS | 705.1122 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 515363 [CENT 4 138.00] CKT 1 | 11.3888 | PASS | 0.80511 | PASS | 705.1118 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 515785 [WINDFRM4 138.00] CKT 1 | 11.2159 | PASS | 0.80588 | PASS | 705.8825 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514785 [WOODWRD4 138.00] TO BUS 514782 [WODWRD 2 69.00] TO BUS 515771 [WOODWR21 13.2] CKT 2 | 11.3731 | PASS | 0.80533 | PASS | 705.3259 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514796 [IODINE-4 138.00] TO BUS 515533 [REDCLFT4 138.00] CKT 1 | 11.3431 | PASS | 0.80555 | PASS | 705.5476 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515444 [MCNOWND7 345.00] CKT 1 | 11.3915 | PASS | 0.80436 | PASS | 704.3552 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515549 [MNCWND37 345.00] CKT 1 | 11.3924 | PASS | 0.80463 | PASS | 704.6338 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 11.3396 | PASS | 0.80604 | PASS | 706.038 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 761250 [GEN-2017-233 345.00] CKT 1 | 11.3905 | PASS | 0.80485 | PASS | 704.8496 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514828 [KETCHTP4 138.00] CKT 1 | 11.3838 | PASS | 0.8052 | PASS | 705.2 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514854 [BRADEN 4 138.00] CKT 1 | 11.3834 | PASS | 0.80524 | PASS | 705.2402 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514864 [PIEDMNT4 138.00] CKT 1 | 11.3855 | PASS | 0.80525 | PASS | 705.2499 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514873 [LNEOAK 4 138.00] CKT 1 | 11.3815 | PASS | 0.8052 | PASS | 705.2008 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] TO BUS 515742 [NORTWS21 13.8] CKT 2 | 11.381 | PASS | 0.805 | PASS | 704.9981 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] TO BUS 515743 [NORTWS31 13.8] CKT 3 | 11.3813 | PASS | 0.80502 | PASS | 705.0245 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] TO BUS 514885 [NORTWS41 13.8] CKT 4 | 11.3814 | PASS | 0.80522 | PASS | 705.2209 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514882 [SPGCK1&2 13.8.00] CKT 1 | 11.3612 | PASS | 0.80482 | PASS | 704.8225 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514883 [SPGCK3&4 13.8.00] CKT 1 | 11.3613 | PASS | 0.80482 | PASS | 704.8226 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 11.3268 | PASS | 0.80804 | PASS | 708.038 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784620 [GEN-2024-255 345.00] CKT 3 | 11.3894 | PASS | 0.80478 | PASS | 704.7831 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784621 [GEN-2024-255 345.00] CKT 1 | 11.3235 | PASS | 0.80439 | PASS | 704.386 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 511425 [TUTCONT4 138.00] CKT 1 | 11.3821 | PASS | 0.80517 | PASS | 705.1738 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514819 [EL-RENO4 138.00] CKT 1 | 11.3876 | PASS | 0.80518 | PASS | 705.1757 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514820 [JENSENT4 138.00] CKT 1 | 11.3874 | PASS | 0.80518 | PASS | 705.1808 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514863 [HAYMAKR4 138.00] CKT 1 | 11.3861 | PASS | 0.80526 | PASS | 705.264 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514894 [CZECHAL4 138.00] CKT 1 | 11.377 | PASS | 0.80508 | PASS | 705.0788 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514895 [SARA 4 138.00] CKT 1 | 11.3747 | PASS | 0.80518 | PASS | 705.1812 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] TO BUS 515714 [CIMARO11 13.8] CKT 1 | 11.3721 | PASS | 0.80603 | PASS | 706.0252 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] TO BUS 515715 [CIMARO21 13.8] CKT 2 | 11.3716 | PASS | 0.8041 | PASS | 704.0987 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 11.361 | PASS | 0.80538 | PASS | 705.3772 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 | 11.3865 | PASS | 0.80619 | PASS | 706.1892 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 | 11.3865 | PASS | 0.80619 | PASS | 706.1892 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 3 | 11.3865 | PASS | 0.80619 | PASS | 706.1892 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515703 [ARCADI21 13.8] CKT 2 | 11.3871 | PASS | 0.80527 | PASS | 705.265 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515704 [ARCADI31 13.8] CKT 3 | 11.3872 | PASS | 0.80519 | PASS | 705.1935 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515700 [ARCADI41 13.8] CKT 4 | 11.3872 | PASS | 0.8052 | PASS | 705.2027 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 787290 [G24-344-TAP 345.00] CKT 1 | 11.3155 | PASS | 0.80315 | PASS | 703.1524 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514899 [REDBUD1S 18.00] TO BUS 514910 [REDBUD1G 18] CKT 1 | 11.3504 | PASS | 0.80506 | PASS | 705.0648 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514900 [REDBUD2S 18.00] TO BUS 514911 [REDBUD2G 18] CKT 1 | 11.3504 | PASS | 0.80507 | PASS | 705.0655 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514905 [REDBUD3S 18.00] TO BUS 514912 [REDBUD3G 18] CKT 1 | 11.3504 | PASS | 0.80507 | PASS | 705.0719 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514940 [REDBUD4S 18.00] TO BUS 514942 [REDBUD4G 18] CKT 1 | 11.3504 | PASS | 0.80507 | PASS | 705.0658 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515795 [WWDEHV21 13.8] CKT 2 | 11.3329 | PASS | 0.80475 | PASS | 704.748 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515799 [WWDEHV31 13.8] CKT 3 | 11.3261 | PASS | 0.80447 | PASS | 704.4676 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515394 [KEENAN 4 138.00] TO BUS 515393 [KEENAN 1 34.5.00] TO BUS 515392 [KEENAN T 10] CKT 1 | 11.3861 | PASS | 0.80569 | PASS | 705.6863 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515398 [OUSPRT 4 138.00] TO BUS 515397 [OUSPRT 1 34.5.00] TO BUS 515396 [OUSPRT T 10] CKT 1 | 11.3864 | PASS | 0.80556 | PASS | 705.5648 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515450 [CRSRDW21 34.5.00] TO BUS 515452 [CRSRDWT2 13.8] CKT 2 | 11.4041 | PASS | 0.8021 | PASS | 702.1018 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515449 [CRSRDW11 34.5.00] TO BUS 515451 [CRSRDWT1 13.8] CKT 1 | 11.4005 | PASS | 0.80282 | PASS | 702.8162 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 525832 [TUCO_INT 7 345.00] CKT 1 | 11.3543 | PASS | 0.80591 | PASS | 705.9128 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515458 [BORDER 7 345.00] TO BUS 525839 [G17-151TAP 345.00] CKT 1 | 11.3425 | PASS | 0.80503 | PASS | 705.0284 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515583 [SLINGW11 34.5.00] TO BUS 515584 [SILNGWT1 13.8] CKT 1 | 11.4209 | PASS | 0.80061 | PASS | 700.612 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515632 [SILNGW21 34.5.00] TO BUS 515633 [SILNGWT2 13.8] CKT 2 | 11.4141 | PASS | 0.80154 | PASS | 701.5369 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515610 [FSHRTAP7 345.00] TO BUS 515600 [KNGFSHR7 345.00] CKT 1 | 11.3897 | PASS | 0.80498 | PASS | 704.9814 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515610 [FSHRTAP7 345.00] TO BUS 515605 [CANADN7 345.00] CKT 1 | 11.3896 | PASS | 0.80488 | PASS | 704.8784 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515554 [BVRCNTY7 345.00] CKT 1 | 11.3293 | PASS | 0.80442 | PASS | 704.418 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515554 [BVRCNTY7 345.00] CKT 2 | 11.3292 | PASS | 0.80442 | PASS | 704.4177 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515686 [BLUWND 7 345.00] CKT 1 | 11.3885 | PASS | 0.80529 | PASS | 705.2918 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516074 [PONDRSA7 345.00] CKT 1 | 11.3886 | PASS | 0.80578 | PASS | 705.7816 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 585420 [SUBST HS 345.00] CKT 1 | 11.3939 | PASS | 0.8051 | PASS | 705.1019 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 515820 [GRTWSL11 34.5.00] TO BUS 515860 [GRTWST11 13.8] CKT 1 | 11.3899 | PASS | 0.80512 | PASS | 705.1192 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515825 [GRTWSRN7 345.00] TO BUS 515823 [GRTWSL21 34.5.00] TO BUS 515824 [GRTWST21 13.8] CKT 1 | 11.3903 | PASS | 0.80512 | PASS | 705.1192 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515852 [DGRASSE7 345.00] TO BUS 515853 [DGRASSE4 138.00] TO BUS 515854 [DGRASSE1 13.8] CKT 3 | 11.3253 | PASS | 0.80593 | PASS | 705.9283 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 514795 [KNOBHIL4 138.00] CKT 1 | 11.3842 | PASS | 0.80524 | PASS | 705.2352 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 520436 [ROSEVLY4 138.00] CKT 1 | 11.3836 | PASS | 0.8053 | PASS | 705.3001 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 520999 [MOORLND4 138.00] CKT 1 | 11.3713 | PASS | 0.80623 | PASS | 706.23 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515853 [DGRASSE4 138.00] TO BUS 763769 [GEN-2019-045 138.00] CKT 1 | 11.3871 | PASS | 0.80564 | PASS | 705.6432 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] TO BUS 515884 [RDDRTT11 13.2] CKT 1 | 11.3868 | PASS | 0.80544 | PASS | 705.4386 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] TO BUS 515885 [RDDRTT21 13.2] CKT 1 | 11.3867 | PASS | 0.80544 | PASS | 705.4414 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515951 [PERSIMN7 345.00] TO BUS 562020 [PRSCRKII 7 345.00] CKT 1 | 11.3874 | PASS | 0.80567 | PASS | 705.6696 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515951 [PERSIMN7 345.00] TO BUS 515953 [PRSMNL11 34.5.00] TO BUS 515952 [PRSMNT11 13.8] CKT 1 | 11.388 | PASS | 0.80604 | PASS | 706.0433 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516054 [TRAV1WD7 345.00] CKT 1 | 11.387 | PASS | 0.80581 | PASS | 705.8092 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516087 [TRAV22Z7 345.00] CKT 1 | 11.3873 | PASS | 0.8054 | PASS | 705.3966 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516107 [TRAV21Z7 345.00] CKT 1 | 11.3871 | PASS | 0.80534 | PASS | 705.3384 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516086 [TRAV3WZ7 345.00] TO BUS 516035 [TRAV3L11 34.5.00] TO BUS 516037 [TRAV3T11 13.8] CKT 1 | 11.387 | PASS | 0.80538 | PASS | 705.384 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 1 | 11.3767 | PASS | 0.80539 | PASS | 705.3945 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 11.3758 | PASS | 0.80541 | PASS | 705.4108 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 777361 [GEN-2024-013 345.00] CKT 1 | 11.3452 | PASS | 0.80294 | PASS | 702.9371 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] TO BUS 516099 [NORMHL21 13.8] CKT 2 | 11.3857 | PASS | 0.80525 | PASS | 705.2526 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] TO BUS 516098 [NORMHL11 13.8] CKT 1 | 11.3857 | PASS | 0.80525 | PASS | 705.2523 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516146 [25MILE 7 345.00] TO BUS 516159 [25MILZ 7 345.00] CKT 1 | 11.3855 | PASS | 0.80627 | PASS | 706.2693 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 11.2706 | PASS | 0.80521 | PASS | 705.2053 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 524296 [SPNSPUR_WND7 345.00] CKT 1 | 11.3868 | PASS | 0.80539 | PASS | 705.3932 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 525549 [TOLK 7 345.00] CKT 1 | 11.3752 | PASS | 0.80524 | PASS | 705.2448 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523967 [POTTER_TR3 3 13.2] CKT 1 | 11.3869 | PASS | 0.80523 | PASS | 705.2327 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523964 [POTTER_TR3 1 13.2] CKT 1 | 11.3869 | PASS | 0.80523 | PASS | 705.2327 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523965 [POTTER_TR3 2 13.2] CKT 1 | 11.3869 | PASS | 0.80523 | PASS | 705.2327 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] TO BUS 523958 [POTTER_TR2 1 13.2] CKT 2 | 11.3808 | PASS | 0.80489 | PASS | 704.893 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523959 [POTTER_CO 6 230.00] TO BUS 523957 [POTTER_TR 1 13.2] CKT 1 | 11.3799 | PASS | 0.80505 | PASS | 705.0454 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 11.3097 | PASS | 0.80355 | PASS | 703.552 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 2 | 11.31 | PASS | 0.8036 | PASS | 703.6 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539800 [CLARKCOUNTY7 345.00] CKT 1 | 11.3684 | PASS | 0.80603 | PASS | 706.0255 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539800 [CLARKCOUNTY7 345.00] CKT 2 | 11.3675 | PASS | 0.80588 | PASS | 705.8826 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539871 [PIXLEY-SOLAR 345.00] CKT 1 | 11.3876 | PASS | 0.80527 | PASS | 705.2655 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 762834 [GEN-2018-049 345.00] CKT 1 | 11.3889 | PASS | 0.80554 | PASS | 705.5368 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.8] CKT 1 | 11.3674 | PASS | 0.80524 | PASS | 705.2371 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 588560 [GEN-2017-011 345.00] TO BUS 588561 [G17-011XFMR1 34.5.00] CKT 1 | 11.3851 | PASS | 0.80568 | PASS | 705.6805 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 763527 [GEN-2019-012 345.00] TO BUS 763528 [G19-012-XFM1 34.5.00] CKT 1 | 11.3905 | PASS | 0.80454 | PASS | 704.5448 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767221 [GEN-2022-012 345.00] TO BUS 767222 [G22-012XFMR1 34.5.00] CKT 1 | 11.3865 | PASS | 0.80534 | PASS | 705.3391 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767301 [GEN-2022-016 345.00] TO BUS 767302 [G22-016XFMR1 34.5.00] CKT 1 | 11.386 | PASS | 0.80556 | PASS | 705.5595 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767301 [GEN-2022-016 345.00] TO BUS 767305 [G22-016XFMR2 34.5.00] CKT 1 | 11.386 | PASS | 0.80556 | PASS | 705.5595 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 767301 [GEN-2022-016 345.00] TO BUS 767321 [GEN-2022-017 345.00] CKT 1 | 11.3856 | PASS | 0.80558 | PASS | 705.5805 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776822 [G23-102XFMR1 34.5.00] CKT 1 | 11.3857 | PASS | 0.80561 | PASS | 705.6111 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776823 [G23-102XFMR2 34.5.00] CKT 1 | 11.3857 | PASS | 0.80561 | PASS | 705.6078 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776824 [G23-102XFMR3 34.5.00] CKT 1 | 11.3857 | PASS | 0.80561 | PASS | 705.6066 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 776821 [GEN-2023-102 345.00] TO BUS 776825 [G23-102XFMR4 34.5.00] CKT 1 | 11.3858 | PASS | 0.80559 | PASS | 705.5881 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 780991 [GEN-2024-134 345.00] TO BUS 780992 [G24-134XFMR1 34.5.00] TO BUS 781007 [G24-134TER1 13.8] CKT 1 | 11.3853 | PASS | 0.80572 | PASS | 705.7182 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 780991 [GEN-2024-134 345.00] TO BUS 780995 [G24-134XFMR2 34.5.00] TO BUS 781008 [G24-134TER2 13.8] CKT 1 | 11.3854 | PASS | 0.80571 | PASS | 705.7119 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 781021 [GEN-2024-135 345.00] TO BUS 781022 [G24-135XFMR1 34.5.00] TO BUS 781037 [G24-135TER1 13.8] CKT 1 | 11.3853 | PASS | 0.80572 | PASS | 705.7182 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 781021 [GEN-2024-135 345.00] TO BUS 781025 [G24-135XFMR2 34.5.00] TO BUS 781038 [G24-135TER2 13.8] CKT 1 | 11.3854 | PASS | 0.80571 | PASS | 705.7119 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 781591 [GEN-2024-154 345.00] TO BUS 781592 [G24-154XFMR1 34.5.00] TO BUS 781607 [G24-154TER1 13.8] CKT 1 | 11.3875 | PASS | 0.80517 | PASS | 705.1684 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784141 [GEN-2024-239 345.00] TO BUS 784142 [G24-239XFMR1 34.5.00] TO BUS 784157 [G24-239TER1 13.8] CKT 1 | 11.3931 | PASS | 0.80416 | PASS | 704.1558 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784530 [GEN-2024-252 345.00] TO BUS 784535 [G24-252XFMR2 34.5.00] TO BUS 784548 [G24-252TER2 13.8] CKT 2 | 11.39 | PASS | 0.80465 | PASS | 704.6461 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 784534 [G24-252GEN1 13.8.00] CKT 1 | 11.2944 | PASS | 0.80443 | PASS | 704.4272 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 784595 [G24-254XFMR2 34.5.00] TO BUS 784608 [G24-254TER2 13.8] CKT 2 | 11.3908 | PASS | 0.80447 | PASS | 704.4745 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 784594 [G24-254GEN1 13.8.00] CKT 1 | 11.2299 | PASS | 0.80401 | PASS | 704.0088 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT1 & 2 | 11.3863 | PASS | 0.807 | PASS | 707.0034 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT1 & 3 | 11.3863 | PASS | 0.807 | PASS | 707.0034 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT2 & 3 | 11.3863 | PASS | 0.807 | PASS | 707.0034 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515554 [BVRCNTY7 345.00] CKT1 & 2 | 10.6721 | PASS | 0.80345 | PASS | 703.4536 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 514934 [DRAPER 7 345.00] CKT1 & 2 | 11.3093 | PASS | 0.80621 | PASS | 706.207 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT1 & 2 | 11.0854 | PASS | 0.79965 | PASS | 699.6541 | 41.89 | 46.95
GEN-2026-PR2 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR2 | 345kV Bus at OGE Tatonga Substation, Dewey County, OK | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539800 [CLARKCOUNTY7 345.00] CKT1 & 2 | 11.2986 | PASS | 0.80678 | PASS | 706.7812 | 41.89 | 46.95

## WSCR
* WSCR is not applicable to this study.