## Executive Summary
Executive Summary: GEN-2026-PR3 Priority Process Study
Interconnection Customer GEN-2026-PR3 (Group 04) has requested a Priority System Impact Study persuant to Section 3.11 of the GIP under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new generation for a total of:
49.68 MW
The minimum cost of interconnecting GEN-2026-PR3 included in this Priority Process is estimated at:
Total Network Upgrade $70,972,000 Steady State Network Upgrade $70,972,000 Stability Network Upgrade $0 Steady State/Stability Network Upgrade $0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR3 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 05/19/2026
Costs for Wind Requests were allocated using the 27L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4616100% | SPP | Final Report Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | 0 | 0 | 0 | 0 | 0 | 0 | 49.68 | 49.68 | -0.3 | ER | OG&E | Otter 138kV | None
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | None
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | None
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR3 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 49.68 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 49.68 | 49.68
GEN-2026-PR3 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 49.68 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 49.68 | 49.68
GEN-2026-PR3 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 49.68 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 49.68 | N/A
GEN-2026-PR3 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 49.68 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 49.68 | N/A
GEN-2026-PR3 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 49.68 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 49.68 | 49.68
GEN-2026-PR3 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 49.68 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 49.68 | 49.68
GEN-2026-PR3 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 49.68 | 49.68 | None | None | N/A | N/A | N/A | 49.68 | N/A | N/A | N/A | N/A | N/A | 49.68
GEN-2026-PR3 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 49.68 | 49.68 | None | None | N/A | N/A | N/A | 49.68 | N/A | N/A | N/A | N/A | N/A | 49.68

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR3 PSIS | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29L | System Intact | 830 | 830 | 107.57 | 108.42 |  |  |  | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR3 PSIS | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP, 29SP | System Intact | 829 | 829 | 109.55 | 109.82 |  |  |  | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
04ALL | GEN-2026-PR3 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 121.12 | 121.56 |  |  |  | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
04ALL | GEN-2026-PR3 PSIS | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29L | System Intact | 830 | 830 | 106.71 | 107.57 |  |  |  | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR3 PSIS | ERIS | Thermal | None | 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS CF | ERIS | Thermal | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS CF | ERIS | Voltage | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS CF | ERIS | Non-Converged | None | 26SP, 29L, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR3 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR3 | GEN-2026-PR3 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 2390 MVA | 0 | 0% | 81488001.7662 | 0.04577
GEN-2026-PR3 | GEN-2026-PR3 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1 | Contingent | Rebuild the existing NEOSHO 7 to G24-240-TAP 345 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | 0 | 0% | 93984002.037 | 0.02184
GEN-2026-PR3 | GEN-2026-PR3 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | Current Study | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1050 MVA* * The minimum required rating has been adjusted to ensure resolution of similar issues identified for the GEN-2026-PR5 and GEN-2026-PR6 projects. | 45914000 | 100% | 45914000 | 0.09711
GEN-2026-PR3 | GEN-2026-PR3 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1 | Current Study | Rebuild the existing VIOLA 7 to G18-128-TAP 345 kV line 1 (11.39 miles) to a minimum rating of 1050 MVA* * The minimum required rating has been adjusted to ensure resolution of similar issues identified for the GEN-2026-PR5 and GEN-2026-PR6 projects. | 25058000 | 100% | 25058000 | 0.09711
GEN-2026-PR3 | GEN-2026-PR3 PSIS | 04 SOUTHEAST | TBD | ERIS | Otter 138 kV Substation GEN-2026-PR3 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR3 (49.68/Wind), into Otter 138 kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR3 | GEN-2026-PR3 PSIS | 04 SOUTHEAST | TBD | ERIS | Otter 138 kV Substation GEN-2026-PR3 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR3 (49.68/Wind), into Otter 138 kV Substation | TBD | 100% | TBD | 1
Total | [7 empty] | 70972000

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR3 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 2390 MVA | WERE | TBD | 81488001.7662
Contingent | GEN-2026-PR3 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1 | TBD | Rebuild the existing NEOSHO 7 to G24-240-TAP 345 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | WERE/AEPW | TBD | 93984002.037
Current Study | GEN-2026-PR3 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR3 PSIS | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1050 MVA* * The minimum required rating has been adjusted to ensure resolution of similar issues identified for the GEN-2026-PR5 and GEN-2026-PR6 projects. | OKGE/WERE | 36 | 45914000
Current Study | GEN-2026-PR3 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR3 PSIS | ERIS | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing VIOLA 7 to G18-128-TAP 345 kV line 1 (11.39 miles) to a minimum rating of 1050 MVA* * The minimum required rating has been adjusted to ensure resolution of similar issues identified for the GEN-2026-PR5 and GEN-2026-PR6 projects. | WERE | 36 | 25058000
Interconnection | GEN-2026-PR3 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR3 PSIS | ERIS | Otter 138 kV Substation GEN-2026-PR3 Interconnection (TOIF) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR3 (49.68/Wind), into Otter 138 kV Substation | OGE | TBD | TBD
Interconnection | GEN-2026-PR3 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR3 PSIS | ERIS | Otter 138 kV Substation GEN-2026-PR3 Interconnection (Non-Shared NU) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR3 (49.68/Wind), into Otter 138 kV Substation | OGE | TBD | TBD
246444003.8033

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR3 | 04 SOUTHEAST | ER | TBD | 503229 | Woodring - Marshall 138 kV Line Rebuild Woodring - Arcadia 345 kV New Line Marshall - Cottonwood Creek 138 kV Line Rebuild Cottonwood Creek - Arcadia 138 kV Line Rebuild | Cottonwood Creek - Arcadia 138 kV Ckt 1 Rebuild | Rebuild 13.67-mile Ckt 1 line from Cottonwood Creek 138 kV substation to Arcadia 138 kV substation | 2025 ITP | Yes | N/A | 0.05575 | TBD | 193890000
GEN-2026-PR3 | 04 SOUTHEAST | ER | TBD | 503892 | Matthewson - Redington 345 kV Line Rebuild Matthewson - Redington 345 kV New Line | Matthewson - Redington 345 kV Ckt 1 Rebuild | Rebuild 22.16-mile Ckt 1 line from Matthewson 345 kV substation to Redington 345 kV substation | 2025 ITP | Yes | N/A | 0.14436 | TBD | 137572000
GEN-2026-PR3 | 04 SOUTHEAST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.03798 | 4821400% | 3304340617.4944
GEN-2026-PR3 | 04 SOUTHEAST | ER | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | N/A | 0.03652 | 4565800% | 647852
GEN-2026-PR3 | 04 SOUTHEAST | ER | 210556 | 112187 | Dover - Henessey 138 kV Ckt 1 Rebuild | Dover - Henessey 138 kV Ckt 1 Rebuild | Rebuild Hennessey - Bull Foot Tap 138kV to rating 268/287 MVA | DISIS-2016-002 | Yes | N/A | 0.08037 | TBD | 20000

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR3 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 3e-05 | 0.0014904 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00377 | -0.18729 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00177 | -0.087934 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00177 | -0.087934 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00095 | -0.047196 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00556 | 0.27622 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.0049 | 0.24343 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -0.00023 | -0.011426 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -0.00023 | -0.011426 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.0008 | 0.039744 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00078 | 0.03875 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.0024 | 0.11923 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00339 | 0.16842 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00056 | -0.027821 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00056 | -0.027821 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00736 | -0.36564 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.00066 | -0.032789 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00024 | 0.011923 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00024 | 0.011923 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.0003 | 0.014904 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00046 | 0.022853 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00019 | 0.0094392 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00022 | 0.01093 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.0004968 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.0004968 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.0004968 | No
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.0004968 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR3 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR3 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.06832 | 109.29 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR3 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03555 | 101.17 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR3 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.06537 | 121.56 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR3 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03473 | 109.82 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 29L | GEN-2026-PR3 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.09711 | 108.42 | System Intact | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 29L | GEN-2026-PR3 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.09711 | 107.57 | System Intact | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Non-Converged | GEN-2026-PR3 PSIS | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR3 PSIS | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS CF | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR3 PSIS CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR3 PSIS CF | 04ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR3 PSIS CF | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR3 PSIS CF | 04ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR3 PSIS CF | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR3 PSIS | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS CF | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR3 PSIS CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.3. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.4. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.5. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on HELENAT2 69.000 (515371) 69 kV Bus a. Apply fault at the HELENAT2 69.000 (515371) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 2 (514716) 69.0 kV to HELENAT2 (515371) 69.0 kV Transmission Circuit #1 b.2. SALINE 2 (514716) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.4. GOLTRY 2 (514720) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.5. HELENAT2 (515371) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.7. HELENAT2 (515371) 69.0 kV to HELENA2 (521121) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 b.2. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.3. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.3. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SUNDCG11 (516022) and SUNDCG21 (516076). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips THNDRG11 (515886) and THNDRG21 (515887). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Protection trips G24-239 (784144), G18-029 (762650) and G21-088 (766112). This was also observed in the base case and CQ unit did not impact the behavior. | Reduce simulation timestep to 1/8th of a cycle, operational steady state fixes (existing caps/taps/gen set points), and protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Voltage protection trips G18-029 (762650) and G21-088 (766112). This was also observed in the base case and CQ unit did not impact the behavior. | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BRCKWND4 138.00 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 138.00 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. KGFSHSW4 (520533) 138.0 kV to EKFSHTP4 (520600) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on BUNCHCK4 138.00 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 138.00 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on COWCRK 2 69.000 (514705) 69 kV Bus a. Apply fault at the COWCRK 2 69.000 (514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to CLEVLND2 (514723) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV to GRANRYT2 (515957) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on SO4TH 2 69.000 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 69.000 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on OTOE 4 138.00 (514737) 138 kV Bus a. Apply fault at the OTOE 4 138.00 (514737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on ORLANDO2 69.000 (514766) 69 kV Bus a. Apply fault at the ORLANDO2 69.000 (514766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on HENESEY4 138.00 (514774) 138 kV Bus a. Apply fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on BRONRD 2 69.000 (514797) 69 kV Bus a. Apply fault at the BRONRD 2 69.000 (514797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on SOONER 4 138.00 (514802) 138 kV Bus a. Apply fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on STILWTR4 138.00 (515011) 138 kV Bus a. Apply fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on DMANCRK4 138.00 (515400) 138 kV Bus a. Apply fault at the DMANCRK4 138.00 (515400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784590) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784591) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on ARMFTWD4 138.00 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4 138.00 (515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 (515694) 138.0 kV to ARMADILLO_HV (516363) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on BULFOOT4 138.00 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 138.00 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on SKELTON7 345.00 (515990) 345 kV Bus a. Apply fault at the SKELTON7 345.00 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 (515990) 345.0 kV to GEN-2016-128 (588190) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on MAVERIK4 138.00 (520580) 138 kV Bus a. Apply fault at the MAVERIK4 138.00 (520580) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAVERIK4 (520580) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on DOVER 4 138.00 (520879) 138 kV Bus a. Apply fault at the DOVER 4 138.00 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2018-011 (762493) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2024-062 (778831) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to DOVERSW2 (520881) 69.0 kV to DVRTERT (521166) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 b.3. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.5. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.6. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.2. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.3. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.5. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at GRNTWDG1 (515660) and GRNTWDG2 (515661). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.4. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.9. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.4. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.5. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.6. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.7. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.8. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.9. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.10. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.2. IMO 4 (514790) 138.0 kV to GLENWD 4 (514734) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on GEN-2016-128345.00 (588190) 345 kV Bus a. Apply Fault at the GEN-2016-128345.00 (588190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-128 (588190) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-128 (588190) 345.0 kV to G16-128XFMR1 (588191) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PERRY 4 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FRMNTAP4 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WAUKOMI4 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FAIRMON4 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on WRVALLY4 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MARSHL 4 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GLENWD 4 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IMO 4 (514790) 138 kV Bus a. Apply Fault at the IMO 4 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on ARMFTL11 (515695) 34.5 kV Bus a. Apply Fault at the ARMFTL11 (515695) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTL11 (515695) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on ARMFTT11 (515698) 13.8 kV Bus a. Apply Fault at the ARMFTT11 (515698) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTT11 (515698) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GARBER 4 (520461) 138 kV Bus a. Apply Fault at the GARBER 4 (520461) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARBER 4 (520461) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on MARSHAL4 (521006) 138 kV Bus a. Apply Fault at the MARSHAL4 (521006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL4 (521006) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WARREN 4 (521100) 138 kV Bus a. Apply Fault at the WARREN 4 (521100) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARREN 4 (521100) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWD11 (515689) 34.5 kV to Load #S1 b.5. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.6. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.7. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.8. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.9. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 22.02 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.12. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.22. CTNWOOD4 (514827) 138.0 kV to Load #1 b.23. PINE ST4 (514829) 138.0 kV to Load #1 b.24. PINE ST4 (514829) 138.0 kV to Load #2 b.25. FITZGRD4 (514830) 138.0 kV to Load #1 b.26. WATRLOO4 (514831) 138.0 kV to Load #1 b.27. UNVRSTY4 (515181) 138.0 kV to Load #1 b.28. LBRTYLK4 (515373) 138.0 kV to Load #1 b.29. MITCHSB4 (515466) 138.0 kV to Load #1 b.30. WHITESB4 (515467) 138.0 kV to Load #1 b.31. MARSHAL4 (521006) 138.0 kV to Load #1 b.32. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.33. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.34. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.35. PINE ST4 (514829) 138.0 kV to Trip Bus # b.36. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.37. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.38. KINZE 4 (515008) 138.0 kV to Trip Bus # b.39. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.40. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.41. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.42. WHITESB4 (515467) 138.0 kV to Trip Bus # b.43. MARSHAL4 (521006) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. SO4TH 4 (514731) 138.0 kV to Load #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. CLEOPLT4 (515562) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.5. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.16. GLASMTN4 (514788) 138.0 kV to Load #1 b.17. GLASMTN4 (514788) 138.0 kV to Load #2 b.18. MENOTAP4 (514789) 138.0 kV to Load #1 b.19. CLEO PL4 (515553) 138.0 kV to Load #1 b.20. GLASMTN4 (514788) 138.0 kV to Trip Bus # b.21. MENOTAP4 (514789) 138.0 kV to Trip Bus # b.22. CLEO PL4 (515553) 138.0 kV to Trip Bus # b.23. CLEOPLT4 (515562) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on OKEENE 4 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 (521016) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Breaker at To Bus #1 b.3. PIC4 (520425) 138.0 kV to Load #1 b.4. CEDRDAL4 (520507) 138.0 kV to Load #1 b.5. PIC4 (520425) 138.0 kV to Trip Bus # b.6. CDRDLTP4 (520848) 138.0 kV to Trip Bus # b.7. CEDRDAL4 (520507) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on TWNLKSW4 (521073) 138 kV Bus a. Apply Fault at the TWNLKSW4 (521073) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Breaker at To Bus #1 b.2. KGFSHSW4 (520533) 138.0 kV to REEDING4 (521037) 138.0 kV Breaker at From Bus #1 b.3. TWNLKJT4 (520847) 138.0 kV to TWNLKSW4 (521073) 138.0 kV Breaker at To Bus #1 b.4. DOVER 4 (520879) 138.0 kV to Load #1 b.5. TWNLAKE4 (520540) 138.0 kV to Load #1 b.6. DOVER 4 (520879) 138.0 kV to Trip Bus # b.7. TWNLAKE4 (520540) 138.0 kV to Trip Bus # b.8. REEDING4 (521037) 138.0 kV to Load #1 b.9. CMBLCRK4 (515930) 138.0 kV to Load #1 b.10. FOURCNT4 (520546) 138.0 kV to Load #1 b.11. CASHION4 (520479) 138.0 kV to Load #1 b.12. REEDING4 (521037) 138.0 kV to Trip Bus # b.13. CMBLTP 4 (520474) 138.0 kV to Trip Bus # b.14. CMBLCRK4 (515930) 138.0 kV to Trip Bus # b.15. FOURCTP4 (520545) 138.0 kV to Trip Bus # b.16. FOURCNT4 (520546) 138.0 kV to Trip Bus # b.17. TWNLKJT4 (520847) 138.0 kV to Trip Bus # b.18. CASHION4 (520479) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Increase acceleration factor to 0.7.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior. | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior. | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661). Switching the fault bus to G18-128-TAP (763421) and performing the event simulation allowed successful clearance of fault. This indicates the simulation crash is sensitive to the proximity between fault location and generator and the crash is not impacted by system state. The generator units are gnet and the simulation was successful indicating possible controller issues. This was also observed in the base case and the CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed at fault clearance. This was also observed in the base case and CQ unit has no impact on this behavior. | Reduction of clearing time 4.5 cycles resolves the issue.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_074 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior. | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_075 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_076 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior. | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG1 (506752). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG2 (506753). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511) and G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips G20-020 (764511). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG1 (506752). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG2 (506753). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511) and G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Real and reactive power oscillations observed at G19-045 (763772). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at GRNTWDG1 (515660) and GRNTWDG2 (515661). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661). Switching the fault bus to G18-128-TAP (763421) and performing the event simulation allowed successful clearance of fault. This indicates the simulation crash is sensitive to the proximity between fault location and generator and the crash is not impacted by system state. The generator units are gnet and the simulation was successful indicating possible controller issues. This was also observed in the base case and the CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.3. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.4. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.5. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on HELENAT2 69.000 (515371) 69 kV Bus a. Apply fault at the HELENAT2 69.000 (515371) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 2 (514716) 69.0 kV to HELENAT2 (515371) 69.0 kV Transmission Circuit #1 b.2. SALINE 2 (514716) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.4. GOLTRY 2 (514720) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.5. HELENAT2 (515371) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.7. HELENAT2 (515371) 69.0 kV to HELENA2 (521121) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 b.2. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.3. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.3. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SUNDCG11 (516022) and SUNDCG21 (516076). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips THNDRG11 (515886) and THNDRG21 (515887). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Protection trips G18-029 (762650) and G21-088 (766112). | Reduce simulation timestep to 1/8th of a cycle, operational steady state fixes (existing caps/taps/gen set points), and protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Voltage protection trips G24-239 (784144), G18-029 (762650) and G21-088 (766112). | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BRCKWND4 138.00 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 138.00 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. KGFSHSW4 (520533) 138.0 kV to EKFSHTP4 (520600) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on BUNCHCK4 138.00 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 138.00 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on COWCRK 2 69.000 (514705) 69 kV Bus a. Apply fault at the COWCRK 2 69.000 (514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to CLEVLND2 (514723) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV to GRANRYT2 (515957) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on SO4TH 2 69.000 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 69.000 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on OTOE 4 138.00 (514737) 138 kV Bus a. Apply fault at the OTOE 4 138.00 (514737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on ORLANDO2 69.000 (514766) 69 kV Bus a. Apply fault at the ORLANDO2 69.000 (514766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on HENESEY4 138.00 (514774) 138 kV Bus a. Apply fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on BRONRD 2 69.000 (514797) 69 kV Bus a. Apply fault at the BRONRD 2 69.000 (514797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on SOONER 4 138.00 (514802) 138 kV Bus a. Apply fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on STILWTR4 138.00 (515011) 138 kV Bus a. Apply fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on DMANCRK4 138.00 (515400) 138 kV Bus a. Apply fault at the DMANCRK4 138.00 (515400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784590) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784591) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on ARMFTWD4 138.00 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4 138.00 (515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 (515694) 138.0 kV to ARMADILLO_HV (516363) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on BULFOOT4 138.00 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 138.00 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on SKELTON7 345.00 (515990) 345 kV Bus a. Apply fault at the SKELTON7 345.00 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 (515990) 345.0 kV to GEN-2016-128 (588190) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on MAVERIK4 138.00 (520580) 138 kV Bus a. Apply fault at the MAVERIK4 138.00 (520580) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAVERIK4 (520580) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on DOVER 4 138.00 (520879) 138 kV Bus a. Apply fault at the DOVER 4 138.00 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2018-011 (762493) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2024-062 (778831) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to DOVERSW2 (520881) 69.0 kV to DVRTERT (521166) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 b.3. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.5. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.6. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.2. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.3. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.5. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at GRNTWDG1 (515660) and GRNTWDG2 (515661). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.4. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.9. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.4. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.5. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.6. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.7. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.8. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.9. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.10. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.2. IMO 4 (514790) 138.0 kV to GLENWD 4 (514734) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on GEN-2016-128345.00 (588190) 345 kV Bus a. Apply Fault at the GEN-2016-128345.00 (588190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-128 (588190) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-128 (588190) 345.0 kV to G16-128XFMR1 (588191) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PERRY 4 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FRMNTAP4 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WAUKOMI4 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FAIRMON4 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on WRVALLY4 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MARSHL 4 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GLENWD 4 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IMO 4 (514790) 138 kV Bus a. Apply Fault at the IMO 4 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on ARMFTL11 (515695) 34.5 kV Bus a. Apply Fault at the ARMFTL11 (515695) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTL11 (515695) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on ARMFTT11 (515698) 13.8 kV Bus a. Apply Fault at the ARMFTT11 (515698) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTT11 (515698) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GARBER 4 (520461) 138 kV Bus a. Apply Fault at the GARBER 4 (520461) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARBER 4 (520461) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on MARSHAL4 (521006) 138 kV Bus a. Apply Fault at the MARSHAL4 (521006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL4 (521006) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WARREN 4 (521100) 138 kV Bus a. Apply Fault at the WARREN 4 (521100) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARREN 4 (521100) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWD11 (515689) 34.5 kV to Load #S1 b.5. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.6. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.7. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.8. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.9. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 22.02 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.12. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.22. CTNWOOD4 (514827) 138.0 kV to Load #1 b.23. PINE ST4 (514829) 138.0 kV to Load #1 b.24. PINE ST4 (514829) 138.0 kV to Load #2 b.25. FITZGRD4 (514830) 138.0 kV to Load #1 b.26. WATRLOO4 (514831) 138.0 kV to Load #1 b.27. UNVRSTY4 (515181) 138.0 kV to Load #1 b.28. LBRTYLK4 (515373) 138.0 kV to Load #1 b.29. MITCHSB4 (515466) 138.0 kV to Load #1 b.30. WHITESB4 (515467) 138.0 kV to Load #1 b.31. MARSHAL4 (521006) 138.0 kV to Load #1 b.32. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.33. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.34. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.35. PINE ST4 (514829) 138.0 kV to Trip Bus # b.36. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.37. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.38. KINZE 4 (515008) 138.0 kV to Trip Bus # b.39. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.40. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.41. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.42. WHITESB4 (515467) 138.0 kV to Trip Bus # b.43. MARSHAL4 (521006) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. SO4TH 4 (514731) 138.0 kV to Load #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. CLEOPLT4 (515562) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.5. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.16. GLASMTN4 (514788) 138.0 kV to Load #1 b.17. GLASMTN4 (514788) 138.0 kV to Load #2 b.18. MENOTAP4 (514789) 138.0 kV to Load #1 b.19. CLEO PL4 (515553) 138.0 kV to Load #1 b.20. GLASMTN4 (514788) 138.0 kV to Trip Bus # b.21. MENOTAP4 (514789) 138.0 kV to Trip Bus # b.22. CLEO PL4 (515553) 138.0 kV to Trip Bus # b.23. CLEOPLT4 (515562) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on OKEENE 4 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 (521016) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Breaker at To Bus #1 b.3. PIC4 (520425) 138.0 kV to Load #1 b.4. CEDRDAL4 (520507) 138.0 kV to Load #1 b.5. PIC4 (520425) 138.0 kV to Trip Bus # b.6. CDRDLTP4 (520848) 138.0 kV to Trip Bus # b.7. CEDRDAL4 (520507) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on TWNLKSW4 (521073) 138 kV Bus a. Apply Fault at the TWNLKSW4 (521073) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Breaker at To Bus #1 b.2. KGFSHSW4 (520533) 138.0 kV to REEDING4 (521037) 138.0 kV Breaker at From Bus #1 b.3. TWNLKJT4 (520847) 138.0 kV to TWNLKSW4 (521073) 138.0 kV Breaker at To Bus #1 b.4. DOVER 4 (520879) 138.0 kV to Load #1 b.5. TWNLAKE4 (520540) 138.0 kV to Load #1 b.6. DOVER 4 (520879) 138.0 kV to Trip Bus # b.7. TWNLAKE4 (520540) 138.0 kV to Trip Bus # b.8. REEDING4 (521037) 138.0 kV to Load #1 b.9. CMBLCRK4 (515930) 138.0 kV to Load #1 b.10. FOURCNT4 (520546) 138.0 kV to Load #1 b.11. CASHION4 (520479) 138.0 kV to Load #1 b.12. REEDING4 (521037) 138.0 kV to Trip Bus # b.13. CMBLTP 4 (520474) 138.0 kV to Trip Bus # b.14. CMBLCRK4 (515930) 138.0 kV to Trip Bus # b.15. FOURCTP4 (520545) 138.0 kV to Trip Bus # b.16. FOURCNT4 (520546) 138.0 kV to Trip Bus # b.17. TWNLKJT4 (520847) 138.0 kV to Trip Bus # b.18. CASHION4 (520479) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Increase acceleration factor to 0.7.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661). Switching the fault bus to G18-128-TAP (763421) and performing the event simulation allowed successful clearance of fault. This indicates the simulation crash is sensitive to the proximity between fault location and generator and the crash is not impacted by system state. The generator units are gnet and the simulation was successful indicating possible controller issues.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed at fault clearance. | Reduction of clearing time 4.5 cycles resolves the issue.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_074 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_075 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_076 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). | Reduce simulation timestep to 1/8th of a cycle and operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG1 (506752). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG2 (506753). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511) and G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips G20-020 (764511). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG1 (506752). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LEBROCG2 (506753). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511) and G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Real and reactive power oscillations observed at G19-045 (763772). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at GRNTWDG1 (515660) and GRNTWDG2 (515661). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661). Switching the fault bus to G18-128-TAP (763421) and performing the event simulation allowed successful clearance of fault. This indicates the simulation crash is sensitive to the proximity between fault location and generator and the crash is not impacted by system state. The generator units are gnet and the simulation was successful indicating possible controller issues.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.3. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.4. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.5. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.1.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on HELENAT2 69.000 (515371) 69 kV Bus a. Apply fault at the HELENAT2 69.000 (515371) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 2 (514716) 69.0 kV to HELENAT2 (515371) 69.0 kV Transmission Circuit #1 b.2. SALINE 2 (514716) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.4. GOLTRY 2 (514720) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.5. HELENAT2 (515371) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.7. HELENAT2 (515371) 69.0 kV to HELENA2 (521121) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 b.2. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.3. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.3. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SUNDCG11 (516022) and SUNDCG21 (516076). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the fault. This was also observed in base case and CQ unit did not impact the behavior. | Fault clearing time was reduced to 1 cycle for both base case and transfer case to simulate the fault event. Reclosing is removed.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at WCGS U1 (532751). This was also observed in the base case and CQ unit did not impact the behavior. Voltage protection trips REDBDPLNW0 (511974), G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at WCGS U1 (532751). This was also observed in the base case and CQ unit did not impact the behavior. Voltage protection trips REDBDPLNW0 (511974), G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BRCKWND4 138.00 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 138.00 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. KGFSHSW4 (520533) 138.0 kV to EKFSHTP4 (520600) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on BUNCHCK4 138.00 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 138.00 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on COWCRK 2 69.000 (514705) 69 kV Bus a. Apply fault at the COWCRK 2 69.000 (514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to CLEVLND2 (514723) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV to GRANRYT2 (515957) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on SO4TH 2 69.000 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 69.000 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on OTOE 4 138.00 (514737) 138 kV Bus a. Apply fault at the OTOE 4 138.00 (514737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on ORLANDO2 69.000 (514766) 69 kV Bus a. Apply fault at the ORLANDO2 69.000 (514766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on HENESEY4 138.00 (514774) 138 kV Bus a. Apply fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on BRONRD 2 69.000 (514797) 69 kV Bus a. Apply fault at the BRONRD 2 69.000 (514797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on SOONER 4 138.00 (514802) 138 kV Bus a. Apply fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on STILWTR4 138.00 (515011) 138 kV Bus a. Apply fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on DMANCRK4 138.00 (515400) 138 kV Bus a. Apply fault at the DMANCRK4 138.00 (515400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784590) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784591) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Increase acceleration factor to 0.9.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on ARMFTWD4 138.00 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4 138.00 (515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 (515694) 138.0 kV to ARMADILLO_HV (516363) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on BULFOOT4 138.00 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 138.00 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on SKELTON7 345.00 (515990) 345 kV Bus a. Apply fault at the SKELTON7 345.00 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 (515990) 345.0 kV to GEN-2016-128 (588190) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on MAVERIK4 138.00 (520580) 138 kV Bus a. Apply fault at the MAVERIK4 138.00 (520580) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAVERIK4 (520580) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on DOVER 4 138.00 (520879) 138 kV Bus a. Apply fault at the DOVER 4 138.00 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2018-011 (762493) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2024-062 (778831) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to DOVERSW2 (520881) 69.0 kV to DVRTERT (521166) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 b.3. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.5. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.6. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.2. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.3. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.5. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.4. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.9. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.4. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.5. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.6. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.7. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.8. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.9. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.10. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.2. IMO 4 (514790) 138.0 kV to GLENWD 4 (514734) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on GEN-2016-128345.00 (588190) 345 kV Bus a. Apply Fault at the GEN-2016-128345.00 (588190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-128 (588190) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-128 (588190) 345.0 kV to G16-128XFMR1 (588191) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PERRY 4 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FRMNTAP4 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WAUKOMI4 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FAIRMON4 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on WRVALLY4 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MARSHL 4 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GLENWD 4 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IMO 4 (514790) 138 kV Bus a. Apply Fault at the IMO 4 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on ARMFTL11 (515695) 34.5 kV Bus a. Apply Fault at the ARMFTL11 (515695) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTL11 (515695) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on ARMFTT11 (515698) 13.8 kV Bus a. Apply Fault at the ARMFTT11 (515698) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTT11 (515698) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GARBER 4 (520461) 138 kV Bus a. Apply Fault at the GARBER 4 (520461) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARBER 4 (520461) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on MARSHAL4 (521006) 138 kV Bus a. Apply Fault at the MARSHAL4 (521006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL4 (521006) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WARREN 4 (521100) 138 kV Bus a. Apply Fault at the WARREN 4 (521100) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARREN 4 (521100) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWD11 (515689) 34.5 kV to Load #S1 b.5. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.6. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.7. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.8. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.9. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 22.02 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.12. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.22. CTNWOOD4 (514827) 138.0 kV to Load #1 b.23. PINE ST4 (514829) 138.0 kV to Load #1 b.24. PINE ST4 (514829) 138.0 kV to Load #2 b.25. FITZGRD4 (514830) 138.0 kV to Load #1 b.26. WATRLOO4 (514831) 138.0 kV to Load #1 b.27. UNVRSTY4 (515181) 138.0 kV to Load #1 b.28. LBRTYLK4 (515373) 138.0 kV to Load #1 b.29. MITCHSB4 (515466) 138.0 kV to Load #1 b.30. WHITESB4 (515467) 138.0 kV to Load #1 b.31. MARSHAL4 (521006) 138.0 kV to Load #1 b.32. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.33. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.34. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.35. PINE ST4 (514829) 138.0 kV to Trip Bus # b.36. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.37. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.38. KINZE 4 (515008) 138.0 kV to Trip Bus # b.39. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.40. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.41. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.42. WHITESB4 (515467) 138.0 kV to Trip Bus # b.43. MARSHAL4 (521006) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. SO4TH 4 (514731) 138.0 kV to Load #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. CLEOPLT4 (515562) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.5. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.16. GLASMTN4 (514788) 138.0 kV to Load #1 b.17. GLASMTN4 (514788) 138.0 kV to Load #2 b.18. MENOTAP4 (514789) 138.0 kV to Load #1 b.19. CLEO PL4 (515553) 138.0 kV to Load #1 b.20. GLASMTN4 (514788) 138.0 kV to Trip Bus # b.21. MENOTAP4 (514789) 138.0 kV to Trip Bus # b.22. CLEO PL4 (515553) 138.0 kV to Trip Bus # b.23. CLEOPLT4 (515562) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on OKEENE 4 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 (521016) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Breaker at To Bus #1 b.3. PIC4 (520425) 138.0 kV to Load #1 b.4. CEDRDAL4 (520507) 138.0 kV to Load #1 b.5. PIC4 (520425) 138.0 kV to Trip Bus # b.6. CDRDLTP4 (520848) 138.0 kV to Trip Bus # b.7. CEDRDAL4 (520507) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on TWNLKSW4 (521073) 138 kV Bus a. Apply Fault at the TWNLKSW4 (521073) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Breaker at To Bus #1 b.2. KGFSHSW4 (520533) 138.0 kV to REEDING4 (521037) 138.0 kV Breaker at From Bus #1 b.3. TWNLKJT4 (520847) 138.0 kV to TWNLKSW4 (521073) 138.0 kV Breaker at To Bus #1 b.4. DOVER 4 (520879) 138.0 kV to Load #1 b.5. TWNLAKE4 (520540) 138.0 kV to Load #1 b.6. DOVER 4 (520879) 138.0 kV to Trip Bus # b.7. TWNLAKE4 (520540) 138.0 kV to Trip Bus # b.8. REEDING4 (521037) 138.0 kV to Load #1 b.9. CMBLCRK4 (515930) 138.0 kV to Load #1 b.10. FOURCNT4 (520546) 138.0 kV to Load #1 b.11. CASHION4 (520479) 138.0 kV to Load #1 b.12. REEDING4 (521037) 138.0 kV to Trip Bus # b.13. CMBLTP 4 (520474) 138.0 kV to Trip Bus # b.14. CMBLCRK4 (515930) 138.0 kV to Trip Bus # b.15. FOURCTP4 (520545) 138.0 kV to Trip Bus # b.16. FOURCNT4 (520546) 138.0 kV to Trip Bus # b.17. TWNLKJT4 (520847) 138.0 kV to Trip Bus # b.18. CASHION4 (520479) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trip G19-002 (763475). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the fault. This was also observed in base case and CQ unit did not impact the behavior. | Fault clearing time was reduced to 1 cycle for both base case and transfer case to simulate the fault event fully. Reclosing is removed.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.1.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).Reactive power oscillations observed at G20-087 (764556, 764559). This was also observed in the base case and CQ unit did not impact the behavior. | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Increase acceleration factor to 0.9.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the fault. This was also observed in base case and CQ unit did not impact the behavior. | Fault clearing time was reduced to 1 cycle for both base case and transfer case to simulate the fault event fully. Reclosing is removed.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_074 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_075 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_076 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511) and G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips G18-064 (763002). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trip G19-002 (763475). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511) and G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips G18-064 (763002). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trip G19-002 (763475). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Voltage protection trips G22-145 (769884). | Operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Reactive power oscillations observed at G20-087 (764556, 764559). Voltage protection trips G22-145 (769884). | Operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at WCGS U1 (532751). This was also observed in the base case and CQ unit did not impact the behavior.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.3. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.4. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.5. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.1.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on HELENAT2 69.000 (515371) 69 kV Bus a. Apply fault at the HELENAT2 69.000 (515371) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 2 (514716) 69.0 kV to HELENAT2 (515371) 69.0 kV Transmission Circuit #1 b.2. SALINE 2 (514716) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.4. GOLTRY 2 (514720) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.5. HELENAT2 (515371) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.7. HELENAT2 (515371) 69.0 kV to HELENA2 (521121) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 b.2. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.3. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.3. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips SUNDCG11 (516022) and SUNDCG21 (516076). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the fault. | Fault clearing time was reduced to 1 cycle for both base case and transfer case to simulate the fault event. Reclosing is removed.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at WCGS U1 (532751). Voltage protection trips REDBDPLNW0 (511974), G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at WCGS U1 (532751). Voltage protection trips REDBDPLNW0 (511974), G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on BRCKWND4 138.00 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 138.00 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to THUNDER7 (515894) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. KGFSHSW4 (520533) 138.0 kV to EKFSHTP4 (520600) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on BUNCHCK4 138.00 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 138.00 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on COWCRK 2 69.000 (514705) 69 kV Bus a. Apply fault at the COWCRK 2 69.000 (514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on OTTER 4 138.00 (514708) 138 kV Bus a. Apply fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on IMO 2 69.000 (514721) 69 kV Bus a. Apply fault at the IMO 2 69.000 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to CLEVLND2 (514723) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CLEVLND2 69.000 (514723) 69 kV Bus a. Apply fault at the CLEVLND2 69.000 (514723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVLND2 (514723) 69.0 kV to GRANRYT2 (515957) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on SO4TH 2 69.000 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 69.000 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on OTOE 4 138.00 (514737) 138 kV Bus a. Apply fault at the OTOE 4 138.00 (514737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on ORLANDO2 69.000 (514766) 69 kV Bus a. Apply fault at the ORLANDO2 69.000 (514766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on NE ENID4 138.00 (514769) 138 kV Bus a. Apply fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on HENESEY4 138.00 (514774) 138 kV Bus a. Apply fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on MENOTAP4 138.00 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 138.00 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on BRONRD 2 69.000 (514797) 69 kV Bus a. Apply fault at the BRONRD 2 69.000 (514797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on SOONER 4 138.00 (514802) 138 kV Bus a. Apply fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on STILWTR4 138.00 (515011) 138 kV Bus a. Apply fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on DMANCRK4 138.00 (515400) 138 kV Bus a. Apply fault at the DMANCRK4 138.00 (515400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784590) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to GEN-2024-254 (784591) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-029 (762650) and G21-088 (766112). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Increase acceleration factor to 0.9.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on ARMFTWD4 138.00 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4 138.00 (515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 (515694) 138.0 kV to ARMADILLO_HV (516363) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on BULFOOT4 138.00 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 138.00 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 (515960) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on SKELTON7 345.00 (515990) 345 kV Bus a. Apply fault at the SKELTON7 345.00 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 (515990) 345.0 kV to GEN-2016-128 (588190) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on BULFTTP4 138.00 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 138.00 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 (520535) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on MAVERIK4 138.00 (520580) 138 kV Bus a. Apply fault at the MAVERIK4 138.00 (520580) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAVERIK4 (520580) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on NKNGFSH4 138.00 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 138.00 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 (520603) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on DOVER 4 138.00 (520879) 138 kV Bus a. Apply fault at the DOVER 4 138.00 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2018-011 (762493) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to GEN-2024-062 (778831) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on DOVERSW4 138.00 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 138.00 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 (520882) 138.0 kV to DOVERSW2 (520881) 69.0 kV to DVRTERT (521166) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips MAVWTG1 (520587), MAVWTG2 (520588), MAVWTG3 (520589), and MAVWTG4 (520590). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 b.3. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.5. COWCRK 4 (514706) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.6. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 b.4. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on NE ENID4 138.00 (514769) 138 kV Bus a. Apply Fault at the NE ENID4 138.00 (514769) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.2. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.3. NE ENID2 (514732) 69.0 kV to NE ENID4 (514769) 138.0 kV to NE ENID1 (515741) 13.8 kV Three Winding #3 b.4. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.5. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.3. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.4. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.9. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.4. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRCKWND4 (514642) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.4. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.5. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HENESEY4 138.00 (514774) 138 kV Bus a. Apply Fault at the HENESEY4 138.00 (514774) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.2. HENESEY4 (514774) 138.0 kV to BULFTTP4 (520535) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.6. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.7. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.8. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.9. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.10. WOODRNG7 (514715) 345.0 kV to GEN-2017-164 (762321) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.2. IMO 4 (514790) 138.0 kV to GLENWD 4 (514734) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Reactive power oscillations observed at G20-087 (764556, 764559). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on GEN-2016-128345.00 (588190) 345 kV Bus a. Apply Fault at the GEN-2016-128345.00 (588190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-128 (588190) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-128 (588190) 345.0 kV to G16-128XFMR1 (588191) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PERRY 4 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FRMNTAP4 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WAUKOMI4 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FAIRMON4 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on WRVALLY4 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MARSHL 4 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GLENWD 4 (514734) 138 kV Bus a. Apply Fault at the GLENWD 4 (514734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENWD 4 (514734) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on IMO 4 (514790) 138 kV Bus a. Apply Fault at the IMO 4 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 4 (514790) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on ARMFTL11 (515695) 34.5 kV Bus a. Apply Fault at the ARMFTL11 (515695) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTL11 (515695) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on ARMFTT11 (515698) 13.8 kV Bus a. Apply Fault at the ARMFTT11 (515698) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMFTT11 (515698) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GARBER 4 (520461) 138 kV Bus a. Apply Fault at the GARBER 4 (520461) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARBER 4 (520461) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on MARSHAL4 (521006) 138 kV Bus a. Apply Fault at the MARSHAL4 (521006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL4 (521006) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WARREN 4 (521100) 138 kV Bus a. Apply Fault at the WARREN 4 (521100) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARREN 4 (521100) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | GRDA | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWD11 (515689) 34.5 kV to Load #S1 b.5. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.6. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.7. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.8. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.9. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 22.02 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.12. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.22. CTNWOOD4 (514827) 138.0 kV to Load #1 b.23. PINE ST4 (514829) 138.0 kV to Load #1 b.24. PINE ST4 (514829) 138.0 kV to Load #2 b.25. FITZGRD4 (514830) 138.0 kV to Load #1 b.26. WATRLOO4 (514831) 138.0 kV to Load #1 b.27. UNVRSTY4 (515181) 138.0 kV to Load #1 b.28. LBRTYLK4 (515373) 138.0 kV to Load #1 b.29. MITCHSB4 (515466) 138.0 kV to Load #1 b.30. WHITESB4 (515467) 138.0 kV to Load #1 b.31. MARSHAL4 (521006) 138.0 kV to Load #1 b.32. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.33. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.34. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.35. PINE ST4 (514829) 138.0 kV to Trip Bus # b.36. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.37. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.38. KINZE 4 (515008) 138.0 kV to Trip Bus # b.39. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.40. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.41. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.42. WHITESB4 (515467) 138.0 kV to Trip Bus # b.43. MARSHAL4 (521006) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 b.6. SO4TH 4 (514731) 138.0 kV to Load #1 | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_OKGE_FAULT_006 | Single Phase Fault with Stuck Breaker on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. CLEOPLT4 (515562) 138.0 kV to MENOTAP4 (514789) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.5. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.16. GLASMTN4 (514788) 138.0 kV to Load #1 b.17. GLASMTN4 (514788) 138.0 kV to Load #2 b.18. MENOTAP4 (514789) 138.0 kV to Load #1 b.19. CLEO PL4 (515553) 138.0 kV to Load #1 b.20. GLASMTN4 (514788) 138.0 kV to Trip Bus # b.21. MENOTAP4 (514789) 138.0 kV to Trip Bus # b.22. CLEO PL4 (515553) 138.0 kV to Trip Bus # b.23. CLEOPLT4 (515562) 138.0 kV to Trip Bus # | OKGE | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on OKEENE 4 (521016) 138 kV Bus a. Apply Fault at the OKEENE 4 (521016) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVERSW4 (520882) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Breaker at To Bus #1 b.3. PIC4 (520425) 138.0 kV to Load #1 b.4. CEDRDAL4 (520507) 138.0 kV to Load #1 b.5. PIC4 (520425) 138.0 kV to Trip Bus # b.6. CDRDLTP4 (520848) 138.0 kV to Trip Bus # b.7. CEDRDAL4 (520507) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on TWNLKSW4 (521073) 138 kV Bus a. Apply Fault at the TWNLKSW4 (521073) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. DOVER 4 (520879) 138.0 kV to DOVERSW4 (520882) 138.0 kV Breaker at To Bus #1 b.2. KGFSHSW4 (520533) 138.0 kV to REEDING4 (521037) 138.0 kV Breaker at From Bus #1 b.3. TWNLKJT4 (520847) 138.0 kV to TWNLKSW4 (521073) 138.0 kV Breaker at To Bus #1 b.4. DOVER 4 (520879) 138.0 kV to Load #1 b.5. TWNLAKE4 (520540) 138.0 kV to Load #1 b.6. DOVER 4 (520879) 138.0 kV to Trip Bus # b.7. TWNLAKE4 (520540) 138.0 kV to Trip Bus # b.8. REEDING4 (521037) 138.0 kV to Load #1 b.9. CMBLCRK4 (515930) 138.0 kV to Load #1 b.10. FOURCNT4 (520546) 138.0 kV to Load #1 b.11. CASHION4 (520479) 138.0 kV to Load #1 b.12. REEDING4 (521037) 138.0 kV to Trip Bus # b.13. CMBLTP 4 (520474) 138.0 kV to Trip Bus # b.14. CMBLCRK4 (515930) 138.0 kV to Trip Bus # b.15. FOURCTP4 (520545) 138.0 kV to Trip Bus # b.16. FOURCNT4 (520546) 138.0 kV to Trip Bus # b.17. TWNLKJT4 (520847) 138.0 kV to Trip Bus # b.18. CASHION4 (520479) 138.0 kV to Trip Bus # | WFEC | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trip G19-002 (763475). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the fault. | Fault clearing time was reduced to 1 cycle for both base case and transfer case to simulate the fault event fully. Reclosing is removed.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.1.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Increase acceleration factor to 0.9.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the fault. | Fault clearing time was reduced to 1 cycle for both base case and transfer case to simulate the fault event fully. Reclosing is removed.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_074 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324). | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_075 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_076 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips G18-064 (763002). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trip G19-002 (763475). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-111 (769204). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412). Voltage protection trips G18-064 (763002). | Reduce simulation timestep to 1/8th of a cycle and protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection trip G19-002 (763475). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Voltage protection trips G22-145 (769884). | Operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-024 (762595), G22-136 (769704), G22-143 (769844), and G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the fault. | Reduce acceleration factor to 0.3.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412). | Reduce simulation timestep to 1/8th of a cycle
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL_1 (523170) and GOODWELL_2 (523171). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Reactive power oscillations observed at G20-087 (764556, 764559). Voltage protection trips G22-145 (769884). | Operational steady state fixes (existing caps/taps/gen set points). Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G20-020 (764511). | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips 1ANO U1 (337910) and 1ANO U2 (337911). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G18-064 (763002). | Protection disabled with no impact on stability.
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at WCGS U1 (532751).
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Protection trips G24-239 (784144), G18-029 (762650) and G21-088 (766112).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324). Voltage protection trips G18-029 (762650) and G21-088 (766112).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing fault.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_074 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P1_REGIONAL_FAULT_076 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G17-141 (760412), G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29S | Base | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to dynamic models at GRNTWDG1 (515660) and GRNTWDG2 (515661).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at WCGS U1 (532751). Voltage protection trips REDBDPLNW0 (511974), G18-029 (762650) and G21-088 (766112).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed at WCGS U1 (532751). Voltage protection trips REDBDPLNW0 (511974), G18-029 (762650) and G21-088 (766112).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).Reactive power oscillations observed at G20-087 (764556, 764559).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Simulation crashed following the fault.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_076 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Simulation crashed following the fault.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | No | No | No | No | No | No | No | Simulation crashed following the fault.
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115 (763321, 763324).
04 SOUTHEAST | GEN-2026-PR3 PSIS | 29W | Base | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at WCGS U1 (532751).

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR3 | 04 SOUTHEAST | 515694 | ARMFTWD4 | 138 | 11.8265 | 12.0604 | 0.2339
GEN-2026-PR3 | 04 SOUTHEAST | 516363 | ARMADILLO_HV | 138 | 11.6177 | 11.8516 | 0.2339
GEN-2026-PR3 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 11.8579 | 12.0911 | 0.2332
GEN-2026-PR3 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 21.3734 | 21.4478 | 0.0744
GEN-2026-PR3 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.8629 | 19.9233 | 0.0604
GEN-2026-PR3 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 9.9225 | 9.9632 | 0.0407
GEN-2026-PR3 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 16.9844 | 17.0213 | 0.0369
GEN-2026-PR3 | 04 SOUTHEAST | 514731 | SO4TH 4 | 138 | 16.6012 | 16.6345 | 0.0333
GEN-2026-PR3 | 04 SOUTHEAST | 514712 | FAIRMON4 | 138 | 15.2303 | 15.2587 | 0.0284
GEN-2026-PR3 | 04 SOUTHEAST | 515641 | PLNSMEN4 | 138 | 15.0778 | 15.105 | 0.0272
GEN-2026-PR3 | 04 SOUTHEAST | 514815 | BRECKNR4 | 138 | 15.1256 | 15.1509 | 0.0253
GEN-2026-PR3 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 13.3797 | 13.4015 | 0.0218
GEN-2026-PR3 | 04 SOUTHEAST | 515383 | ENIDINT4 | 138 | 14.0603 | 14.0816 | 0.0213
GEN-2026-PR3 | 04 SOUTHEAST | 521100 | WARREN 4 | 138 | 6.8419 | 6.8592 | 0.0173
GEN-2026-PR3 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 12.6929 | 12.7089 | 0.016
GEN-2026-PR3 | 04 SOUTHEAST | 514790 | IMO 4 | 138 | 12.5769 | 12.5922 | 0.0153
GEN-2026-PR3 | 04 SOUTHEAST | 514710 | WAUKOMI4 | 138 | 11.0603 | 11.0716 | 0.0113
GEN-2026-PR3 | 04 SOUTHEAST | 514734 | GLENWD 4 | 138 | 10.8007 | 10.8115 | 0.0108
GEN-2026-PR3 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 15.1441 | 15.1527 | 0.0086
GEN-2026-PR3 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 15.1681 | 15.1767 | 0.0086
GEN-2026-PR3 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.7932 | 20.8014 | 0.0082
GEN-2026-PR3 | 04 SOUTHEAST | 778650 | G24-056-TAP | 138 | 11.2867 | 11.2941 | 0.0074
GEN-2026-PR3 | 04 SOUTHEAST | 778651 | GEN-2024-056 | 138 | 11.1486 | 11.1557 | 0.0071
GEN-2026-PR3 | 04 SOUTHEAST | 520461 | GARBER 4 | 138 | 4.8032 | 4.8103 | 0.0071
GEN-2026-PR3 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.6169 | 32.6236 | 0.0067
GEN-2026-PR3 | 04 SOUTHEAST | 514642 | BRCKWND4 | 138 | 8.5727 | 8.5791 | 0.0064
GEN-2026-PR3 | 04 SOUTHEAST | 514730 | SO4TH 2 | 69 | 13.1804 | 13.1866 | 0.0062
GEN-2026-PR3 | 04 SOUTHEAST | 514774 | HENESEY4 | 138 | 10.1019 | 10.1079 | 0.006
GEN-2026-PR3 | 04 SOUTHEAST | 520535 | BULFTTP4 | 138 | 10.7981 | 10.804 | 0.0059
GEN-2026-PR3 | 04 SOUTHEAST | 514721 | IMO 2 | 69 | 12.0657 | 12.0702 | 0.0045
GEN-2026-PR3 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.147 | 8.1515 | 0.0045
GEN-2026-PR3 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.147 | 8.1515 | 0.0045
GEN-2026-PR3 | 04 SOUTHEAST | 514722 | CLEVETP2 | 69 | 11.5917 | 11.596 | 0.0043
GEN-2026-PR3 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 45.0298 | 45.034 | 0.0042
GEN-2026-PR3 | 04 SOUTHEAST | 515456 | CHSTNTT2 | 69 | 11.3397 | 11.3435 | 0.0038
GEN-2026-PR3 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.357 | 18.3606 | 0.0036
GEN-2026-PR3 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 19.505 | 19.5086 | 0.0036
GEN-2026-PR3 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 19.5 | 19.5035 | 0.0035
GEN-2026-PR3 | 04 SOUTHEAST | 784591 | GEN-2024-254 | 345 | 39.7774 | 39.7808 | 0.0034
GEN-2026-PR3 | 04 SOUTHEAST | 784590 | GEN-2024-254 | 345 | 39.2485 | 39.2518 | 0.0033
GEN-2026-PR3 | 04 SOUTHEAST | 514727 | ENID 2 | 69 | 10.5523 | 10.5556 | 0.0033
GEN-2026-PR3 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 45.4633 | 45.4666 | 0.0033
GEN-2026-PR3 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 40.2079 | 40.211 | 0.0031
GEN-2026-PR3 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 42.596 | 42.5988 | 0.0028
GEN-2026-PR3 | 04 SOUTHEAST | 514789 | MENOTAP4 | 138 | 7.2185 | 7.2212 | 0.0027
GEN-2026-PR3 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 40.5635 | 40.5661 | 0.0026
GEN-2026-PR3 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 9.6396 | 9.6422 | 0.0026
GEN-2026-PR3 | 04 SOUTHEAST | 777841 | GEN-2024-029 | 138 | 9.7838 | 9.7864 | 0.0026
GEN-2026-PR3 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 9.9483 | 9.9509 | 0.0026
GEN-2026-PR3 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.5951 | 17.5974 | 0.0023
GEN-2026-PR3 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.6594 | 17.6617 | 0.0023
GEN-2026-PR3 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.8581 | 11.8603 | 0.0022
GEN-2026-PR3 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 33.7238 | 33.726 | 0.0022
GEN-2026-PR3 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.4266 | 30.4287 | 0.0021
GEN-2026-PR3 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 34.1518 | 34.1538 | 0.002
GEN-2026-PR3 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.5867 | 14.5884 | 0.0017
GEN-2026-PR3 | 04 SOUTHEAST | 516100 | HORIZON4 | 138 | 6.6944 | 6.696 | 0.0016
GEN-2026-PR3 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.3841 | 12.3856 | 0.0015
GEN-2026-PR3 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.5064 | 14.5077 | 0.0013
GEN-2026-PR3 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.0621 | 15.0631 | 0.001
GEN-2026-PR3 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.3222 | 21.3232 | 0.001
GEN-2026-PR3 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.7399 | 21.7408 | 0.0009
GEN-2026-PR3 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.1698 | 8.1706 | 0.0008
GEN-2026-PR3 | 04 SOUTHEAST | 514718 | VANCE 2 | 69 | 6.8428 | 6.8434 | 0.0006
GEN-2026-PR3 | 04 SOUTHEAST | 516207 | GADWALL7 | 345 | 15.7428 | 15.7433 | 0.0005
GEN-2026-PR3 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.143 | 9.1434 | 0.0004
GEN-2026-PR3 | 04 SOUTHEAST | 516036 | TRAV3WD7 | 345 | 9.1299 | 9.1302 | 0.0003
GEN-2026-PR3 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 5.6399 | 5.6401 | 0.0002
GEN-2026-PR3 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.7111 | 13.7113 | 0.0002
GEN-2026-PR3 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.6891 | 13.6893 | 0.0002
GEN-2026-PR3 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 5.3298 | 5.33 | 0.0002
GEN-2026-PR3 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 19.1395 | 19.1396 | 0.0001
GEN-2026-PR3 | 04 SOUTHEAST | 515975 | G15-066T | 345 | 19.6732 | 19.6731 | -0.0001
GEN-2026-PR3 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.6238 | 13.6236 | -0.0002
GEN-2026-PR3 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 21.9551 | 21.9545 | -0.0006
GEN-2026-PR3 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 19.4188 | 19.4181 | -0.0007
GEN-2026-PR3 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.8922 | 20.8914 | -0.0008
GEN-2026-PR3 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 20.9536 | 20.9528 | -0.0008
GEN-2026-PR3 | 04 SOUTHEAST | 514701 | BUNCHCK4 | 138 | 6.6842 | 6.6833 | -0.0009
GEN-2026-PR3 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 14.7756 | 14.7746 | -0.001
GEN-2026-PR3 | 04 SOUTHEAST | 514800 | BRRDTP 2 | 69 | 1.9011 | 1.8998 | -0.0013
GEN-2026-PR3 | 04 SOUTHEAST | 521034 | PERRY 2 | 69 | 2.3394 | 2.3379 | -0.0015
GEN-2026-PR3 | 04 SOUTHEAST | 515646 | GRNTWD 7 | 345 | 10.4943 | 10.4927 | -0.0016
GEN-2026-PR3 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12 | 11.9984 | -0.0016
GEN-2026-PR3 | 04 SOUTHEAST | 514768 | WF KAY 2 | 69 | 3.2722 | 3.2703 | -0.0019
GEN-2026-PR3 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.6539 | 4.6518 | -0.0021
GEN-2026-PR3 | 04 SOUTHEAST | 763421 | G18-128-TAP | 345 | 11.1963 | 11.1942 | -0.0021
GEN-2026-PR3 | 04 SOUTHEAST | 515544 | RENFROW4 | 138 | 13.983 | 13.9798 | -0.0032

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR3 | 2.6485 | FAIL | 0.35484 | PASS | None | PASS | YES

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | base | 7.0845 | PASS | 0.35485 | PASS | 254.8451 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514707 [PERRY 4 138.00] CKT 1 | 6.7064 | PASS | 0.35532 | PASS | 255.3241 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 4.5842 | FAIL | 0.35949 | PASS | 259.494 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 515006 [MORRISN4 138.00] CKT 1 | 6.9514 | PASS | 0.35503 | PASS | 255.0265 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 6.9539 | PASS | 0.35502 | PASS | 255.0241 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514707 [PERRY 4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 6.7101 | PASS | 0.3553 | PASS | 255.2982 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 4.576 | FAIL | 0.35962 | PASS | 259.6221 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 2.6485 | FAIL | 0.36919 | PASS | 269.1874 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514712 [FAIRMON4 138.00] CKT 1 | 7.046 | PASS | 0.35494 | PASS | 254.9378 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 7.0016 | PASS | 0.35505 | PASS | 255.0453 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 7.0689 | PASS | 0.35488 | PASS | 254.8846 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514711 [WAUKOTP4 138.00] CKT 1 | 6.8951 | PASS | 0.35513 | PASS | 255.1252 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 7.0232 | PASS | 0.35498 | PASS | 254.9781 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 7.0836 | PASS | 0.35485 | PASS | 254.8545 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514712 [FAIRMON4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 7.0463 | PASS | 0.35493 | PASS | 254.9328 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 7.0802 | PASS | 0.35487 | PASS | 254.8655 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514733 [MARSHL 4 138.00] CKT 1 | 6.9077 | PASS | 0.35508 | PASS | 255.0794 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 7.048 | PASS | 0.35488 | PASS | 254.8818 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 6.9266 | PASS | 0.35495 | PASS | 254.9505 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 7.0857 | PASS | 0.35485 | PASS | 254.8522 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.0053 | PASS | 0.35489 | PASS | 254.8919 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 7.0854 | PASS | 0.35485 | PASS | 254.8503 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 6.9072 | PASS | 0.35508 | PASS | 255.0781 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 521006 [MARSHAL4 138.00] CKT Z1 | 7.0843 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 6.9432 | PASS | 0.355 | PASS | 255.0021 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.0035 | PASS | 0.35489 | PASS | 254.8877 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 6.4314 | PASS | 0.35581 | PASS | 255.8127 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 6.9466 | PASS | 0.35503 | PASS | 255.0312 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 6.8617 | PASS | 0.35521 | PASS | 255.2083 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515477 [CHSHLMV7 345.00] CKT 1 | 7.0847 | PASS | 0.35485 | PASS | 254.8489 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515543 [RENFROW7 345.00] CKT 1 | 7.0471 | PASS | 0.35487 | PASS | 254.8743 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 6.9241 | PASS | 0.35494 | PASS | 254.9407 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 7.0847 | PASS | 0.35485 | PASS | 254.8475 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 588190 [GEN-2016-128 345.00] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8482 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 516010 [PINTAIL7 345.00] TO BUS 516019 [KINGWD 7 345.00] CKT Z1 | 7.0848 | PASS | 0.35485 | PASS | 254.8471 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 520461 [GARBER 4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 7.0848 | PASS | 0.35485 | PASS | 254.8474 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762342 [GEN-2017-178 345.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8459 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 778650 [G24-056-TAP 138.00] TO BUS 778651 [GEN-2024-056 138.00] CKT 0 | 7.0901 | PASS | 0.35484 | PASS | 254.8401 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514768 [WF KAY 2 69.00] CKT 1 | 7.0833 | PASS | 0.35485 | PASS | 254.8509 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514706 [COWCRK 4 138.00] TO BUS 515717 [COWCRK 1 13.8] CKT 2 | 7.0833 | PASS | 0.35485 | PASS | 254.8509 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514774 [HENESEY4 138.00] CKT 1 | 6.896 | PASS | 0.35512 | PASS | 255.1197 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514715 [WOODRNG7 345.00] TO BUS 515770 [WOODRNG1 13.8] CKT 2 | 5.8929 | FAIL | 0.35598 | PASS | 255.9808 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514790 [IMO 4 138.00] CKT 1 | 7.0592 | PASS | 0.35491 | PASS | 254.9077 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8467 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514730 [SO4TH 2 69.00] TO BUS 515758 [SO4TH 1 13.2] CKT 1 | 7.0815 | PASS | 0.35486 | PASS | 254.8567 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514704 [MILLERT4 138.00] CKT 1 | 7.0839 | PASS | 0.35485 | PASS | 254.8486 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514798 [SNRPMPT4 138.00] CKT 1 | 7.084 | PASS | 0.35485 | PASS | 254.8475 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514805 [SOONER1G 22.00] CKT 1 | 6.9393 | PASS | 0.35498 | PASS | 254.9805 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514803 [SOONER 7 345.00] TO BUS 515760 [SOONER 1 13.8] CKT 5 | 6.9771 | PASS | 0.35499 | PASS | 254.9901 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 509755 [WEKIWA-7 345.00] CKT 1 | 7.073 | PASS | 0.35485 | PASS | 254.8532 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 7.0799 | PASS | 0.35485 | PASS | 254.8482 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 514806 [SOONER2G 20.00] CKT 1 | 7.0613 | PASS | 0.35486 | PASS | 254.8569 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515576 [RANCHRD7 345.00] CKT 1 | 7.074 | PASS | 0.35486 | PASS | 254.8572 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515894 [THUNDER7 345.00] CKT 1 | 7.0853 | PASS | 0.35485 | PASS | 254.8482 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 7.0798 | PASS | 0.35485 | PASS | 254.8488 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 7.0758 | PASS | 0.35485 | PASS | 254.8522 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514829 [PINE ST4 138.00] CKT 1 | 7.0833 | PASS | 0.35485 | PASS | 254.8463 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 7.0395 | PASS | 0.35488 | PASS | 254.8848 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515373 [LBRTYLK4 138.00] CKT 1 | 7.0529 | PASS | 0.35488 | PASS | 254.8777 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515377 [CRESENT4 138.00] CKT 1 | 7.0762 | PASS | 0.35484 | PASS | 254.8445 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515009 [MCELROY4 138.00] CKT 1 | 7.0148 | PASS | 0.35495 | PASS | 254.9525 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 7.0293 | PASS | 0.35492 | PASS | 254.9205 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515479 [CHSHMVE1 34.5.00] TO BUS 515482 [CHSHMVET 13.2] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.847 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515484 [CHSHMVW1 34.5.00] TO BUS 515485 [CHSHMVWT 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.847 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514880 [NORTWST7 345.00] CKT 1 | 7.0829 | PASS | 0.35485 | PASS | 254.8458 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 7.0821 | PASS | 0.35485 | PASS | 254.8467 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 2 | 7.0821 | PASS | 0.35485 | PASS | 254.8467 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 7.0816 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8454 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 7.0845 | PASS | 0.35485 | PASS | 254.8454 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 7.0849 | PASS | 0.35485 | PASS | 254.8464 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 7.0844 | PASS | 0.35485 | PASS | 254.8453 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 7.079 | PASS | 0.35485 | PASS | 254.8478 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8473 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 7.0291 | PASS | 0.35488 | PASS | 254.8848 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.8] CKT 2 | 7.0817 | PASS | 0.35485 | PASS | 254.8481 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515641 [PLNSMEN4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 7.0514 | PASS | 0.35491 | PASS | 254.9137 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 515695 [ARMFTL11 34.5.00] TO BUS 515698 [ARMFTT11 13.8] CKT 1 | 6.9795 | PASS | 0.35612 | PASS | 256.1227 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] TO BUS 515884 [RDDRTT11 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8462 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] TO BUS 515885 [RDDRTT21 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8464 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 515991 [SKELTL11 34.5.00] TO BUS 515992 [SKELTT11 13.8] CKT 1 | 7.0851 | PASS | 0.35485 | PASS | 254.8491 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516017 [KNGWDL11 34.5.00] TO BUS 516020 [KNGWDT11 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516018 [KNGWDL21 34.5.00] TO BUS 516021 [KNGWDT21 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 588190 [GEN-2016-128 345.00] TO BUS 588191 [G16-128XFMR1 34.5.00] CKT 1 | 7.0844 | PASS | 0.35485 | PASS | 254.8483 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762322 [G17-164XFM1 34.5.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8499 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 762342 [GEN-2017-178 345.00] TO BUS 762343 [G17-178XFM1 34.5.00] CKT 1 | 7.0841 | PASS | 0.35485 | PASS | 254.8462 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 778651 [GEN-2024-056 138.00] TO BUS 778652 [G24-056XFMR1 34.5.00] TO BUS 778667 [G24-056TER1 13.8] CKT 0 | 7.0901 | PASS | 0.35484 | PASS | 254.8401 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 & 2 | 7.0743 | PASS | 0.35485 | PASS | 254.8518 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 & 2 | 7.084 | PASS | 0.35485 | PASS | 254.8463 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | base | 7.0035 | PASS | 0.35502 | PASS | 255.0181 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514707 [PERRY 4 138.00] CKT 1 | 6.7064 | PASS | 0.35532 | PASS | 255.3241 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 4.5842 | FAIL | 0.35949 | PASS | 259.494 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 515006 [MORRISN4 138.00] CKT 1 | 6.9514 | PASS | 0.35503 | PASS | 255.0265 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 6.9539 | PASS | 0.35502 | PASS | 255.0241 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514707 [PERRY 4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 6.7101 | PASS | 0.3553 | PASS | 255.2982 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 4.576 | FAIL | 0.35962 | PASS | 259.6221 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 2.6485 | FAIL | 0.36919 | PASS | 269.1874 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514712 [FAIRMON4 138.00] CKT 1 | 7.046 | PASS | 0.35494 | PASS | 254.9378 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 7.0016 | PASS | 0.35505 | PASS | 255.0453 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 7.0689 | PASS | 0.35488 | PASS | 254.8846 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514711 [WAUKOTP4 138.00] CKT 1 | 6.8951 | PASS | 0.35513 | PASS | 255.1252 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 7.0232 | PASS | 0.35498 | PASS | 254.9781 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 7.0836 | PASS | 0.35485 | PASS | 254.8545 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514712 [FAIRMON4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 7.0463 | PASS | 0.35493 | PASS | 254.9328 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 7.0802 | PASS | 0.35487 | PASS | 254.8655 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514733 [MARSHL 4 138.00] CKT 1 | 6.9077 | PASS | 0.35508 | PASS | 255.0794 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 7.048 | PASS | 0.35488 | PASS | 254.8818 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 6.9266 | PASS | 0.35495 | PASS | 254.9505 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 7.0857 | PASS | 0.35485 | PASS | 254.8522 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.0053 | PASS | 0.35489 | PASS | 254.8919 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 7.0854 | PASS | 0.35485 | PASS | 254.8503 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 6.9072 | PASS | 0.35508 | PASS | 255.0781 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 521006 [MARSHAL4 138.00] CKT Z1 | 7.0843 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 6.9432 | PASS | 0.355 | PASS | 255.0021 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.0035 | PASS | 0.35489 | PASS | 254.8877 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 6.4314 | PASS | 0.35581 | PASS | 255.8127 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 6.9466 | PASS | 0.35503 | PASS | 255.0312 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 6.8617 | PASS | 0.35521 | PASS | 255.2083 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515477 [CHSHLMV7 345.00] CKT 1 | 7.0847 | PASS | 0.35485 | PASS | 254.8489 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515543 [RENFROW7 345.00] CKT 1 | 7.0471 | PASS | 0.35487 | PASS | 254.8743 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 6.9241 | PASS | 0.35494 | PASS | 254.9407 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 7.0847 | PASS | 0.35485 | PASS | 254.8475 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 588190 [GEN-2016-128 345.00] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8482 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 516010 [PINTAIL7 345.00] TO BUS 516019 [KINGWD 7 345.00] CKT Z1 | 7.0848 | PASS | 0.35485 | PASS | 254.8471 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 520461 [GARBER 4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 7.0848 | PASS | 0.35485 | PASS | 254.8474 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762342 [GEN-2017-178 345.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8459 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 778650 [G24-056-TAP 138.00] TO BUS 778651 [GEN-2024-056 138.00] CKT 0 | 7.0901 | PASS | 0.35484 | PASS | 254.8401 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514768 [WF KAY 2 69.00] CKT 1 | 7.0833 | PASS | 0.35485 | PASS | 254.8509 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514706 [COWCRK 4 138.00] TO BUS 515717 [COWCRK 1 13.8] CKT 2 | 7.0833 | PASS | 0.35485 | PASS | 254.8509 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514774 [HENESEY4 138.00] CKT 1 | 6.896 | PASS | 0.35512 | PASS | 255.1197 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514715 [WOODRNG7 345.00] TO BUS 515770 [WOODRNG1 13.8] CKT 2 | 5.8929 | FAIL | 0.35598 | PASS | 255.9808 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514790 [IMO 4 138.00] CKT 1 | 7.0592 | PASS | 0.35491 | PASS | 254.9077 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8467 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514730 [SO4TH 2 69.00] TO BUS 515758 [SO4TH 1 13.2] CKT 1 | 7.0815 | PASS | 0.35486 | PASS | 254.8567 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514704 [MILLERT4 138.00] CKT 1 | 7.0839 | PASS | 0.35485 | PASS | 254.8486 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514798 [SNRPMPT4 138.00] CKT 1 | 7.084 | PASS | 0.35485 | PASS | 254.8475 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514805 [SOONER1G 22.00] CKT 1 | 6.9393 | PASS | 0.35498 | PASS | 254.9805 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514803 [SOONER 7 345.00] TO BUS 515760 [SOONER 1 13.8] CKT 5 | 6.9771 | PASS | 0.35499 | PASS | 254.9901 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 509755 [WEKIWA-7 345.00] CKT 1 | 7.073 | PASS | 0.35485 | PASS | 254.8532 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 7.0799 | PASS | 0.35485 | PASS | 254.8482 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 514806 [SOONER2G 20.00] CKT 1 | 7.0613 | PASS | 0.35486 | PASS | 254.8569 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515576 [RANCHRD7 345.00] CKT 1 | 7.074 | PASS | 0.35486 | PASS | 254.8572 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515894 [THUNDER7 345.00] CKT 1 | 7.0853 | PASS | 0.35485 | PASS | 254.8482 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 7.0798 | PASS | 0.35485 | PASS | 254.8488 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 7.0758 | PASS | 0.35485 | PASS | 254.8522 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514829 [PINE ST4 138.00] CKT 1 | 7.0833 | PASS | 0.35485 | PASS | 254.8463 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 7.0395 | PASS | 0.35488 | PASS | 254.8848 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515373 [LBRTYLK4 138.00] CKT 1 | 7.0529 | PASS | 0.35488 | PASS | 254.8777 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515377 [CRESENT4 138.00] CKT 1 | 7.0762 | PASS | 0.35484 | PASS | 254.8445 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515009 [MCELROY4 138.00] CKT 1 | 7.0148 | PASS | 0.35495 | PASS | 254.9525 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 7.0293 | PASS | 0.35492 | PASS | 254.9205 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515479 [CHSHMVE1 34.5.00] TO BUS 515482 [CHSHMVET 13.2] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.847 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515484 [CHSHMVW1 34.5.00] TO BUS 515485 [CHSHMVWT 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.847 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514880 [NORTWST7 345.00] CKT 1 | 7.0829 | PASS | 0.35485 | PASS | 254.8458 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 7.0821 | PASS | 0.35485 | PASS | 254.8467 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 2 | 7.0821 | PASS | 0.35485 | PASS | 254.8467 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 7.0816 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8454 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 7.0845 | PASS | 0.35485 | PASS | 254.8454 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 7.0849 | PASS | 0.35485 | PASS | 254.8464 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 7.0844 | PASS | 0.35485 | PASS | 254.8453 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 7.079 | PASS | 0.35485 | PASS | 254.8478 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8473 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 7.0291 | PASS | 0.35488 | PASS | 254.8848 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.8] CKT 2 | 7.0817 | PASS | 0.35485 | PASS | 254.8481 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515641 [PLNSMEN4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 7.0514 | PASS | 0.35491 | PASS | 254.9137 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 515695 [ARMFTL11 34.5.00] TO BUS 515698 [ARMFTT11 13.8] CKT 1 | 6.9795 | PASS | 0.35612 | PASS | 256.1227 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] TO BUS 515884 [RDDRTT11 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8462 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] TO BUS 515885 [RDDRTT21 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8464 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 515991 [SKELTL11 34.5.00] TO BUS 515992 [SKELTT11 13.8] CKT 1 | 7.0851 | PASS | 0.35485 | PASS | 254.8491 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516017 [KNGWDL11 34.5.00] TO BUS 516020 [KNGWDT11 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516018 [KNGWDL21 34.5.00] TO BUS 516021 [KNGWDT21 13.2] CKT 1 | 7.0846 | PASS | 0.35485 | PASS | 254.8461 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 588190 [GEN-2016-128 345.00] TO BUS 588191 [G16-128XFMR1 34.5.00] CKT 1 | 7.0844 | PASS | 0.35485 | PASS | 254.8483 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762322 [G17-164XFM1 34.5.00] CKT 1 | 7.0845 | PASS | 0.35485 | PASS | 254.8499 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 762342 [GEN-2017-178 345.00] TO BUS 762343 [G17-178XFM1 34.5.00] CKT 1 | 7.0841 | PASS | 0.35485 | PASS | 254.8462 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 778651 [GEN-2024-056 138.00] TO BUS 778652 [G24-056XFMR1 34.5.00] TO BUS 778667 [G24-056TER1 13.8] CKT 0 | 7.0901 | PASS | 0.35484 | PASS | 254.8401 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 & 2 | 7.0743 | PASS | 0.35485 | PASS | 254.8518 | 49.68 | 56.3
GEN-2026-PR3 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR3 | 138kV Bus at OGE Otter Substation, Garfield County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 & 2 | 7.084 | PASS | 0.35485 | PASS | 254.8463 | 49.68 | 56.3

## WSCR
* WSCR is not applicable for this study.