## Executive Summary
Executive Summary: Group 05 GEN-2026-PR4 Priority Process Study
Interconnection Customer GEN-2026-PR4 (Group 05) has requested a Priority System Impact Study persuant to Section 3.11 of the GIP under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifcations@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR4 generation for total of:
133.764 MW
The minimum cost of interconnecting GEN-2026-PR4 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Models Used in Stability Study
2024 MDWG*
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR4 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 07/14/2026
Costs for Wind Requests were allocated using the 27L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4617100% | SPP | Draft Report (Missing full SCRCCT data to complete analysis. SPP will repost report once the data has been received.)
4619700% | SPP | Draft Report (Inclusion of SCRCCT Results)

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4619700% | Results | 17, 18 | SCRCCT, SCRCCT Results | Inclusion of CCT and Stability Margin Results

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 133.376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.6 | ER | SPS | Hitchland 345 kV | None
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | None
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | None
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | None
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | None
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | None
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | None
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | None
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | None
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | None
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | None
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | None
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | None
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation | None
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | IA PENDING
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | IA PENDING
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
ASGI-2017-013 | 01 NORTH | 23.5 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV | None
ASGI-2018-003 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV | None
ASGI-2018-006 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV | None
ASGI-2018-007 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV | None
ASGI-2018-010 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV | None
ASGI-2018-011 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV | None
GEN-2018-003 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 23.5 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 23.5 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 23.5 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | WITHDRAWN
GEN-2018-015 | 05 SOUTHWEST | 23.5 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 23.5 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-026 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 23.5 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 23.5 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 23.5 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 23.5 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-049 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 23.5 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 23.5 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 23.5 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 23.5 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL |  | None
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW |  | None
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW |  | None
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL |  | None
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW |  | None
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE |  | None
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW |  | None
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL |  | None
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL |  | None
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW |  | None
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP |  | None
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL |  | None
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP |  | None
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL |  | None
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW |  | None
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW |  | None
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP |  | None
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC |  | None
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC |  | None
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP |  | None
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW |  | None
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP |  | None
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | None
MPC04500 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 250 | [9 empty] | ER/NR | OTP |  | None
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0 | None
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0 | None
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | [9 empty] | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | WITHDRAWN
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | [9 empty] | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | WITHDRAWN
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | WITHDRAWN
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | NPPD | Antelope 345kV substation | WITHDRAWN
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER/NR | MIDW | ITC Post Rock 345 kV Substation | WITHDRAWN
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0 | None
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0 | None
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Patent Gate Substation 345 kV | WITHDRAWN
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP |  | None
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP |  | None
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP |  | None
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP |  | None
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP |  | None
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | WITHDRAWN
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE |  | None
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE |  | None
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW |  | None
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW |  | None
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC |  | None
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | WITHDRAWN
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC | Neset 230 kV Substation | TERMINATED
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE |  | None
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC |  | None
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC |  | None
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC |  | None
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC |  | None
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD |  | None
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS |  | None
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA |  | None
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA |  | None
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA |  | None
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation | None
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE |  | None
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS |  | None
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW |  | None
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC |  | None
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE |  | None
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0 | None
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0 | None
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0 | None
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line | None
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0 | None
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0 | None
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0 | None
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445 | None
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | None
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV | None
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation | None
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA |  | None
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA |  | None
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW |  | None
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC |  | None
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC |  | None
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA |  | None
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW |  | None
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC |  | None
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA |  | None
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC |  | None
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC |  | None
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA |  | None
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC |  | None
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC |  | None
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE |  | None
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD |  | None
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA |  | None
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC |  | None
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC |  | None
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC |  | None
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE |  | None
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE |  | None
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE |  | None
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE |  | None
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC |  | None
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC |  | None
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL |  | None
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL |  | None
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC |  | None
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD |  | None
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD |  | None
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC |  | None
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP |  | None
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP |  | None
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP |  | None
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP |  | None
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE |  | None
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP |  | None
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP |  | None
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP |  | None
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS |  | None
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE |  | None
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | 0 | None
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0 | None
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE |  | None
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC |  | None
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC |  | None
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC |  | None
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS |  | None
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD |  | None
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS |  | None
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE |  | None
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW |  | None
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS |  | None
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS |  | None
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD |  | None
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD |  | None
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS |  | None
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS |  | None
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS |  | None
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS |  | None
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS |  | None
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS |  | None
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA |  | None
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA |  | None
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0 | None
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD |  | None
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD |  | None
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD |  | None
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0 | None
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0 | None
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL |  | None
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS |  | None
GEN-2011-056 | 02 NEBRASKA | 6 | DIS-11-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0 | None
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0 | None
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0 | None
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE |  | None
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0 | None
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 4 | DIS-10-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE |  | None
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC |  | None
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL |  | None
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL |  | Surplus | Solar | 175 | [9 empty] | ER | SUNC |  | None
GEN-2006-044N | 02 NEBRASKA |  | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-GR1 | 04 SOUTHEAST |  | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR1 | 04 SOUTHEAST |  | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR2 | 04 SOUTHEAST |  | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR3 | 05 SOUTHWEST |  | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST |  | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-GR5 | 05 SOUTHWEST |  | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
HAWCT_GEN-2021-SR9 | 03 CENTRAL |  | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL |  | None
GEN-2023-GR5 | 05 SOUTHWEST |  | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
HAWCT_GEN-2021-SR9 | 03 CENTRAL |  | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL |  | None

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | N/A | 0 | 133.376 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | N/A | 0 | 133.376 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | N/A | 0 | 133.376 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | N/A | 0 | 133.376 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | N/A | N/A | 133.376 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2026-PR4 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 133.376 | 0 | Stability | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line | N/A | N/A | N/A | 133.376 | N/A | N/A | N/A | N/A | N/A | 0

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
05ALL | GEN-2026-PR4 PSIS | ERIS | Thermal | None | 26SP, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR4 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR4 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 26SP, 29SP | System Intact | 353 | 353 | 144.7 | 147.16 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 26SP, 29SP | System Intact | 349 | 395 | 142.45 | 144.99 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 26SP, 29SP | p42:345:okge:sb_wwhv7385:::ehv: | 1793 | 1793 | 108.35 | 113.38 |  |  |  | Woodward 345-765 kV New Transformer ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 26SP, 29SP | p42:345:okge:sb_boat7386:::ehv: | 1793 | 1793 | 108.29 | 113.48 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 26SP, 29SP | p42:345:okge:sb_baer7384:::ehv: | 1793 | 1793 | 104.99 | 109.87 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 26SP, 29SP | p12:345:okge:bkrbkr4194:::ehv: | 1793 | 1793 | 103.7 | 108.05 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 29SP | p12:345:okge:bkrbkr4193:::ehv: | 1793 | 1793 | 99.5 | 103.7 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 29SP | p42:345:okge:sb_boat7306:::ehv: | 1793 | 1793 | 99.54 | 103.8 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 26SP, 29SP | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | 1084 | 1084 | <90% | 102.4 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 26SP, 29SP | p42:345:okge:sb_dgse7385:::ehv: | 1098 | 1098 | 121.86 | 125.51 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 29SP | System Intact | 1098 | 1098 | 99.83 | 102.86 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 26SP, 29SP | System Intact | 478 | 547 | 116.46 | 118.08 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 26SP, 29SP | System Intact | 353 | 353 | 141.37 | 143.88 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 26SP, 29SP | System Intact | 478 | 610 | 115.74 | 117.47 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 29SP | System Intact | 478 | 546 | 108.28 | 109.64 |  |  |  | Chisholm - Beckham 345 kV New Line
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 29SP | System Intact | 615 | 699 | 130.1 | 131.73 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 29SP | System Intact | 559 | 637 | 124.74 | 126.3 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 26SP | System Intact | 615 | 699 | 136.57 | 138.27 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 26SP | System Intact | 559 | 637 | 130.94 | 132.57 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 29SP | System Intact | 615 | 699 | 128.8 | 130.36 |  |  |  | Chisholm - Beckham 345 kV New Line
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 29SP | System Intact | 559 | 637 | 123.5 | 125 |  |  |  | Woodward 345-765 kV New Transformer ckt1
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 26SP | System Intact | 615 | 699 | 135.52 | 137.35 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 26SP | System Intact | 559 | 637 | 129.94 | 131.7 |  |  |  | Crawfish Draw - Phantom 765 kV New Line ckt2
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Thermal | None | 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
05ALL | GEN-2026-PR4 PSIS | ERIS | Stability | P0 – System Intact | 29SP, 29WP | Group5_P0 | [7 empty] | Woodward - Potter Co 765 kV New Line
05ALL | GEN-2026-PR4 PSIS | ERIS | Stability | P0 – System Intact | 29SP, 29WP | Group5_P0 | [7 empty] | Woodward - Viola 765 kV New Line
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Stability | Loss of Synchronism of multiple units | 29SP | GROUP5_P1_LOCAL_FAULT_106 | [7 empty] | Build New Beckham to Potter 345 kV Line Ckt 2 Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05ALL | GEN-2026-PR4 PSIS CF | ERIS | Stability | Loss of Synchronism of multiple units | 29WP | GROUP5_P1_LOCAL_FAULT_109 | [7 empty] | Build New Beckham to Potter 345 kV Line Ckt 2 Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 503567 | ERIS | Woodward 345-765 kV New Transformer ckt1 | Contingent | Build a new WWARD9 to WWRDEHV7 765-345 kV transformer 1 with a rating of 2400 MVA | 0 | 0 | 61500000 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 503570 | ERIS | Woodward 345-765 kV New Transformer ckt2 | Contingent | Build a new WWARD9 to WWRDEHV7 765-345 kV transformer 2 with a rating of 2400 MVA | 0 | 0 | 61500000 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 504291 | ERIS | Woodward - Viola 765 kV New Line | Contingent | Build a new WWARD9 to VIOLA9 765 kV line 1 (140.8 miles) to a standard rating of 5300 MVA | 0 | 0 | 883920000 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 0 | 12238460 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 0 | 0 | 428620878 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 503539 | ERIS | Crawfish Draw - Phantom 765 kV New Line ckt1 | Contingent | Build a new CRDRW9 to PHANTOM 9 765 kV line 1 (220.8 miles) to a standard rating of 5300 MVA | 0 | 0 | 896306387.8 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS CF | 05 SOUTHWEST | 502134 | ERIS | Crawfish Draw - Phantom 765 kV New Line ckt2 | Contingent | Build a new CRDRW9 to PHANTOM 9 765 kV line 2 (220.8 miles) to a standard rating of 5300 MVA | 0 | 0 | 896306387.8 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS | 05 SOUTHWEST | 504291 | ERIS | Woodward - Viola 765 kV New Line | Contingent | Build a new WWARD9 to VIOLA9 765 kV line 1 (140.8 miles) to a standard rating of 5300 MVA | 0 | 0 | 883920000 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS | 05 SOUTHWEST | 504237 | ERIS | Woodward - Potter Co 765 kV Ckt 1 New Line | Contingent | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 0 | 0 | 1200600000 | N/A
GEN-2026-PR4 | GEN-2026-PR4 PSIS | 05 SOUTHWEST | TBD | ERIS | Hitchland 345 kV Substation GEN-2026-PR4 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR4 (131.56/Storage), into Hitchland 345 kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR4 | GEN-2026-PR4 PSIS | 05 SOUTHWEST | TBD | ERIS | Hitchland 345 kV Substation GEN-2026-PR4 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR4 (131.56/Storage), into Hitchland 345 kV Substation | TBD | 100% | TBD | 1
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR4 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward 345-765 kV New Transformer ckt1 | 503567 | Build a new WWARD9 to WWRDEHV7 765-345 kV transformer 1 with a rating of 2400 MVA | OGE | 4821400% | 61500000
Contingent | GEN-2026-PR4 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward 345-765 kV New Transformer ckt2 | 503570 | Build a new WWARD9 to WWRDEHV7 765-345 kV transformer 2 with a rating of 2400 MVA | OGE | 4821400% | 61500000
Contingent | GEN-2026-PR4 PSIS CF | Steady State/Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Viola 765 kV New Line | 504291 | Build a new WWARD9 to VIOLA9 765 kV line 1 (140.8 miles) to a standard rating of 5300 MVA | TBD | 4821400% | 883920000
Contingent | GEN-2026-PR4 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Crawfish Draw - Phantom 765 kV New Line ckt1 | 503539 | Build a new CRDRW9 to PHANTOM 9 765 kV line 1 (220.8 miles) to a standard rating of 5300 MVA | TBD | 4821400% | 896306387.8
Contingent | GEN-2026-PR4 PSIS CF | Steady State | 05 SOUTHWEST | 2025 ITP | ERIS | Crawfish Draw - Phantom 765 kV New Line ckt2 | 502134 | Build a new CRDRW9 to PHANTOM 9 765 kV line 2 (220.8 miles) to a standard rating of 5300 MVA | TBD | 4821400% | 896306387.8
Contingent | GEN-2026-PR4 PSIS CF | Steady State/Stability | 05 SOUTHWEST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | AEPW/OKGE | 4593900% | 12238460
Contingent | GEN-2026-PR4 PSIS CF | Stability | 05 SOUTHWEST | 2024 ITP | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 170066, 170093 | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | OKGE/SPS | 4743400% | $ 428,620,878.00
Current | GEN-2026-PR4 PSIS | Stability | 05 SOUTHWEST | 2025 ITP | ERIS | Woodward - Potter Co 765 kV Ckt 1 New Line | 504237 | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | TBD | 4821400% | 1200600000
Interconnection | GEN-2026-PR4 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR4 PSIS | ERIS | Hitchland 345 kV Substation GEN-2026-PR4 Interconnection (TOIF) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR4 (131.56/Storage), into Hitchland 345 kV Substation | SPS | TBD | TBD
Interconnection | GEN-2026-PR4 PSIS | Steady State | 05 SOUTHWEST | GEN-2026-PR4 PSIS | ERIS | Hitchland 345 kV Substation GEN-2026-PR4 Interconnection (Non-Shared NU) (SPS) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR4 (131.56/Storage), into Hitchland 345 kV Substation | SPS | TBD | TBD
Total | [10 empty] | 4012371235.6

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.18719 | 4821400% | 883920000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 504296 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | 0.0997 | 4821400% | 1044580000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 504237 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward - Potter Co 765 kV Ckt 1 New Line | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 2025 ITP | Yes | N/A | 0.12481 | 4821400% | 1200600000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 504167 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Seminole 765 kV Ckt 1 New Line | Build a 99.8-mile 765 kV Ckt 1 line from Minco to Seminole | 2025 ITP | Yes | N/A | 0.10643 | 4821400% | 580000000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 504167 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Crawfish Draw 765 kV New Line | Build a 284.8-mile 765 kV Ckt 1 line from Minco to Crawfish Draw | 2025 ITP | Yes | N/A | 0.10941 | 4821400% | 1646620000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503353 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Lawton Eastside - Seminole 765 kV New Line Lawton Eastside - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Lawton Eastside 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Lawton Eastside 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.2-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | 0.06846 | 4821400% | 1822360000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503392 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Lawton Eastside - Seminole 765 kV New Line Lawton Eastside - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Lawton Eastside 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Lawton Eastside 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Southwest Shreveport 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Southwest Shreveport | 2025 ITP | Yes | N/A | 0.03423 | 4821400% | 61500000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503396 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Lawton Eastside - Seminole 765 kV New Line Lawton Eastside - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Lawton Eastside 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Lawton Eastside 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Southwest Shreveport 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Southwest Shreveport | 2025 ITP | Yes | N/A | 0.03423 | 4821400% | 61500000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503720 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Seminole - Crawfish Draw 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03341 | 4821400% | 75911804.43
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503724 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03341 | 4821400% | 75911804.43
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503727 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Anthem | 2025 ITP | Yes | N/A | 0.03341 | 4821400% | 75911804.43
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503567 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Woodward | 2025 ITP | Yes | N/A | -0.04168 | 4821400% | 61500000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503570 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Woodward | 2025 ITP | Yes | N/A | -0.04168 | 4821400% | 61500000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503570 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward - Crawfish Draw 765 kV New Line | Build a 263.6-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw | 2025 ITP | Yes | N/A | -0.04168 | 4821400% | 1528880000
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 503539 | Crawfish Draw - Phantom 765 kV Single-Circuit New Line Tuco - Oklaunion 345kV Line Tap Tuco - Border 345kV Line Tap Tuco - Crawfish Draw 345 kV New Line Oklaunion - Crawfish Draw 345 kV New Line Crawfish Draw 345 kV New Substation Crawfish Draw 765 kV New Substation Crawfish Draw 345/765 kV New Transformer Oklaunion 345 kV New Reactor Crawfish Draw 345 kV New Reactor Crawfish Draw 765 kV New Reactor Phantom 765 kV New Reactor Border 345 kV New Reactor | Crawfish Draw - Phantom 765 kV Ckt 1 New Line | Build a 238.6-mile 765 kV Ckt 1 line from Crawfish Draw to Phantom | 2025 ITP | Yes | N/A | 0.03566 | 4780500% | 896306387.8
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | 502134 | Crawfish Draw - Phantom 765 kV Second Circuit New Line | Crawfish Draw - Phantom 765 kV Ckt 2 New Line | Build a 238.6-mile 765 kV Ckt 2 line from Crawfish Draw to Phantom | 2025 ITP | Yes | N/A | 0.03566 | 4780500% | 896306387.8
GEN-2026-PR4 | 05 SOUTHWEST | ER | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 2020 ITP | Yes | N/A | 0.05701 | 4593900% | 12238460
GEN-2026-PR4 | 05 SOUTHWEST | ER | 220812, 220817 | 170066, 170093 | Line - Beckham County - Potter -345 kV New Line | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | N/A | 0.03003 | 4743400% | 428620878
GEN-2026-PR4 | 05 SOUTHWEST | ER | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | N/A | 0.03991 | TBD (36-month lead time) | 102596000

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR4 | 05 SOUTHWEST | Yes | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00588 | -0.78425 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00718 | -0.95764 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00091 | -0.12137 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00091 | -0.12137 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | 0.00162 | 0.21607 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.01142 | 1.5232 | Yes
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | -0.00047 | -0.062687 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | 0.00022 | 0.029343 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | 0.00022 | 0.029343 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00033 | 0.044014 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00032 | 0.04268 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00317 | 0.4228 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | -0.00171 | -0.22807 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00069 | -0.092029 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00069 | -0.092029 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.01113 | -1.4845 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.01189 | -1.5858 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00012 | 0.016005 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | -0.00012 | -0.016005 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 2e-05 | 0.0026675 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | -0.00014 | -0.018673 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.0004 | 0.05335 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00041 | 0.054684 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 0 | 0 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 0 | 0 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 0 | 0 | No
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 0 | 0 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR4 | 05 SOUTHWEST | G05 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR4 PSIS | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR4 PSIS | 05ALL | 1 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR4 PSIS | 05ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR4 PSIS | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR4 PSIS | 05ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR4 PSIS | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR4 PSIS CF | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR4 PSIS CF | 05ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR4 PSIS CF | 05ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Woodward 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Chisholm - Beckham 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Beckham - Potter Co 345 kV New Line
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt1
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.0529 | 147.16 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.0537 | 144.99 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.0537 | 143.88 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 138.27 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997111 UPDATE LATER 230 1 | 615 | 699 | 0.04871 | 137.35 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 132.57 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997112 SIEM 8743066 230 2 | 559 | 637 | 0.04245 | 131.7 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.04258 | 118.08 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.06129 | 104.33 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05043 | 137.6 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | 349 | 395 | 0.05114 | 135.03 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 353 | 353 | 0.05114 | 134.04 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 131.73 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997034 UPDATE LATER 230 1 | 615 | 699 | 0.05027 | 130.36 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525830 TUCO_INT 6 230 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 126.3 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 525832 TUCO_INT 7 345 997035 SIEM 8743066 230 2 | 559 | 637 | 0.04381 | 125 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | 478 | 610 | 0.05075 | 117.47 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 478 | 547 | 0.03699 | 112.73 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 546 | 0.03133 | 109.64 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 102.86 | System Intact | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.48 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.38 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.46526 | 113.32 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.46521 | 113.3 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 109.87 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.75 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.59 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.45073 | 109.53 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.45068 | 109.52 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.47004 | 108.05 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 108.04 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 106.47 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 2 | 1793 | 1793 | 0.4555 | 105.03 | p12:345:okge:bkrbkr4194:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 105.03 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.46999 | 103.87 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.8 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.41982 | 103.7 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 103.7 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515677 BADGER 7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.41978 | 101.68 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 515554 BVRCNTY7 345 515677 BADGER 7 345 1 | 1793 | 1793 | 0.45545 | 100.82 | p42:345:okge:sb_bvty7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 2 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39548 | 100.11 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | TO->FROM | 515375 WWRDEHV7 345 516106 BOBCAT 7 345 1 | 1793 | 1793 | 0.39552 | 100.11 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24084 | 125.51 | p42:345:okge:sb_dgse7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2419 | 119.96 | p42:345:okge:sb_boat7317:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7387:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.24188 | 119.95 | p42:345:okge:sb_boat7316:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.64 | p42:345:okge:sb_boat7306:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 114.54 | p12:345:okge:bkrbkr4193:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23254 | 114.53 | p12:345:okge:bkrbkr4192:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.23256 | 113.96 | p42:345:okge:sb_baer7388:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20659 | 111.38 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20844 | 111.37 | GEN531447 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.2133 | 111.29 | p12:230:aepw:sweetwt6:chisholm6::: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | p12:230:aepw-sps:sweetwt6:wheeler 6::: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 511541 DEMPSEYR POI 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21337 | 109.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 109 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.74 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22067 | 108.73 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22066 | 108.72 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21504 | 107.51 | p12:230:sps:k73:1:grapevine_wheeler___:hv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.20992 | 106.97 | p13:115:sunc:holcomb_gsu:::hv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 106.96 | GEN531447 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.35 | p42:345:okge:sb_wwhv7385:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.27 | p42:345:okge:sb_boat7386:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22474 | 106.18 | p12:345:okge:bkrbkr4191:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22472 | 106.17 | p12:345:okge:bkrbkr4190:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 105.53 | p42:345:okge:sb_baer7384:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j13:2:hitchland_bvrcnty___:ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4202:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p42:345:sps:hitchland-1r60_slg!:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:sps:j12:1:hitchland_bvrcnty___:ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22625 | 105.37 | p12:345:okge-sps:bkrbkr4201:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21162 | 105.21 | p12:345:okge:bkrbkr4890:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.21187 | 104.12 | GEN640011 2 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 1098 | 1098 | 0.22281 | 104 | p12:345:okge:bkrbkr4195:::ehv: | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 26SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 102.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2
Thermal | GEN-2026-PR4 PSIS CF | 05ALL | 1 | 29SP | GEN-2026-PR4 | FROM->TO | 523019 OSLO-SYLVIE7 345 523097 HITCHLAND 7 345 1 | 1084 | 1084 | 1 | 101.79 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1 | TDF Impact | Crawfish Draw - Phantom 765 kV New Line ckt2

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR4 PSIS | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR4 PSIS | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR4 PSIS | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR4 PSIS CF | 05ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR4 PSIS CF | 05ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR4 PSIS CF | 05ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P0 | P0 – System Intact a. No fault is applied b. Observe system performance under dispatched conditions without any disturbances | P0 | Yes | Yes | Yes | No | Yes | Yes | Yes | High export from Group 05 to Group 04 during case dispatch is causing a low voltage profile at the sending terminals of Group 05 in system intact conditions leading to divergence before the desired dispatch is achieved. Additional transmission paths from Group 05 to Group 04 are required to increase power transfer capability and improve the voltage profile at the sending end. | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P0 | P0 – System Intact a. No fault is applied b. Observe system performance under dispatched conditions without any disturbances | P0 | Yes | Yes | Yes | No | Yes | Yes | Yes | High export from Group 05 to Group 04 during case dispatch is causing a low voltage profile at the sending terminals of Group 05 in system intact conditions leading to divergence before the desired dispatch is achieved. Additional transmission paths from Group 05 to Group 04 are required to increase power transfer capability and improve the voltage profile at the sending end. | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P0 | P0 – System Intact a. No fault is applied b. Observe system performance under dispatched conditions without any disturbances | P0 | Yes | Yes | Yes | No | Yes | Yes | Yes | High export from Group 05 to Group 04 during case dispatch is causing a low voltage profile at the sending terminals of Group 05 in system intact conditions leading to divergence before the desired dispatch is achieved. Additional transmission paths from Group 05 to Group 04 are required to increase power transfer capability and improve the voltage profile at the sending end. | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P0 | P0 – System Intact a. No fault is applied b. Observe system performance under dispatched conditions without any disturbances | P0 | Yes | Yes | Yes | No | Yes | Yes | Yes | High export from Group 05 to Group 04 during case dispatch is causing a low voltage profile at the sending terminals of Group 05 in system intact conditions leading to divergence before the desired dispatch is achieved. Additional transmission paths from Group 05 to Group 04 are required to increase power transfer capability and improve the voltage profile at the sending end. | Woodward - Potter Co 765 kV New Line Woodward - Viola 765 kV New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on 25MILE 7 345.00 (516146) 345 kV Bus a. Apply fault at the 25MILE 7 345.00 (516146) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. 25MILE 7 (516146) 345.0 kV to 25MILZ 7 (516159) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.7. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to POWELL CNR 3 (522957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on GOODWELL 3 115.00 (522935) 115 kV Bus a. Apply fault at the GOODWELL 3 115.00 (522935) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 b.2. RED DEVIL 3 (522930) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on TC-THOMPSON269.000 (523065) 69 kV Bus a. Apply fault at the TC-THOMPSON269.000 (523065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on BOAR 2 69.000 (522907) 69 kV Bus a. Apply fault at the BOAR 2 69.000 (522907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOAR 2 (522907) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on TC-TXCOUNTY269.000 (523089) 69 kV Bus a. Apply fault at the TC-TXCOUNTY269.000 (523089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-TXCOUNTY2 (523089) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on PERRYTON 269.000 (523157) 69 kV Bus a. Apply fault at the PERRYTON 269.000 (523157) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 2 (523157) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.5 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.5 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.4. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on BULL_CREEK 3115.00 (523101) 115 kV Bus a. Apply fault at the BULL_CREEK 3115.00 (523101) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULL_CREEK 3 (523101) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.4. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on BOURK 2 69.000 (522926) 69 kV Bus a. Apply fault at the BOURK 2 69.000 (522926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOURK 2 (522926) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on REED 2 69.000 (522931) 69 kV Bus a. Apply fault at the REED 2 69.000 (522931) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REED 2 (522931) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on TC-MCMURRY 3115.00 (523113) 115 kV Bus a. Apply fault at the TC-MCMURRY 3115.00 (523113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on SHERMAN 3115.00 (523168) 115 kV Bus a. Apply fault at the SHERMAN 3115.00 (523168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERMAN 3 (523168) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on LASLEY 3115.00 (523175) 115 kV Bus a. Apply fault at the LASLEY 3115.00 (523175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.5 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_108 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_110 | 3 Phase fault on JONES3 115.00 (531379) 115 kV Bus a. Apply fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_111 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_112 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_113 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_114 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_115 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_116 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_117 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_118 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_119 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_120 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_121 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_122 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_123 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_124 | 3 Phase fault on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_125 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_126 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_127 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_128 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_129 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_130 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_131 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_132 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_133 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_134 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_135 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_137 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_138 | 3 Phase fault on PERRYTON 3115.00 (523158) 115 kV Bus a. Apply fault at the PERRYTON 3115.00 (523158) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 3 (523158) 115.0 kV to PERRYTON 2 (523157) 69.0 kV to PERRYTON 1 (523156) 8.7 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_139 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_140 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_141 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_142 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_143 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_144 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_145 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_146 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_147 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_148 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR3 (527672) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_149 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR1 (527668) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_150 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR2 (527670) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_151 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_152 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_153 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_154 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_155 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_156 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_158 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_159 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_160 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_161 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_162 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_163 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_164 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_027 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on HANSFORD 3115.00 (523195) 115 kV Bus a. Apply Fault at the HANSFORD 3115.00 (523195) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.3. EW4_TER 1 (523198) 13.8 kV to HANSFORD 3 (523195) 115.0 kV to EW4_SEC 1 (523199) 34.5 kV Three Winding #1 b.4. EW4_SEC 1 (523199) 34.5 kV to EW4_COL 1 (523200) 34.5 kV Transmission Circuit #1 b.5. EW4_SEC 1 (523199) 34.5 kV to HANSFORD 3 (523195) 115.0 kV to EW4_TER 1 (523198) 13.8 kV Three Winding #1 b.6. EW4_COL 1 (523200) 34.5 kV to EW4_GEN 1 (523201) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.13. SPNSPUR_GEN1 (524295) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 b.2. TOLK_TR2 1 (525538) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #2 b.3. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.4. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 b.3. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 3115.00 (523084) 115 kV Bus a. Apply Fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 b.2. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 b.3. BOAR 2 (522907) 69.0 kV to TC-THOMPSON2 (523065) 69.0 kV Transmission Circuit #1 b.4. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.5. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to GEN-2018-009 (762471) 115.0 kV Transmission Circuit #1 b.6. CIM-PLT1 (539653) 13.8 kV to CIM-PLT3 (539654) 115.0 kV Two Winding #1 b.7. CIM-PLT3 (539654) 115.0 kV to CIM PLT1 (539780) 13.8 kV Two Winding #1 b.8. CIM-PLT1 (539653) 13.8 kV to CIM PLT1 (539780) 13.8 kV Transmission Circuit #z1 b.9. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.10. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 b.11. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.12. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.13. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 b.14. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.15. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.16. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 b.6. ROLLA 3 (531395) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.7. ROLLA 3 (531395) 115.0 kV to ASGI-2024-03 (788348) 115.0 kV Transmission Circuit #1 b.8. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.9. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply Fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 b.2. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9 (523966) 765.0 kV to WWRDEHV9 (515378) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 6 (523155) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.2. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G24-045-TAP 230.00 (778320) 230 kV Bus a. Apply Fault at the G24-045-TAP 230.00 (778320) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-045-TAP (778320) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. G24-045-TAP (778320) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.3. G24-045GEN1 (778324) 0.6 kV to Generator #1 b.4. G24-045GEN2 (778327) 0.6 kV to Generator #1 b.5. G24-046GEN1 (777094) 0.6 kV to Generator #1 b.6. G24-046GEN2 (777097) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 12.0 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.2. OCHILTREE 3 (523154) 115.0 kV to TXFARMS 3 (523140) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.2. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on HITCHLAND 3 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3 (523093) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSLO-SYLVIE7345.00 (523019) 345 kV Bus a. Apply Fault at the OSLO-SYLVIE7345.00 (523019) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSLO-SYLVIE7 (523019) 345.0 kV to OLSO 7 (523030) 345.0 kV Transmission Circuit #1 b.2. OSLO-SYLVIE7 (523019) 345.0 kV to GPRAIRIE2 (923020) 34.5 kV to GPRAIRIE1 (923019) 13.8 kV Three Winding #1 b.3. GPRAIRIEG1 (923022) 0.7 kV to Generator #1 b.4. OSLO_GEN1 1 (523035) 0.7 kV to Generator #1 b.5. OSLO_GEN2 (523039) 0.7 kV to Generator #1 b.6. G23-SR8-GEN1 (923081) 0.7 kV to Generator #1 b.7. G23-SR8-GEN2 (923082) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.3. G17-151GEN3 (762226) 0.7 kV to Generator #1 b.4. G17-151GEN1 (762220) 0.7 kV to Generator #1 b.5. G17-151GEN2 (762223) 0.7 kV to Generator #1 b.6. G17-151GEN4 (762229) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on 25MILE 7 345.00 (516146) 345 kV Bus a. Apply fault at the 25MILE 7 345.00 (516146) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. 25MILE 7 (516146) 345.0 kV to 25MILZ 7 (516159) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.7. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to POWELL CNR 3 (522957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on GOODWELL 3 115.00 (522935) 115 kV Bus a. Apply fault at the GOODWELL 3 115.00 (522935) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 b.2. RED DEVIL 3 (522930) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on TC-THOMPSON269.000 (523065) 69 kV Bus a. Apply fault at the TC-THOMPSON269.000 (523065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on BOAR 2 69.000 (522907) 69 kV Bus a. Apply fault at the BOAR 2 69.000 (522907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOAR 2 (522907) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on TC-TXCOUNTY269.000 (523089) 69 kV Bus a. Apply fault at the TC-TXCOUNTY269.000 (523089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-TXCOUNTY2 (523089) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on PERRYTON 269.000 (523157) 69 kV Bus a. Apply fault at the PERRYTON 269.000 (523157) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 2 (523157) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171) and G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.4. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on BULL_CREEK 3115.00 (523101) 115 kV Bus a. Apply fault at the BULL_CREEK 3115.00 (523101) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULL_CREEK 3 (523101) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.4. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on BOURK 2 69.000 (522926) 69 kV Bus a. Apply fault at the BOURK 2 69.000 (522926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOURK 2 (522926) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on REED 2 69.000 (522931) 69 kV Bus a. Apply fault at the REED 2 69.000 (522931) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REED 2 (522931) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171) and G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on TC-MCMURRY 3115.00 (523113) 115 kV Bus a. Apply fault at the TC-MCMURRY 3115.00 (523113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on SHERMAN 3115.00 (523168) 115 kV Bus a. Apply fault at the SHERMAN 3115.00 (523168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERMAN 3 (523168) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on LASLEY 3115.00 (523175) 115 kV Bus a. Apply fault at the LASLEY 3115.00 (523175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G24-143 (781264 and 781267) and G24-145 (781324 and 781327). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 4.0 cycles allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_108 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_110 | 3 Phase fault on JONES3 115.00 (531379) 115 kV Bus a. Apply fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_111 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_112 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_113 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_114 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_115 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_116 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_117 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_118 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_119 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_120 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_121 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_122 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_123 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_124 | 3 Phase fault on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_125 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_126 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_127 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_128 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_129 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_130 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_131 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_132 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_133 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_134 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_135 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_137 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_138 | 3 Phase fault on PERRYTON 3115.00 (523158) 115 kV Bus a. Apply fault at the PERRYTON 3115.00 (523158) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 3 (523158) 115.0 kV to PERRYTON 2 (523157) 69.0 kV to PERRYTON 1 (523156) 8.7 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_139 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_140 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_141 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_142 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_143 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_144 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_145 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_146 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_147 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_148 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR3 (527672) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_149 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR1 (527668) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_150 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR2 (527670) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_151 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_152 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_153 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_154 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_155 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_156 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_158 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_159 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_160 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_161 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_162 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_163 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_164 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GOODWELL Units (523170 and 523171). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_027 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on HANSFORD 3115.00 (523195) 115 kV Bus a. Apply Fault at the HANSFORD 3115.00 (523195) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.3. EW4_TER 1 (523198) 13.8 kV to HANSFORD 3 (523195) 115.0 kV to EW4_SEC 1 (523199) 34.5 kV Three Winding #1 b.4. EW4_SEC 1 (523199) 34.5 kV to EW4_COL 1 (523200) 34.5 kV Transmission Circuit #1 b.5. EW4_SEC 1 (523199) 34.5 kV to HANSFORD 3 (523195) 115.0 kV to EW4_TER 1 (523198) 13.8 kV Three Winding #1 b.6. EW4_COL 1 (523200) 34.5 kV to EW4_GEN 1 (523201) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.13. SPNSPUR_GEN1 (524295) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 b.2. TOLK_TR2 1 (525538) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #2 b.3. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.4. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 b.3. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 3115.00 (523084) 115 kV Bus a. Apply Fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 b.2. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 b.3. BOAR 2 (522907) 69.0 kV to TC-THOMPSON2 (523065) 69.0 kV Transmission Circuit #1 b.4. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.5. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to GEN-2018-009 (762471) 115.0 kV Transmission Circuit #1 b.6. CIM-PLT1 (539653) 13.8 kV to CIM-PLT3 (539654) 115.0 kV Two Winding #1 b.7. CIM-PLT3 (539654) 115.0 kV to CIM PLT1 (539780) 13.8 kV Two Winding #1 b.8. CIM-PLT1 (539653) 13.8 kV to CIM PLT1 (539780) 13.8 kV Transmission Circuit #z1 b.9. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.10. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 b.11. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.12. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.13. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 b.14. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.15. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.16. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 b.6. ROLLA 3 (531395) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.7. ROLLA 3 (531395) 115.0 kV to ASGI-2024-03 (788348) 115.0 kV Transmission Circuit #1 b.8. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.9. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply Fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 b.2. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9 (523966) 765.0 kV to WWRDEHV9 (515378) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 6 (523155) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.2. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G24-045-TAP 230.00 (778320) 230 kV Bus a. Apply Fault at the G24-045-TAP 230.00 (778320) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-045-TAP (778320) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. G24-045-TAP (778320) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.3. G24-045GEN1 (778324) 0.6 kV to Generator #1 b.4. G24-045GEN2 (778327) 0.6 kV to Generator #1 b.5. G24-046GEN1 (777094) 0.6 kV to Generator #1 b.6. G24-046GEN2 (777097) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.2. OCHILTREE 3 (523154) 115.0 kV to TXFARMS 3 (523140) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.2. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on HITCHLAND 3 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3 (523093) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSLO-SYLVIE7345.00 (523019) 345 kV Bus a. Apply Fault at the OSLO-SYLVIE7345.00 (523019) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSLO-SYLVIE7 (523019) 345.0 kV to OLSO 7 (523030) 345.0 kV Transmission Circuit #1 b.2. OSLO-SYLVIE7 (523019) 345.0 kV to GPRAIRIE2 (923020) 34.5 kV to GPRAIRIE1 (923019) 13.8 kV Three Winding #1 b.3. GPRAIRIEG1 (923022) 0.7 kV to Generator #1 b.4. OSLO_GEN1 1 (523035) 0.7 kV to Generator #1 b.5. OSLO_GEN2 (523039) 0.7 kV to Generator #1 b.6. G23-SR8-GEN1 (923081) 0.7 kV to Generator #1 b.7. G23-SR8-GEN2 (923082) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.3. G17-151GEN3 (762226) 0.7 kV to Generator #1 b.4. G17-151GEN1 (762220) 0.7 kV to Generator #1 b.5. G17-151GEN2 (762223) 0.7 kV to Generator #1 b.6. G17-151GEN4 (762229) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-100-GEN (589383). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips CNTRPL-WTG (531601). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.5 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.5 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.5 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_163 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P1_LOCAL_FAULT_164 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply Fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9 (523966) 765.0 kV to WWRDEHV9 (515378) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 12.0 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29S | Base | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 1.0 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models. Reducing the critical clearing time to 4.0 cycles allows the simulation to complete with no stability issue observed. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_163 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P1_LOCAL_FAULT_164 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply Fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS | 29W | Base | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9 (523966) 765.0 kV to WWRDEHV9 (515378) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Woodward - Crawfish Draw 765 kV New Line Minco - Crawfish Draw 765 kV New Line Crawfish Draw - Phantom 765 kV Ckt 1 New Line
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_163 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_164 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply Fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9 (523966) 765.0 kV to WWRDEHV9 (515378) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was determined to have impact on the issue by analyzing the critical clearing time. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on 25MILE 7 345.00 (516146) 345 kV Bus a. Apply fault at the 25MILE 7 345.00 (516146) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. 25MILE 7 (516146) 345.0 kV to 25MILZ 7 (516159) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.7. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to POWELL CNR 3 (522957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on GOODWELL 3 115.00 (522935) 115 kV Bus a. Apply fault at the GOODWELL 3 115.00 (522935) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 b.2. RED DEVIL 3 (522930) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on TC-THOMPSON269.000 (523065) 69 kV Bus a. Apply fault at the TC-THOMPSON269.000 (523065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on BOAR 2 69.000 (522907) 69 kV Bus a. Apply fault at the BOAR 2 69.000 (522907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOAR 2 (522907) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on TC-TXCOUNTY269.000 (523089) 69 kV Bus a. Apply fault at the TC-TXCOUNTY269.000 (523089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-TXCOUNTY2 (523089) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on PERRYTON 269.000 (523157) 69 kV Bus a. Apply fault at the PERRYTON 269.000 (523157) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 2 (523157) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.4. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on BULL_CREEK 3115.00 (523101) 115 kV Bus a. Apply fault at the BULL_CREEK 3115.00 (523101) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULL_CREEK 3 (523101) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.4. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on BOURK 2 69.000 (522926) 69 kV Bus a. Apply fault at the BOURK 2 69.000 (522926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOURK 2 (522926) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on REED 2 69.000 (522931) 69 kV Bus a. Apply fault at the REED 2 69.000 (522931) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REED 2 (522931) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on TC-MCMURRY 3115.00 (523113) 115 kV Bus a. Apply fault at the TC-MCMURRY 3115.00 (523113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on SHERMAN 3115.00 (523168) 115 kV Bus a. Apply fault at the SHERMAN 3115.00 (523168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERMAN 3 (523168) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on LASLEY 3115.00 (523175) 115 kV Bus a. Apply fault at the LASLEY 3115.00 (523175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_108 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_110 | 3 Phase fault on JONES3 115.00 (531379) 115 kV Bus a. Apply fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_111 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_112 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_113 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_114 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_115 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_116 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_117 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_118 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_119 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_120 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_121 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_122 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_123 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_124 | 3 Phase fault on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_125 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_126 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_127 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_128 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_129 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_130 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_131 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_132 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_133 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_134 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_135 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_137 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_138 | 3 Phase fault on PERRYTON 3115.00 (523158) 115 kV Bus a. Apply fault at the PERRYTON 3115.00 (523158) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 3 (523158) 115.0 kV to PERRYTON 2 (523157) 69.0 kV to PERRYTON 1 (523156) 8.7 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_139 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_140 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_141 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_142 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_143 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_144 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_145 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_146 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_147 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_148 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR3 (527672) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_149 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR1 (527668) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_150 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR2 (527670) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_151 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_152 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_153 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_154 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_155 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_156 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_158 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_159 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_160 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_161 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_162 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was determined to have impact on the issue by analyzing the critical clearing time. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P1_REGIONAL_FAULT_027 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on HANSFORD 3115.00 (523195) 115 kV Bus a. Apply Fault at the HANSFORD 3115.00 (523195) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.3. EW4_TER 1 (523198) 13.8 kV to HANSFORD 3 (523195) 115.0 kV to EW4_SEC 1 (523199) 34.5 kV Three Winding #1 b.4. EW4_SEC 1 (523199) 34.5 kV to EW4_COL 1 (523200) 34.5 kV Transmission Circuit #1 b.5. EW4_SEC 1 (523199) 34.5 kV to HANSFORD 3 (523195) 115.0 kV to EW4_TER 1 (523198) 13.8 kV Three Winding #1 b.6. EW4_COL 1 (523200) 34.5 kV to EW4_GEN 1 (523201) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.13. SPNSPUR_GEN1 (524295) 0.7 kV to Generator #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 b.2. TOLK_TR2 1 (525538) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #2 b.3. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.4. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 b.3. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 3115.00 (523084) 115 kV Bus a. Apply Fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 b.2. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 b.3. BOAR 2 (522907) 69.0 kV to TC-THOMPSON2 (523065) 69.0 kV Transmission Circuit #1 b.4. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.5. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to GEN-2018-009 (762471) 115.0 kV Transmission Circuit #1 b.6. CIM-PLT1 (539653) 13.8 kV to CIM-PLT3 (539654) 115.0 kV Two Winding #1 b.7. CIM-PLT3 (539654) 115.0 kV to CIM PLT1 (539780) 13.8 kV Two Winding #1 b.8. CIM-PLT1 (539653) 13.8 kV to CIM PLT1 (539780) 13.8 kV Transmission Circuit #z1 b.9. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.10. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 b.11. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.12. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.13. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 b.14. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.15. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.16. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 b.6. ROLLA 3 (531395) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.7. ROLLA 3 (531395) 115.0 kV to ASGI-2024-03 (788348) 115.0 kV Transmission Circuit #1 b.8. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.9. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 b.2. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 6 (523155) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.2. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G24-045-TAP 230.00 (778320) 230 kV Bus a. Apply Fault at the G24-045-TAP 230.00 (778320) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-045-TAP (778320) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. G24-045-TAP (778320) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.3. G24-045GEN1 (778324) 0.6 kV to Generator #1 b.4. G24-045GEN2 (778327) 0.6 kV to Generator #1 b.5. G24-046GEN1 (777094) 0.6 kV to Generator #1 b.6. G24-046GEN2 (777097) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.2. OCHILTREE 3 (523154) 115.0 kV to TXFARMS 3 (523140) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.2. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on HITCHLAND 3 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3 (523093) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSLO-SYLVIE7345.00 (523019) 345 kV Bus a. Apply Fault at the OSLO-SYLVIE7345.00 (523019) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSLO-SYLVIE7 (523019) 345.0 kV to OLSO 7 (523030) 345.0 kV Transmission Circuit #1 b.2. OSLO-SYLVIE7 (523019) 345.0 kV to GPRAIRIE2 (923020) 34.5 kV to GPRAIRIE1 (923019) 13.8 kV Three Winding #1 b.3. GPRAIRIEG1 (923022) 0.7 kV to Generator #1 b.4. OSLO_GEN1 1 (523035) 0.7 kV to Generator #1 b.5. OSLO_GEN2 (523039) 0.7 kV to Generator #1 b.6. G23-SR8-GEN1 (923081) 0.7 kV to Generator #1 b.7. G23-SR8-GEN2 (923082) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.3. G17-151GEN3 (762226) 0.7 kV to Generator #1 b.4. G17-151GEN1 (762220) 0.7 kV to Generator #1 b.5. G17-151GEN2 (762223) 0.7 kV to Generator #1 b.6. G17-151GEN4 (762229) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was determined to have impact on the issue by analyzing the critical clearing time. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was determined to have impact on the issue by analyzing the critical clearing time. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was determined to have impact on the issue by analyzing the critical clearing time. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on 25MILE 7 345.00 (516146) 345 kV Bus a. Apply fault at the 25MILE 7 345.00 (516146) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. 25MILE 7 (516146) 345.0 kV to 25MILZ 7 (516159) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.7. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to POWELL CNR 3 (522957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on GOODWELL 3 115.00 (522935) 115 kV Bus a. Apply fault at the GOODWELL 3 115.00 (522935) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 b.2. RED DEVIL 3 (522930) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on TC-THOMPSON269.000 (523065) 69 kV Bus a. Apply fault at the TC-THOMPSON269.000 (523065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on BOAR 2 69.000 (522907) 69 kV Bus a. Apply fault at the BOAR 2 69.000 (522907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOAR 2 (522907) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR11 (523085) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on TC-TXCOUNTY269.000 (523089) 69 kV Bus a. Apply fault at the TC-TXCOUNTY269.000 (523089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-TXCOUNTY2 (523089) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on PERRYTON 269.000 (523157) 69 kV Bus a. Apply fault at the PERRYTON 269.000 (523157) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 2 (523157) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on RB-SPURLCK+3115.00 (523177) 115 kV Bus a. Apply fault at the RB-SPURLCK+3115.00 (523177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RB-SPURLCK+3 (523177) 115.0 kV to MOORE_E 3 (523308) 115.0 kV Transmission Circuit #1 b.2. RB-ELKS 3 (523176) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 b.3. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 b.4. RB-SPURLCK 3 (523159) 115.0 kV to RB-SPURLCK+3 (523177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on BULL_CREEK 3115.00 (523101) 115 kV Bus a. Apply fault at the BULL_CREEK 3115.00 (523101) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULL_CREEK 3 (523101) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.2. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 b.3. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 b.4. BULL_CREEK 3 (523101) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to GOODWELL 3 (522935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on Y ROAD 3 115.00 (522912) 115 kV Bus a. Apply fault at the Y ROAD 3 115.00 (522912) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on BOURK 2 69.000 (522926) 69 kV Bus a. Apply fault at the BOURK 2 69.000 (522926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOURK 2 (522926) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on REED 2 69.000 (522931) 69 kV Bus a. Apply fault at the REED 2 69.000 (522931) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REED 2 (522931) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on TC-MCMURRY 3115.00 (523113) 115 kV Bus a. Apply fault at the TC-MCMURRY 3115.00 (523113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY 3 (523113) 115.0 kV to TC-MCMURRY+3 (523141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on TC-MCMURRY+3115.00 (523141) 115 kV Bus a. Apply fault at the TC-MCMURRY+3115.00 (523141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TC-MCMURRY+3 (523141) 115.0 kV to TC-AGGIE 3 (523142) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on SHERMAN 3115.00 (523168) 115 kV Bus a. Apply fault at the SHERMAN 3115.00 (523168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERMAN 3 (523168) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on LASLEY 3115.00 (523175) 115 kV Bus a. Apply fault at the LASLEY 3115.00 (523175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASLEY 3 (523175) 115.0 kV to RB-ELKS 3 (523176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_108 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_110 | 3 Phase fault on JONES3 115.00 (531379) 115 kV Bus a. Apply fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_111 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_112 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_113 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_114 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_115 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_116 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_117 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_118 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_119 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_120 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_121 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_122 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_123 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_124 | 3 Phase fault on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_125 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_126 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_127 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_128 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to WWRDEHV7 (515375) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_129 | 3 Phase fault on TEXAS_CO_S 3115.00 (523083) 115 kV Bus a. Apply fault at the TEXAS_CO_S 3115.00 (523083) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_S 3 (523083) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_130 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_131 | 3 Phase fault on TEXAS_CO_N 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CO_N 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CO_N 3 (523090) 115.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV to TC-TXCN_TR21 (523086) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_132 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_133 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_134 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_135 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_137 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_138 | 3 Phase fault on PERRYTON 3115.00 (523158) 115 kV Bus a. Apply fault at the PERRYTON 3115.00 (523158) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRYTON 3 (523158) 115.0 kV to PERRYTON 2 (523157) 69.0 kV to PERRYTON 1 (523156) 8.7 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_139 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_140 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_141 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_142 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_143 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_144 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_145 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_146 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_147 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_148 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR3 (527672) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_149 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR1 (527668) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_150 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to CROSSROAD (527656) 345.0 kV to CROSSROADTR2 (527670) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_151 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_152 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_153 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_154 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_155 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_156 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_157 | 3 Phase fault on SOONER 3115.00 (523084) 115 kV Bus a. Apply fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 3 (523084) 115.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_158 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 9 (523966) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_159 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_160 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_161 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_162 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_163 | 3 Phase fault on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_164 | 3 Phase fault on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_002 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_003 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_005 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_006 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_007 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_008 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_009 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_011 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_012 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_013 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_014 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_015 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_016 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_017 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_019 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_020 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_021 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G24-041-TAP (778200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_022 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_023 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_024 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_025 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_026 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P1_REGIONAL_FAULT_027 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply Fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on HANSFORD 3115.00 (523195) 115 kV Bus a. Apply Fault at the HANSFORD 3115.00 (523195) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARMAN 3 (523186) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 b.3. EW4_TER 1 (523198) 13.8 kV to HANSFORD 3 (523195) 115.0 kV to EW4_SEC 1 (523199) 34.5 kV Three Winding #1 b.4. EW4_SEC 1 (523199) 34.5 kV to EW4_COL 1 (523200) 34.5 kV Transmission Circuit #1 b.5. EW4_SEC 1 (523199) 34.5 kV to HANSFORD 3 (523195) 115.0 kV to EW4_TER 1 (523198) 13.8 kV Three Winding #1 b.6. EW4_COL 1 (523200) 34.5 kV to EW4_GEN 1 (523201) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.2. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.13. SPNSPUR_GEN1 (524295) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 b.2. TOLK_TR2 1 (525538) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #2 b.3. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.4. TOLK 7 (525549) 345.0 kV to G24-109-TAP (780240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 b.3. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SOONER 3115.00 (523084) 115 kV Bus a. Apply Fault at the SOONER 3115.00 (523084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 3 (523084) 115.0 kV to TEXAS_CO_N 3 (523090) 115.0 kV Transmission Circuit #1 b.2. TC-THOMPSON2 (523065) 69.0 kV to TC-TXCOUNTY2 (523089) 69.0 kV Transmission Circuit #1 b.3. BOAR 2 (522907) 69.0 kV to TC-THOMPSON2 (523065) 69.0 kV Transmission Circuit #1 b.4. SOONER 3 (523084) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 b.5. Y ROAD 3 (522912) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to GEN-2018-009 (762471) 115.0 kV Transmission Circuit #1 b.6. CIM-PLT1 (539653) 13.8 kV to CIM-PLT3 (539654) 115.0 kV Two Winding #1 b.7. CIM-PLT3 (539654) 115.0 kV to CIM PLT1 (539780) 13.8 kV Two Winding #1 b.8. CIM-PLT1 (539653) 13.8 kV to CIM PLT1 (539780) 13.8 kV Transmission Circuit #z1 b.9. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.10. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-1 (539967) 13.8 kV Three Winding #1 b.11. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.12. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.13. CMRIVTP3 (539652) 115.0 kV to GEN-2024-218 (783511) 115.0 kV Transmission Circuit #1 b.14. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.15. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.16. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-1 (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply Fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. HUGOTON3 (531481) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.4. HUGOTON3 (531481) 115.0 kV to GEN-2024-032 (777931) 115.0 kV Transmission Circuit #1 b.5. HUGOTON3 (531481) 115.0 kV to HUGOTON2 (531380) 69.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 b.6. ROLLA 3 (531395) 115.0 kV to ABBK 3 (531494) 115.0 kV Transmission Circuit #1 b.7. ROLLA 3 (531395) 115.0 kV to ASGI-2024-03 (788348) 115.0 kV Transmission Circuit #1 b.8. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.9. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.3. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. WALKMYR3 (531405) 115.0 kV to WALKMYR2 (531404) 69.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WWRDEHV9 765.00 (515378) 765 kV Bus a. Apply Fault at the WWRDEHV9 765.00 (515378) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV9 (515378) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 b.2. WWRDEHV9 (515378) 765.0 kV to VIOLA9 (533836) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to SOONER 3 (523084) 115.0 kV Transmission Circuit #1 b.2. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to G24-045-TAP (778320) 230.0 kV Transmission Circuit #1 b.2. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 9 (523966) 765.0 kV to CROSSROADS 9 (527669) 765.0 kV Transmission Circuit #1 b.2. POTTER_CO 9 (523966) 765.0 kV to WWRDEHV9 (515378) 765.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 6 (523155) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.2. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on POTTER_CO 9765.00 (523966) 765 kV Bus a. Apply Fault at the POTTER_CO 9765.00 (523966) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G24-045-TAP 230.00 (778320) 230 kV Bus a. Apply Fault at the G24-045-TAP 230.00 (778320) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-045-TAP (778320) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. G24-045-TAP (778320) 230.0 kV to HITCHLAND 6 (523095) 230.0 kV Transmission Circuit #1 b.3. G24-045GEN1 (778324) 0.6 kV to Generator #1 b.4. G24-045GEN2 (778327) 0.6 kV to Generator #1 b.5. G24-046GEN1 (777094) 0.6 kV to Generator #1 b.6. G24-046GEN2 (777097) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). The issue is also observed in the base case and the CQ unit was not shown to have considerable impact on it. | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.2. OCHILTREE 3 (523154) 115.0 kV to TXFARMS 3 (523140) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.2. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.2. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on HITCHLAND 3 (523093) 115 kV Bus a. Apply Fault at the HITCHLAND 3 (523093) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HITCHLAND 3 (523093) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.2. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. DEMPSEYR POI (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OLYMPIA7 345.00 (523040) 345 kV Bus a. Apply Fault at the OLYMPIA7 345.00 (523040) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_COL2 1 (523049) 34.5 kV to GRVR_GEN 1 (523050) 0.7 kV Two Winding #1 b.3. GRVR_T2 1 (523048) 34.5 kV to GRVR_COL2 1 (523049) 34.5 kV Transmission Circuit #1 b.4. GRVR_T2 1 (523048) 34.5 kV to OLYMPIA7 (523040) 345.0 kV to GRVR_TY 1 (523047) 13.8 kV Three Winding #1 b.5. OLYMPIA7 (523040) 345.0 kV to FRWLN7 (523041) 345.0 kV Transmission Circuit #1 b.6. OLYMPIA7 (523040) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to HITCHLAND 7 (523097) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.15. GRPLNS-WT4-1 (523121) 0.6 kV to Generator #1 b.16. NBLWND-WTG11 (523122) 0.7 kV to Generator #1 b.17. GRPLNS-WT2-1 (523123) 0.6 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.4. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GRAPEVINE 3115.00 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3115.00 (523770) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWERS 3 (523748) 115.0 kV to GRAPEVINE 3 (523770) 115.0 kV Transmission Circuit #1 b.2. GRAPEVINE 3 (523770) 115.0 kV to KIRBY 3 (524088) 115.0 kV Transmission Circuit #1 b.3. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.4. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. COBRN_CREEK3 (523772) 115.0 kV to WHEELER 3 (523776) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-1 (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-1 (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSLO-SYLVIE7345.00 (523019) 345 kV Bus a. Apply Fault at the OSLO-SYLVIE7345.00 (523019) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSLO-SYLVIE7 (523019) 345.0 kV to OLSO 7 (523030) 345.0 kV Transmission Circuit #1 b.2. OSLO-SYLVIE7 (523019) 345.0 kV to GPRAIRIE2 (923020) 34.5 kV to GPRAIRIE1 (923019) 13.8 kV Three Winding #1 b.3. GPRAIRIEG1 (923022) 0.7 kV to Generator #1 b.4. OSLO_GEN1 1 (523035) 0.7 kV to Generator #1 b.5. OSLO_GEN2 (523039) 0.7 kV to Generator #1 b.6. G23-SR8-GEN1 (923081) 0.7 kV to Generator #1 b.7. G23-SR8-GEN2 (923082) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to G23-015-TAP (772280) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on G23-015-TAP 345.00 (772280) 345 kV Bus a. Apply Fault at the G23-015-TAP 345.00 (772280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G23-015-TAP (772280) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. G23-015-TAP (772280) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (525839) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (525839) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.3. G17-151GEN3 (762226) 0.7 kV to Generator #1 b.4. G17-151GEN1 (762220) 0.7 kV to Generator #1 b.5. G17-151GEN2 (762223) 0.7 kV to Generator #1 b.6. G17-151GEN4 (762229) 0.7 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 3 (523776) 115.0 kV to HOWARD 3 (523797) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CARPENTER (523823) 345 kV Bus a. Apply Fault at the CARPENTER (523823) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DN_G21 (523061) 0.7 kV to Generator #1 b.12. BUFF_DN_G11 (523062) 0.7 kV to Generator #1 b.13. BUFF_DN_G21 (523061) 0.7 kV to remove bus # b.14. BUFF_DN_G11 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNMV21 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNMV11 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. None to remove bus # b.7. None to Generator #1 b.8. None to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR3 1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR3 1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to DEMPSEYR POI (511541) 230.0 kV Transmission Circuit #&1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230 kV Bus a. Apply Fault at the WHEELER (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 3 (523776) 115.0 kV to WHEELER 6 (523777) 230.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 b.2. WHEELER 6 (523777) 230.0 kV to remove bus # b.3. WHEELER_TR11 (523774) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Transfer | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. The issue is also observed in the base case and reducing the critical clearing time helped determine the CQ unit has no impact on it. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P1_REGIONAL_FAULT_001 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P1_REGIONAL_FAULT_010 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to G24-266_TAP (784950) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR2 1 (523958) 13.2 kV Three Winding #2 b.8. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 3 (523967) 13.2 kV Three Winding #1 b.9. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 2 (523965) 13.2 kV Three Winding #1 b.10. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 9 (523966) 765.0 kV to POTTER_TR3 1 (523964) 13.2 kV Three Winding #1 b.11. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.12. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.13. SPNSPUR_GEN1 (524295) 0.7 kV to Generator #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.2. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.3. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.4. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.5. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.6. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on CHINA_DRAW (528223) 345 kV Bus a. Apply Fault at the CHINA_DRAW (528223) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHINA_DRAW 7 (528223) 345.0 kV to CHINA_DRAW 3 (528222) 115.0 kV to CHINA_DRAW 1 (528219) 13.2 kV Three Winding #1 b.2. CHINA_DRAW 7 (528223) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 b.3. CHINA_DRAW 7 (528223) 345.0 kV to PHANTOM 7 (528015) 345.0 kV Transmission Circuit #1 b.4. CHINA_DRAW 1 (528219) 13.2 kV to remove bus # b.5. CARPENTER 7 (523823) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29S | Base | GROUP5_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations were observed at the Tolk (525561 and 525562) and Harrington (523971, 523972 and 523973) generating sites in post fault conditions. | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Base | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Base | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | No mitigation required.
05 SOUTHWEST | GEN-2026-PR4 PSIS CF | 29W | Base | GROUP5_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on CROSSROADS 9765.00 (527669) 765 kV Bus a. Apply Fault at the CROSSROADS 9765.00 (527669) 765 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 9 (527669) 765.0 kV to PHANTOM 9 (528014) 765.0 kV Transmission Circuit #1 b.2. CROSSROADS 9 (527669) 765.0 kV to POTTER_CO 9 (523966) 765.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Loss of Synchronism was observed at multiple generator sites including SYL_GEN (523025 and 523029) and OSLO_GEN (523035 and 523039). | Line - Beckham County - Potter -345 kV New Line (2024 ITP) Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 29SP Fault Current 3-Phase (kA) | Request In Service 29SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR4 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 13.9035 | 13.9156 | 0.0121
GEN-2026-PR4 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 13.0587 | 13.0642 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 511587 | MATO 7 | 345 | 9.7403 | 9.7435 | 0.0032
GEN-2026-PR4 | 05 SOUTHWEST | 511592 | SEVEN7A_HV | 345 | 9.2556 | 9.2585 | 0.0029
GEN-2026-PR4 | 05 SOUTHWEST | 511599 | SEVEN7AB2 | 345 | 9.2556 | 9.2585 | 0.0029
GEN-2026-PR4 | 05 SOUTHWEST | 511608 | SEVEN7AB3 | 345 | 9.2556 | 9.2585 | 0.0029
GEN-2026-PR4 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 24.1615 | 24.3099 | 0.1484
GEN-2026-PR4 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 26.2923 | 26.3416 | 0.0493
GEN-2026-PR4 | 05 SOUTHWEST | 515378 | WWRDEHV9 | 765 | 8.3745 | 8.3957 | 0.0212
GEN-2026-PR4 | 05 SOUTHWEST | 515394 | KEENAN 4 | 138 | 9.2943 | 9.2999 | 0.0056
GEN-2026-PR4 | 05 SOUTHWEST | 515398 | OUSPRT 4 | 138 | 9.9744 | 9.981 | 0.0066
GEN-2026-PR4 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 18.4765 | 18.5097 | 0.0332
GEN-2026-PR4 | 05 SOUTHWEST | 515448 | CRSRDSW7 | 345 | 12.7183 | 12.7337 | 0.0154
GEN-2026-PR4 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 11.6844 | 11.6919 | 0.0075
GEN-2026-PR4 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 13.7213 | 14.254 | 0.5327
GEN-2026-PR4 | 05 SOUTHWEST | 515582 | SLNGWND7 | 345 | 8.9001 | 8.9073 | 0.0072
GEN-2026-PR4 | 05 SOUTHWEST | 515585 | MAMTHPW7 | 345 | 14.2497 | 14.2692 | 0.0195
GEN-2026-PR4 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 11.6002 | 11.9726 | 0.3724
GEN-2026-PR4 | 05 SOUTHWEST | 515634 | PALDR1W7 | 345 | 10.0402 | 10.3127 | 0.2725
GEN-2026-PR4 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.4512 | 13.807 | 0.3558
GEN-2026-PR4 | 05 SOUTHWEST | 515686 | BLUWND 7 | 345 | 12.159 | 12.4472 | 0.2882
GEN-2026-PR4 | 05 SOUTHWEST | 515825 | GRTWSRN7 | 345 | 9.6181 | 9.6415 | 0.0234
GEN-2026-PR4 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 15.1333 | 15.1662 | 0.0329
GEN-2026-PR4 | 05 SOUTHWEST | 515951 | PERSIMN7 | 345 | 11.9228 | 11.9588 | 0.036
GEN-2026-PR4 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 13.7163 | 13.764 | 0.0477
GEN-2026-PR4 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 14.0027 | 14.0152 | 0.0125
GEN-2026-PR4 | 05 SOUTHWEST | 516074 | PONDRSA7 | 345 | 10.4523 | 10.662 | 0.2097
GEN-2026-PR4 | 05 SOUTHWEST | 516106 | BOBCAT 7 | 345 | 16.5325 | 16.7029 | 0.1704
GEN-2026-PR4 | 05 SOUTHWEST | 516146 | 25MILE 7 | 345 | 16.4999 | 16.6696 | 0.1697
GEN-2026-PR4 | 05 SOUTHWEST | 516159 | 25MILZ 7 | 345 | 16.4681 | 16.6372 | 0.1691
GEN-2026-PR4 | 05 SOUTHWEST | 522899 | ANTHONY 3 | 115 | 2.5085 | 2.5112 | 0.0027
GEN-2026-PR4 | 05 SOUTHWEST | 522904 | LOBO 3 | 115 | 3.1592 | 3.1633 | 0.0041
GEN-2026-PR4 | 05 SOUTHWEST | 522912 | Y ROAD 3 | 115 | 5.302 | 5.3145 | 0.0125
GEN-2026-PR4 | 05 SOUTHWEST | 522914 | BOYD 3 | 115 | 5.0038 | 5.0153 | 0.0115
GEN-2026-PR4 | 05 SOUTHWEST | 522926 | BOURK 2 | 69 | 10.5409 | 10.5726 | 0.0317
GEN-2026-PR4 | 05 SOUTHWEST | 522930 | RED DEVIL 3 | 115 | 2.5952 | 2.5982 | 0.003
GEN-2026-PR4 | 05 SOUTHWEST | 522931 | REED 2 | 69 | 10.5409 | 10.5726 | 0.0317
GEN-2026-PR4 | 05 SOUTHWEST | 522935 | GOODWELL 3 | 115 | 3.9062 | 3.9129 | 0.0067
GEN-2026-PR4 | 05 SOUTHWEST | 522941 | LOBO-T 3 | 115 | 3.2015 | 3.2057 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 522942 | LITTAU 3 | 115 | 3.2059 | 3.2106 | 0.0047
GEN-2026-PR4 | 05 SOUTHWEST | 522952 | ROSE 3 | 115 | 1.5964 | 1.5975 | 0.0011
GEN-2026-PR4 | 05 SOUTHWEST | 522957 | POWELL CNR 3 | 115 | 4.4295 | 4.4376 | 0.0081
GEN-2026-PR4 | 05 SOUTHWEST | 523012 | TC-ANTHY_TP3 | 115 | 2.6801 | 2.6832 | 0.0031
GEN-2026-PR4 | 05 SOUTHWEST | 523019 | OSLO-SYLVIE7 | 345 | 10.3689 | 11.4842 | 1.1153
GEN-2026-PR4 | 05 SOUTHWEST | 523020 | SYLVIE 7 | 345 | 10.3689 | 11.4842 | 1.1153
GEN-2026-PR4 | 05 SOUTHWEST | 523024 | TC-BEAVER 3 | 115 | 1.5964 | 1.5975 | 0.0011
GEN-2026-PR4 | 05 SOUTHWEST | 523030 | OLSO 7 | 345 | 10.3689 | 11.4842 | 1.1153
GEN-2026-PR4 | 05 SOUTHWEST | 523040 | OLYMPIA7 | 345 | 14.4256 | 15.3803 | 0.9547
GEN-2026-PR4 | 05 SOUTHWEST | 523041 | FRWLN7 | 345 | 11.7522 | 12.371 | 0.6188
GEN-2026-PR4 | 05 SOUTHWEST | 523083 | TEXAS_CO_S 3 | 115 | 9.3667 | 9.4093 | 0.0426
GEN-2026-PR4 | 05 SOUTHWEST | 523084 | SOONER 3 | 115 | 9.4642 | 9.5076 | 0.0434
GEN-2026-PR4 | 05 SOUTHWEST | 523089 | TC-TXCOUNTY2 | 69 | 10.5409 | 10.5726 | 0.0317
GEN-2026-PR4 | 05 SOUTHWEST | 523090 | TEXAS_CO_N 3 | 115 | 9.3794 | 9.422 | 0.0426
GEN-2026-PR4 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 18.8632 | 19.0911 | 0.2279
GEN-2026-PR4 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 15.2567 | 15.7525 | 0.4958
GEN-2026-PR4 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.704 | 15.6993 | 0.9953
GEN-2026-PR4 | 05 SOUTHWEST | 523099 | TC-DRYTRLS 3 | 115 | 2.7523 | 2.7554 | 0.0031
GEN-2026-PR4 | 05 SOUTHWEST | 523101 | BULL_CREEK 3 | 115 | 5.0184 | 5.03 | 0.0116
GEN-2026-PR4 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 11.0011 | 11.1459 | 0.1448
GEN-2026-PR4 | 05 SOUTHWEST | 523106 | TXPHSF 3 | 115 | 4.5136 | 4.522 | 0.0084
GEN-2026-PR4 | 05 SOUTHWEST | 523113 | TC-MCMURRY 3 | 115 | 7.14 | 7.1645 | 0.0245
GEN-2026-PR4 | 05 SOUTHWEST | 523118 | BUFF_DUNES 7 | 345 | 6.2215 | 6.2305 | 0.009
GEN-2026-PR4 | 05 SOUTHWEST | 523120 | COLE 3 | 115 | 5.0038 | 5.0153 | 0.0115
GEN-2026-PR4 | 05 SOUTHWEST | 523130 | GRPLNS-HV4-3 | 115 | 7.4441 | 7.5061 | 0.062
GEN-2026-PR4 | 05 SOUTHWEST | 523131 | GRPLNS-HV2-3 | 115 | 10.1769 | 10.2975 | 0.1206
GEN-2026-PR4 | 05 SOUTHWEST | 523135 | LIPSCOMB 3 | 115 | 2.8968 | 2.9014 | 0.0046
GEN-2026-PR4 | 05 SOUTHWEST | 523136 | NP-HARBOUR 2 | 69 | 2.148 | 2.1486 | 0.0006
GEN-2026-PR4 | 05 SOUTHWEST | 523137 | NP-SUB_A 2 | 69 | 1.0608 | 1.061 | 0.0002
GEN-2026-PR4 | 05 SOUTHWEST | 523138 | NP_SPER1_TP2 | 69 | 3.1897 | 3.191 | 0.0013
GEN-2026-PR4 | 05 SOUTHWEST | 523139 | NP_SPER2_TP2 | 69 | 1.8669 | 1.8673 | 0.0004
GEN-2026-PR4 | 05 SOUTHWEST | 523140 | TXFARMS 3 | 115 | 5.628 | 5.6425 | 0.0145
GEN-2026-PR4 | 05 SOUTHWEST | 523141 | TC-MCMURRY+3 | 115 | 7.1518 | 7.1764 | 0.0246
GEN-2026-PR4 | 05 SOUTHWEST | 523142 | TC-AGGIE 3 | 115 | 4.7815 | 4.792 | 0.0105
GEN-2026-PR4 | 05 SOUTHWEST | 523143 | NP-PERDUR_G3 | 115 | 2.7914 | 2.7932 | 0.0018
GEN-2026-PR4 | 05 SOUTHWEST | 523144 | NP-PERDURE 3 | 115 | 2.4947 | 2.4961 | 0.0014
GEN-2026-PR4 | 05 SOUTHWEST | 523145 | WADE_TP 3 | 115 | 3.7269 | 3.7346 | 0.0077
GEN-2026-PR4 | 05 SOUTHWEST | 523147 | WADE 3 | 115 | 3.5125 | 3.5193 | 0.0068
GEN-2026-PR4 | 05 SOUTHWEST | 523152 | NP-OCHILTRE2 | 69 | 1.8726 | 1.8731 | 0.0005
GEN-2026-PR4 | 05 SOUTHWEST | 523153 | NP-OCHILTRE3 | 115 | 2.1403 | 2.1413 | 0.001
GEN-2026-PR4 | 05 SOUTHWEST | 523154 | OCHILTREE 3 | 115 | 6.7082 | 6.7332 | 0.025
GEN-2026-PR4 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.4939 | 4.5269 | 0.033
GEN-2026-PR4 | 05 SOUTHWEST | 523157 | PERRYTON 2 | 69 | 2.5142 | 2.5163 | 0.0021
GEN-2026-PR4 | 05 SOUTHWEST | 523158 | PERRYTON 3 | 115 | 6.3688 | 6.3914 | 0.0226
GEN-2026-PR4 | 05 SOUTHWEST | 523159 | RB-SPURLCK 3 | 115 | 6.1 | 6.1062 | 0.0062
GEN-2026-PR4 | 05 SOUTHWEST | 523160 | FRISCO_WND 3 | 115 | 7.7094 | 7.733 | 0.0236
GEN-2026-PR4 | 05 SOUTHWEST | 523168 | SHERMAN 3 | 115 | 4.8545 | 4.8589 | 0.0044
GEN-2026-PR4 | 05 SOUTHWEST | 523174 | GOODWELLWND3 | 115 | 6.3939 | 6.4138 | 0.0199
GEN-2026-PR4 | 05 SOUTHWEST | 523175 | LASLEY 3 | 115 | 6.3664 | 6.3759 | 0.0095
GEN-2026-PR4 | 05 SOUTHWEST | 523176 | RB-ELKS 3 | 115 | 6.2876 | 6.2967 | 0.0091
GEN-2026-PR4 | 05 SOUTHWEST | 523177 | RB-SPURLCK+3 | 115 | 6.4981 | 6.5052 | 0.0071
GEN-2026-PR4 | 05 SOUTHWEST | 523178 | NP-LIPS_SHA2 | 69 | 0.5985 | 0.5986 | 0.0001
GEN-2026-PR4 | 05 SOUTHWEST | 523179 | NP-LIPSCOMB2 | 69 | 0.5981 | 0.5982 | 0.0001
GEN-2026-PR4 | 05 SOUTHWEST | 523180 | NP-BOOKER 2 | 69 | 0.9473 | 0.9474 | 0.0001
GEN-2026-PR4 | 05 SOUTHWEST | 523181 | NP-PERRYTON2 | 69 | 1.3967 | 1.3969 | 0.0002
GEN-2026-PR4 | 05 SOUTHWEST | 523182 | NP-PERYTN_G2 | 69 | 1.422 | 1.4222 | 0.0002
GEN-2026-PR4 | 05 SOUTHWEST | 523185 | SPEARMAN 2 | 69 | 4.4216 | 4.4242 | 0.0026
GEN-2026-PR4 | 05 SOUTHWEST | 523186 | SPEARMAN 3 | 115 | 9.5448 | 9.5654 | 0.0206
GEN-2026-PR4 | 05 SOUTHWEST | 523187 | NP-SHATTUCK2 | 69 | 0.5393 | 0.5393 | 0
GEN-2026-PR4 | 05 SOUTHWEST | 523188 | NP-LUCKY_G 2 | 69 | 1.5478 | 1.5481 | 0.0003
GEN-2026-PR4 | 05 SOUTHWEST | 523189 | NP-LUCKY_CR2 | 69 | 1.5462 | 1.5466 | 0.0004
GEN-2026-PR4 | 05 SOUTHWEST | 523190 | NP-ROGER_SP2 | 69 | 1.255 | 1.2552 | 0.0002
GEN-2026-PR4 | 05 SOUTHWEST | 523192 | NP-GLAZIR_G2 | 69 | 0.74 | 0.7401 | 0.0001
GEN-2026-PR4 | 05 SOUTHWEST | 523193 | NP-VALERO_P2 | 69 | 0.624 | 0.624 | 0
GEN-2026-PR4 | 05 SOUTHWEST | 523194 | NP-VALERO-G2 | 69 | 1.5393 | 1.5396 | 0.0003
GEN-2026-PR4 | 05 SOUTHWEST | 523195 | HANSFORD 3 | 115 | 11.0843 | 11.138 | 0.0537
GEN-2026-PR4 | 05 SOUTHWEST | 523203 | SPEARMNSUB 3 | 115 | 6.6017 | 6.6142 | 0.0125
GEN-2026-PR4 | 05 SOUTHWEST | 523204 | NP-ROGERS-G2 | 69 | 1.1187 | 1.1189 | 0.0002
GEN-2026-PR4 | 05 SOUTHWEST | 523205 | NP-ROGERS 2 | 69 | 1.0333 | 1.0334 | 0.0001
GEN-2026-PR4 | 05 SOUTHWEST | 523206 | NP-LEWIE_G 2 | 69 | 1.6913 | 1.6917 | 0.0004
GEN-2026-PR4 | 05 SOUTHWEST | 523207 | NP-LEWIE 2 | 69 | 1.5702 | 1.5705 | 0.0003
GEN-2026-PR4 | 05 SOUTHWEST | 523208 | NP-SPEARMAN2 | 69 | 2.6397 | 2.6406 | 0.0009
GEN-2026-PR4 | 05 SOUTHWEST | 523209 | NP-69_12_TP2 | 69 | 4.3804 | 4.383 | 0.0026
GEN-2026-PR4 | 05 SOUTHWEST | 523210 | NP-GRUVER 2 | 69 | 2.2897 | 2.2904 | 0.0007
GEN-2026-PR4 | 05 SOUTHWEST | 523218 | RB-FARIA 3 | 115 | 6.0354 | 6.0396 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 523220 | XIT_INTG 3 | 115 | 8.4562 | 8.4637 | 0.0075
GEN-2026-PR4 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 7.2211 | 7.2304 | 0.0093
GEN-2026-PR4 | 05 SOUTHWEST | 523222 | RB-WOLVES | 115 | 7.9074 | 7.914 | 0.0066
GEN-2026-PR4 | 05 SOUTHWEST | 523256 | ETTER 3 | 115 | 7.1078 | 7.1135 | 0.0057
GEN-2026-PR4 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 12.1734 | 12.1863 | 0.0129
GEN-2026-PR4 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.6362 | 4.6384 | 0.0022
GEN-2026-PR4 | 05 SOUTHWEST | 523277 | VALERO 3 | 115 | 13.0855 | 13.1067 | 0.0212
GEN-2026-PR4 | 05 SOUTHWEST | 523304 | MOORE_W 3 | 115 | 14.853 | 14.8805 | 0.0275
GEN-2026-PR4 | 05 SOUTHWEST | 523308 | MOORE_E 3 | 115 | 14.853 | 14.8805 | 0.0275
GEN-2026-PR4 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 9.5298 | 9.5577 | 0.0279
GEN-2026-PR4 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 11.042 | 11.0493 | 0.0073
GEN-2026-PR4 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 10.7844 | 10.8005 | 0.0161
GEN-2026-PR4 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.6848 | 6.7629 | 0.0781
GEN-2026-PR4 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.4915 | 9.5138 | 0.0223
GEN-2026-PR4 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 6.2028 | 6.2074 | 0.0046
GEN-2026-PR4 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 31.5502 | 31.6171 | 0.0669
GEN-2026-PR4 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 24.0985 | 24.1967 | 0.0982
GEN-2026-PR4 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 10.7665 | 10.8079 | 0.0414
GEN-2026-PR4 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 32.4715 | 32.5089 | 0.0374
GEN-2026-PR4 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 32.4715 | 32.5089 | 0.0374
GEN-2026-PR4 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 32.4715 | 32.5089 | 0.0374
GEN-2026-PR4 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 21.663 | 21.6714 | 0.0084
GEN-2026-PR4 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 20.659 | 20.6666 | 0.0076
GEN-2026-PR4 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 24.8078 | 24.8369 | 0.0291
GEN-2026-PR4 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 11.9231 | 11.9256 | 0.0025
GEN-2026-PR4 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 12.3073 | 12.3128 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 5.7891 | 5.7902 | 0.0011
GEN-2026-PR4 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 7.9421 | 7.9442 | 0.0021
GEN-2026-PR4 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 6.8941 | 6.9008 | 0.0067
GEN-2026-PR4 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 6.8941 | 6.9008 | 0.0067
GEN-2026-PR4 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.5853 | 8.5867 | 0.0014
GEN-2026-PR4 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.8425 | 9.8431 | 0.0006
GEN-2026-PR4 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.3582 | 11.3597 | 0.0015
GEN-2026-PR4 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 16.1773 | 16.1789 | 0.0016
GEN-2026-PR4 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 12.4773 | 12.4794 | 0.0021
GEN-2026-PR4 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.8267 | 24.8309 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 32.5492 | 32.5563 | 0.0071
GEN-2026-PR4 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.1925 | 15.198 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 11.5647 | 11.5655 | 0.0008
GEN-2026-PR4 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.6388 | 11.6396 | 0.0008
GEN-2026-PR4 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.6388 | 11.6396 | 0.0008
GEN-2026-PR4 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.6526 | 5.6528 | 0.0002
GEN-2026-PR4 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 26.1105 | 26.1132 | 0.0027
GEN-2026-PR4 | 05 SOUTHWEST | 525831 | TUCO_SVC 6 | 230 | 26.1105 | 26.1132 | 0.0027
GEN-2026-PR4 | 05 SOUTHWEST | 525839 | G17-151TAP | 345 | 10.9388 | 10.94 | 0.0012
GEN-2026-PR4 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 25.8729 | 25.8755 | 0.0026
GEN-2026-PR4 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.7518 | 11.7523 | 0.0005
GEN-2026-PR4 | 05 SOUTHWEST | 527598 | SAGA_NDCOL 7 | 345 | 12.2125 | 12.2167 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 15.1338 | 15.1406 | 0.0068
GEN-2026-PR4 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 15.1338 | 15.1406 | 0.0068
GEN-2026-PR4 | 05 SOUTHWEST | 527601 | SAGA_NCOL 7 | 345 | 12.2125 | 12.2167 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 15.1338 | 15.1406 | 0.0068
GEN-2026-PR4 | 05 SOUTHWEST | 527640 | MILO_WIND 7 | 345 | 14.7179 | 14.7245 | 0.0066
GEN-2026-PR4 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 12.0029 | 12.0071 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 14.7179 | 14.7245 | 0.0066
GEN-2026-PR4 | 05 SOUTHWEST | 527656 | CROSSROAD | 345 | 18.5456 | 18.5564 | 0.0108
GEN-2026-PR4 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 12.0029 | 12.0071 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 12.0029 | 12.0071 | 0.0042
GEN-2026-PR4 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 8.1986 | 8.2087 | 0.0101
GEN-2026-PR4 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 6.0526 | 6.056 | 0.0034
GEN-2026-PR4 | 05 SOUTHWEST | 531380 | HUGOTON2 | 69 | 2.9772 | 2.9789 | 0.0017
GEN-2026-PR4 | 05 SOUTHWEST | 531384 | MOSCOW 2 | 69 | 2.2401 | 2.2413 | 0.0012
GEN-2026-PR4 | 05 SOUTHWEST | 531385 | MOSCOWT2 | 69 | 2.3564 | 2.3577 | 0.0013
GEN-2026-PR4 | 05 SOUTHWEST | 531388 | NORTH6 2 | 69 | 2.6505 | 2.6522 | 0.0017
GEN-2026-PR4 | 05 SOUTHWEST | 531389 | NORTH6T2 | 69 | 3.101 | 3.1033 | 0.0023
GEN-2026-PR4 | 05 SOUTHWEST | 531395 | ROLLA 3 | 115 | 2.669 | 2.6712 | 0.0022
GEN-2026-PR4 | 05 SOUTHWEST | 531404 | WALKMYR2 | 69 | 8.683 | 8.7024 | 0.0194
GEN-2026-PR4 | 05 SOUTHWEST | 531405 | WALKMYR3 | 115 | 10.2136 | 10.2584 | 0.0448
GEN-2026-PR4 | 05 SOUTHWEST | 531406 | WOODS 2 | 69 | 6.2525 | 6.2624 | 0.0099
GEN-2026-PR4 | 05 SOUTHWEST | 531448 | HOLCOMB3 | 115 | 21.4529 | 21.4712 | 0.0183
GEN-2026-PR4 | 05 SOUTHWEST | 531449 | HOLCOMB7 | 345 | 9.5936 | 9.6159 | 0.0223
GEN-2026-PR4 | 05 SOUTHWEST | 531465 | SETAB 7 | 345 | 6.6772 | 6.6843 | 0.0071
GEN-2026-PR4 | 05 SOUTHWEST | 531479 | CHUGTON2 | 69 | 2.6802 | 2.6815 | 0.0013
GEN-2026-PR4 | 05 SOUTHWEST | 531481 | HUGOTON3 | 115 | 5.8334 | 5.8441 | 0.0107
GEN-2026-PR4 | 05 SOUTHWEST | 531494 | ABBK 3 | 115 | 5.3491 | 5.3581 | 0.009
GEN-2026-PR4 | 05 SOUTHWEST | 531501 | BUCKNER7 | 345 | 9.2325 | 9.2434 | 0.0109
GEN-2026-PR4 | 05 SOUTHWEST | 531502 | CIMRRN 7 | 345 | 7.3679 | 7.3749 | 0.007
GEN-2026-PR4 | 05 SOUTHWEST | 531504 | CIMWD2 7 | 345 | 7.3679 | 7.3749 | 0.007
GEN-2026-PR4 | 05 SOUTHWEST | 531510 | HARBNGR3 | 115 | 10.8584 | 10.9117 | 0.0533
GEN-2026-PR4 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.6788 | 6.7568 | 0.078
GEN-2026-PR4 | 05 SOUTHWEST | 533836 | VIOLA9 | 765 | 7.8565 | 7.8644 | 0.0079
GEN-2026-PR4 | 05 SOUTHWEST | 539654 | CIM-PLT3 | 115 | 6.1314 | 6.1392 | 0.0078
GEN-2026-PR4 | 05 SOUTHWEST | 539672 | E-LIBER3 | 115 | 4.8008 | 4.8059 | 0.0051
GEN-2026-PR4 | 05 SOUTHWEST | 539690 | E-PINE 3 | 115 | 4.1269 | 4.1306 | 0.0037
GEN-2026-PR4 | 05 SOUTHWEST | 562020 | PRSCRKII 7 | 345 | 10.8577 | 10.8876 | 0.0299
GEN-2026-PR4 | 05 SOUTHWEST | 585420 | SUBST HS | 345 | 7.2718 | 7.2852 | 0.0134
GEN-2026-PR4 | 05 SOUTHWEST | 588560 | GEN-2017-011 | 345 | 13.2185 | 13.3272 | 0.1087
GEN-2026-PR4 | 05 SOUTHWEST | 588860 | GEN-2017-047 | 115 | 4.9084 | 4.9194 | 0.011
GEN-2026-PR4 | 05 SOUTHWEST | 589380 | GEN-2017-100 | 115 | 5.7018 | 5.7162 | 0.0144
GEN-2026-PR4 | 05 SOUTHWEST | 599950 | LAMAR7 | 345 | 2.4574 | 2.4588 | 0.0014
GEN-2026-PR4 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.8425 | 9.8431 | 0.0006
GEN-2026-PR4 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.4684 | 14.4696 | 0.0012
GEN-2026-PR4 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.423 | 7.4235 | 0.0005
GEN-2026-PR4 | 05 SOUTHWEST | 762471 | GEN-2018-009 | 115 | 2.3367 | 2.3379 | 0.0012
GEN-2026-PR4 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 12.0973 | 12.0992 | 0.0019
GEN-2026-PR4 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.8938 | 8.8942 | 0.0004
GEN-2026-PR4 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 20.7476 | 20.8569 | 0.1093
GEN-2026-PR4 | 05 SOUTHWEST | 764980 | GEN-2020-008 | 345 | 6.6848 | 6.7629 | 0.0781
GEN-2026-PR4 | 05 SOUTHWEST | 765490 | GEN-2021-021 | 345 | 6.3063 | 6.3758 | 0.0695
GEN-2026-PR4 | 05 SOUTHWEST | 767221 | GEN-2022-012 | 345 | 23.7616 | 23.9052 | 0.1436
GEN-2026-PR4 | 05 SOUTHWEST | 767301 | GEN-2022-016 | 345 | 23.7616 | 23.9052 | 0.1436
GEN-2026-PR4 | 05 SOUTHWEST | 767321 | GEN-2022-017 | 345 | 23.3748 | 23.5137 | 0.1389
GEN-2026-PR4 | 05 SOUTHWEST | 772280 | G23-015-TAP | 345 | 8.2124 | 8.2356 | 0.0232
GEN-2026-PR4 | 05 SOUTHWEST | 772281 | GEN-2023-015 | 345 | 7.7964 | 7.8173 | 0.0209
GEN-2026-PR4 | 05 SOUTHWEST | 774121 | GEN-2023-107 | 345 | 5.221 | 5.2253 | 0.0043
GEN-2026-PR4 | 05 SOUTHWEST | 775421 | GEN-2023-172 | 345 | 8.7787 | 8.7974 | 0.0187
GEN-2026-PR4 | 05 SOUTHWEST | 776821 | GEN-2023-102 | 345 | 10.9648 | 10.982 | 0.0172
GEN-2026-PR4 | 05 SOUTHWEST | 777091 | GEN-2024-046 | 230 | 6.8671 | 6.9059 | 0.0388
GEN-2026-PR4 | 05 SOUTHWEST | 777931 | GEN-2024-032 | 115 | 5.8189 | 5.8296 | 0.0107
GEN-2026-PR4 | 05 SOUTHWEST | 778200 | G24-041-TAP | 345 | 9.5276 | 9.5286 | 0.001
GEN-2026-PR4 | 05 SOUTHWEST | 778201 | GEN-2024-041 | 345 | 7.541 | 7.5416 | 0.0006
GEN-2026-PR4 | 05 SOUTHWEST | 778238 | GEN-2024-042 | 345 | 6.2364 | 6.2368 | 0.0004
GEN-2026-PR4 | 05 SOUTHWEST | 778260 | G24-043-TAP | 345 | 16.3912 | 16.3995 | 0.0083
GEN-2026-PR4 | 05 SOUTHWEST | 778261 | GEN-2024-043 | 345 | 14.0395 | 14.0456 | 0.0061
GEN-2026-PR4 | 05 SOUTHWEST | 778320 | G24-045-TAP | 230 | 6.8834 | 6.9223 | 0.0389
GEN-2026-PR4 | 05 SOUTHWEST | 778321 | GEN-2024-045 | 230 | 6.8671 | 6.9059 | 0.0388
GEN-2026-PR4 | 05 SOUTHWEST | 778861 | GEN-2024-063 | 230 | 19.2986 | 19.3011 | 0.0025
GEN-2026-PR4 | 05 SOUTHWEST | 779281 | GEN-2024-077 | 230 | 4.6297 | 4.6318 | 0.0021
GEN-2026-PR4 | 05 SOUTHWEST | 779311 | GEN-2024-078 | 230 | 4.6297 | 4.6318 | 0.0021
GEN-2026-PR4 | 05 SOUTHWEST | 779941 | GEN-2024-099 | 230 | 12.4279 | 12.43 | 0.0021
GEN-2026-PR4 | 05 SOUTHWEST | 780031 | GEN-2024-102 | 345 | 5.4557 | 5.4629 | 0.0072
GEN-2026-PR4 | 05 SOUTHWEST | 780240 | G24-109-TAP | 345 | 13.4401 | 13.4445 | 0.0044
GEN-2026-PR4 | 05 SOUTHWEST | 780241 | GEN-2024-109 | 345 | 6.6251 | 6.6261 | 0.001
GEN-2026-PR4 | 05 SOUTHWEST | 780991 | GEN-2024-134 | 345 | 11.2486 | 11.2667 | 0.0181
GEN-2026-PR4 | 05 SOUTHWEST | 781021 | GEN-2024-135 | 345 | 11.2486 | 11.2667 | 0.0181
GEN-2026-PR4 | 05 SOUTHWEST | 781051 | GEN-2024-136 | 345 | 5.8865 | 5.892 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 781081 | GEN-2024-137 | 345 | 5.8865 | 5.892 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 781111 | GEN-2024-138 | 345 | 5.8865 | 5.892 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 781261 | GEN-2024-143 | 230 | 4.1766 | 4.1791 | 0.0025
GEN-2026-PR4 | 05 SOUTHWEST | 781291 | GEN-2024-144 | 345 | 5.8865 | 5.892 | 0.0055
GEN-2026-PR4 | 05 SOUTHWEST | 781321 | GEN-2024-145 | 230 | 4.1766 | 4.1791 | 0.0025
GEN-2026-PR4 | 05 SOUTHWEST | 781561 | GEN-2024-153 | 230 | 12.2014 | 12.2067 | 0.0053
GEN-2026-PR4 | 05 SOUTHWEST | 781591 | GEN-2024-154 | 345 | 13.8529 | 13.8649 | 0.012
GEN-2026-PR4 | 05 SOUTHWEST | 784291 | GEN-2024-244 | 115 | 9.3245 | 9.3666 | 0.0421
GEN-2026-PR4 | 05 SOUTHWEST | 784950 | G24-266_TAP | 345 | 12.8864 | 12.9695 | 0.0831
GEN-2026-PR4 | 05 SOUTHWEST | 784951 | GEN-2024-266 | 345 | 12.8864 | 12.9695 | 0.0831
GEN-2026-PR4 | 05 SOUTHWEST | 786061 | GEN-2024-303 | 345 | 13.646 | 13.6519 | 0.0059
GEN-2026-PR4 | 05 SOUTHWEST | 786091 | GEN-2024-304 | 345 | 13.646 | 13.6519 | 0.0059
GEN-2026-PR4 | 05 SOUTHWEST | 787891 | GEN-2024-364 | 230 | 12.2598 | 12.2652 | 0.0054
GEN-2026-PR4 | 05 SOUTHWEST | 787904 | G24-364-C1 | 230 | 12.2598 | 12.2652 | 0.0054
GEN-2026-PR4 | 05 SOUTHWEST | 787905 | G24-364-C2 | 230 | 12.2598 | 12.2652 | 0.0054
GEN-2026-PR4 | 05 SOUTHWEST | 788348 | ASGI-2024-03 | 115 | 2.6652 | 2.6675 | 0.0023
GEN-2026-PR4 | 05 SOUTHWEST | 788378 | ASGI-2024-00 | 115 | 5.2717 | 5.2841 | 0.0124
GEN-2026-PR4 | 05 SOUTHWEST | 999958 | ZSWSH_999958 | 765 | 8.1986 | 8.2087 | 0.0101

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
05 SOUTHWEST | GEN-2026-PR4 | 2.3029 | FAIL | 47.189 | PASS | N/A | N/A | YES

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | base | 3.4562 | FAIL | 47.3238 | PASS | 47223.7806 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 3.4578 | FAIL | 47.8993 | PASS | 47799.3161 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515634 [PALDR1W7 345.00] CKT 1 | 3.4361 | FAIL | 47.9273 | PASS | 47827.3187 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 3.3233 | FAIL | 48.5996 | PASS | 48499.5697 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 3.3231 | FAIL | 48.6025 | PASS | 48502.5404 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 3.2919 | FAIL | 49.442 | PASS | 49341.9521 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 2 | 3.2919 | FAIL | 49.442 | PASS | 49341.9521 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515686 [BLUWND 7 345.00] CKT 1 | 3.4425 | FAIL | 47.5502 | PASS | 47450.1827 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516074 [PONDRSA7 345.00] CKT 1 | 3.4529 | FAIL | 47.576 | PASS | 47475.9939 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 3.1895 | FAIL | 49.6271 | PASS | 49527.054 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 3.1894 | FAIL | 49.6291 | PASS | 49529.132 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 1 | 3.4289 | FAIL | 47.3614 | PASS | 47261.3631 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 2 | 3.226 | FAIL | Not Converged | PASS | Not Converged | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523019 [OSLO-SYLVIE7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 3.3826 | FAIL | 47.8057 | PASS | 47705.7411 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523040 [OLYMPIA7 345.00] TO BUS 523041 [FRWLN7 345.00] CKT 1 | 3.2895 | FAIL | 48.4477 | PASS | 48347.6799 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523040 [OLYMPIA7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 3.4351 | FAIL | 48.3953 | PASS | 48295.3192 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 523155 [OCHILTREE 6 230.00] CKT 1 | 3.2624 | FAIL | 49.8997 | PASS | 49799.7114 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 778320 [G24-045-TAP 230.00] CKT 1 | 2.9599 | FAIL | 55.9047 | PASS | 55804.7045 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523097 [HITCHLAND 7 345.00] TO BUS 523823 [CARPENTER 7 345.00] CKT 1 | 2.8318 | FAIL | 58.1192 | PASS | 58019.1936 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523097 [HITCHLAND 7 345.00] TO BUS 784950 [G24-266_TAP 345.00] CKT 1 | 3.4872 | FAIL | 47.9812 | PASS | 47881.1568 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523103 [NOBLE_WND 3 115.00] TO BUS 523131 [GRPLNS-HV2-3 115.00] CKT 1 | 3.454 | FAIL | 47.3583 | PASS | 47258.2839 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7 345.00] TO BUS 523853 [FINNEY 7 345.00] CKT 1 | 3.4674 | FAIL | 47.5335 | PASS | 47433.4783 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523130 [GRPLNS-HV4-3 115.00] TO BUS 523131 [GRPLNS-HV2-3 115.00] CKT 1 | 3.254 | FAIL | 49.9251 | PASS | 49825.1377 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 778320 [G24-045-TAP 230.00] CKT 1 | 3.4022 | FAIL | 48.7666 | PASS | 48666.6111 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 3.1141 | FAIL | 50.8033 | PASS | 50703.2938 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 772280 [G23-015-TAP 345.00] CKT 1 | 3.091 | FAIL | 51.7653 | PASS | 51665.3136 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523853 [FINNEY 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.4562 | FAIL | 47.189 | PASS | 47088.997 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523853 [FINNEY 7 345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 3.1112 | FAIL | 50.8398 | PASS | 50739.8463 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523853 [FINNEY 7 345.00] TO BUS 772280 [G23-015-TAP 345.00] CKT 1 | 3.4346 | FAIL | 47.4623 | PASS | 47362.2972 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 525549 [TOLK 7 345.00] CKT 1 | 2.7539 | FAIL | 58.6936 | PASS | 58593.5652 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 784950 [G24-266_TAP 345.00] CKT 1 | 3.4261 | FAIL | 47.7178 | PASS | 47617.82 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531405 [WALKMYR3 115.00] TO BUS 531481 [HUGOTON3 115.00] CKT 1 | 3.4022 | FAIL | 48.7658 | PASS | 48665.7897 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531405 [WALKMYR3 115.00] TO BUS 531510 [HARBNGR3 115.00] CKT 1 | 3.4429 | FAIL | 47.8703 | PASS | 47770.2647 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531405 [WALKMYR3 115.00] TO BUS 539654 [CIM-PLT3 115.00] CKT 1 | 3.4568 | FAIL | 47.608 | PASS | 47508.0213 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515618 [BALKOW 7 345.00] TO BUS 515615 [BALKOW12 34.5.00] TO BUS 515617 [BALKOWT2 12.5] CKT 1 | 3.4568 | FAIL | 47.608 | PASS | 47508.0213 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515618 [BALKOW 7 345.00] TO BUS 515614 [BALKOW11 34.5.00] TO BUS 515616 [BALKOWT1 12.5] CKT 1 | 3.4583 | FAIL | 47.822 | PASS | 47722.0038 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515634 [PALDR1W7 345.00] TO BUS 515591 [PALDRW11 34.5.00] TO BUS 515593 [PALDRWT1 13.2] CKT 1 | 3.433 | FAIL | 47.4339 | PASS | 47333.8671 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515634 [PALDR1W7 345.00] TO BUS 915591 [PALDRW21 34.5.00] TO BUS 915593 [PALDRW2T1 13.8] CKT 1 | 3.4492 | FAIL | 47.4385 | PASS | 47338.4677 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515686 [BLUWND 7 345.00] TO BUS 515680 [BLUWND11 34.5.00] TO BUS 515681 [BLUWDT11 13.8] CKT 1 | 3.4493 | FAIL | 47.4362 | PASS | 47336.1666 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515686 [BLUWND 7 345.00] TO BUS 515684 [BLUWND21 34.5.00] TO BUS 515685 [BLUWDT21 13.8] CKT 1 | 3.4092 | FAIL | 47.4739 | PASS | 47373.9071 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 511553 [CHISHOLM7 345.00] CKT 1 | 3.4059 | FAIL | 47.6007 | PASS | 47500.7233 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 3.4535 | FAIL | 47.3279 | PASS | 47227.858 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 515458 [BORDER 7 345.00] CKT 2 | 3.4535 | FAIL | 47.3279 | PASS | 47227.858 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516074 [PONDRSA7 345.00] TO BUS 516073 [PDRSAL11 34.5.00] TO BUS 516075 [PDRSAT11 13.8] CKT 1 | 3.4522 | FAIL | 47.5834 | PASS | 47483.3638 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 3.3096 | FAIL | 48.5433 | PASS | 48443.3396 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 2 | 3.3094 | FAIL | 48.5458 | PASS | 48445.8211 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 516146 [25MILE 7 345.00] CKT 1 | 3.4562 | FAIL | 47.3224 | PASS | 47222.4271 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 588560 [GEN-2017-011 345.00] CKT 1 | 3.4562 | FAIL | 47.3228 | PASS | 47222.8276 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523019 [OSLO-SYLVIE7 345.00] TO BUS 523020 [SYLVIE 7 345.00] CKT 1 | 3.3415 | FAIL | 48.074 | PASS | 47973.9589 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523019 [OSLO-SYLVIE7 345.00] TO BUS 523030 [OLSO 7 345.00] CKT 1 | 3.3388 | FAIL | 48.181 | PASS | 48081.0499 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523040 [OLYMPIA7 345.00] TO BUS 523048 [GRVR_T2 1 34.5.00] TO BUS 523047 [GRVR_TY 1 13.8] CKT 1 | 3.365 | FAIL | 47.9382 | PASS | 47838.2205 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523041 [FRWLN7 345.00] TO BUS 523043 [FRWLN_T1_L 1 34.5.00] TO BUS 523042 [FRWLN_TY 1 13.8] CKT 1 | 3.3815 | FAIL | 47.8169 | PASS | 47716.9434 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523084 [SOONER 3 115.00] CKT 1 | 3.456 | FAIL | 47.5646 | PASS | 47464.5541 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523084 [SOONER 3 115.00] CKT 2 | 3.4566 | FAIL | 47.4182 | PASS | 47318.2469 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523160 [FRISCO_WND 3 115.00] CKT 1 | 3.4052 | FAIL | 47.8586 | PASS | 47758.5891 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523174 [GOODWELLWND3 115.00] CKT 1 | 3.4831 | FAIL | 47.2376 | PASS | 47137.5531 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523195 [HANSFORD 3 115.00] CKT 1 | 3.3856 | FAIL | 48.1227 | PASS | 48022.652 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523095 [HITCHLAND 6 230.00] TO BUS 523098 [HITCHLD_TR41 13.2] CKT 2 | 3.4364 | FAIL | 48.5881 | PASS | 48488.0502 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523095 [HITCHLAND 6 230.00] TO BUS 523092 [HITCHLD_TR11 13.2] CKT 1 | 3.4346 | FAIL | 48.6605 | PASS | 48560.4595 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 523097 [HITCHLAND 7 345.00] TO BUS 523091 [HITCHLD_TR01 13.2] CKT 1 | 3.4074 | FAIL | 49.329 | PASS | 49228.9956 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 523097 [HITCHLAND 7 345.00] TO BUS 523094 [HITCHLD_TR21 13.2] CKT 2 | 3.3935 | FAIL | 49.9097 | PASS | 49809.7379 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523097 [HITCHLAND 7 345.00] TO BUS 523103 [NOBLE_WND 3 115.00] TO BUS 523102 [NOBLE_TR 1 13.8] CKT 1 | 3.4872 | FAIL | 47.9835 | PASS | 47883.5072 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7 345.00] TO BUS 523116 [BUFF_DUNES11 34.5.00] TO BUS 523114 [BUFF_DN_TR11 13.2] CKT 1 | 3.4554 | FAIL | 47.3423 | PASS | 47242.2509 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7 345.00] TO BUS 523117 [BUFF_DUNES21 34.5.00] TO BUS 523115 [BUFF_DN_TR21 13.2] CKT 2 | 3.4554 | FAIL | 47.3428 | PASS | 47242.8409 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523130 [GRPLNS-HV4-3 115.00] TO BUS 523127 [GRPLNS-LV4-1 34.5.00] CKT 1 | 3.4663 | FAIL | 47.5398 | PASS | 47439.7732 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523131 [GRPLNS-HV2-3 115.00] TO BUS 523128 [NBLWND-LV2 1 34.5.00] CKT 1 | 3.4733 | FAIL | 47.4981 | PASS | 47398.1433 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523131 [GRPLNS-HV2-3 115.00] TO BUS 523129 [GRPLNS-LV2-1 34.5.00] CKT 1 | 3.4645 | FAIL | 47.5306 | PASS | 47430.5692 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523101 [BULL_CREEK 3 115.00] CKT 1 | 3.4562 | FAIL | 47.2985 | PASS | 47198.5324 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523140 [TXFARMS 3 115.00] CKT 1 | 3.4292 | FAIL | 47.5381 | PASS | 47438.091 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523145 [WADE_TP 3 115.00] CKT 1 | 3.4449 | FAIL | 47.645 | PASS | 47544.9949 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523158 [PERRYTON 3 115.00] CKT 1 | 3.4562 | FAIL | 47.3238 | PASS | 47223.8183 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523158 [PERRYTON 3 115.00] CKT 2 | 3.4562 | FAIL | 47.3238 | PASS | 47223.8193 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523155 [OCHILTREE 6 230.00] TO BUS 523151 [OCHLTRE_TR11 13.2] CKT 1 | 3.4328 | FAIL | 48.4057 | PASS | 48305.7102 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523221 [XIT_INTG 6 230.00] CKT 1 | 3.4498 | FAIL | 47.4381 | PASS | 47338.1141 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523308 [MOORE_E 3 115.00] CKT 2 | 3.4555 | FAIL | 47.386 | PASS | 47285.9758 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523323 [MCDWL_CREEK6 230.00] CKT 1 | 3.4163 | FAIL | 47.4334 | PASS | 47333.3586 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523308 [MOORE_E 3 115.00] TO BUS 523302 [MOORE_TR1 1 13.2] CKT 1 | 3.4529 | FAIL | 47.3825 | PASS | 47282.4559 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 764980 [GEN-2020-008 345.00] CKT 1 | 3.4598 | FAIL | 47.2864 | PASS | 47186.4131 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 765490 [GEN-2021-021 345.00] CKT 1 | 3.4569 | FAIL | 47.3167 | PASS | 47216.7015 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523323 [MCDWL_CREEK6 230.00] CKT 1 | 3.4337 | FAIL | 47.2964 | PASS | 47196.4199 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523869 [CHAN+TASCOS6 230.00] CKT 1 | 3.4455 | FAIL | 47.2893 | PASS | 47189.3366 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523979 [HARRNG_EST 6 230.00] CKT 1 | 3.4412 | FAIL | 47.3477 | PASS | 47247.7198 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 524010 [ROLLHILLS 6 230.00] CKT 1 | 3.4411 | FAIL | 47.3586 | PASS | 47258.5918 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 524267 [BUSHLAND 6 230.00] CKT 1 | 3.4517 | FAIL | 47.3887 | PASS | 47288.7376 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 525461 [NEWHART 6 230.00] CKT 1 | 3.4505 | FAIL | 47.3516 | PASS | 47251.5898 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523961 [POTTER_CO 7 345.00] TO BUS 523958 [POTTER_TR2 1 13.2] CKT 2 | 3.4446 | FAIL | 47.4461 | PASS | 47346.135 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523961 [POTTER_CO 7 345.00] TO BUS 523957 [POTTER_TR 1 13.2] CKT 1 | 3.4446 | FAIL | 47.4461 | PASS | 47346.135 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 524296 [SPNSPUR_WND7 345.00] CKT 1 | 3.467 | FAIL | 47.3511 | PASS | 47251.1253 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523964 [POTTER_TR3 1 13.2] CKT 1 | 3.4553 | FAIL | 47.3332 | PASS | 47233.2252 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523965 [POTTER_TR3 2 13.2] CKT 1 | 3.4553 | FAIL | 47.3332 | PASS | 47233.2252 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523967 [POTTER_TR3 3 13.2] CKT 1 | 3.4553 | FAIL | 47.3332 | PASS | 47233.2252 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523966 [POTTER_CO 9 765.00] TO BUS 515378 [WWRDEHV9 765.00] CKT 1 | 4.6695 | FAIL | Not Converged | PASS | Not Converged | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523966 [POTTER_CO 9 765.00] TO BUS 527669 [CROSSROADS 9 765.00] CKT 1 | 3.3554 | FAIL | 48.0813 | PASS | 47981.3369 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 525549 [TOLK 7 345.00] TO BUS 780240 [G24-109-TAP 345.00] CKT 1 | 3.4531 | FAIL | 47.3007 | PASS | 47200.7487 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 525549 [TOLK 7 345.00] TO BUS 525531 [TOLK 6 230.00] TO BUS 525538 [TOLK_TR2 1 13.2] CKT 2 | 3.4515 | FAIL | 47.3236 | PASS | 47223.6439 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 525549 [TOLK 7 345.00] TO BUS 525531 [TOLK 6 230.00] TO BUS 525537 [TOLK_TR 1 13.2] CKT 1 | 3.4515 | FAIL | 47.3236 | PASS | 47223.6489 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531404 [WALKMYR2 69.00] TO BUS 531389 [NORTH6T2 69.00] CKT 1 | 3.4558 | FAIL | 47.3663 | PASS | 47266.3372 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531404 [WALKMYR2 69.00] TO BUS 531406 [WOODS 2 69.00] CKT 1 | 3.4559 | FAIL | 47.3541 | PASS | 47254.1317 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531404 [WALKMYR2 69.00] TO BUS 531405 [WALKMYR3 115.00] TO BUS 531252 [WALKMYR1 13.8] CKT 1 | 3.4555 | FAIL | 47.3967 | PASS | 47296.743 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 3.4212 | FAIL | 47.7248 | PASS | 47624.7605 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 3.415 | FAIL | 47.8426 | PASS | 47742.5972 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 659133 [SIDNEY__-MB3 345.00] CKT 1 | 3.4565 | FAIL | 47.3207 | PASS | 47220.6647 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 775421 [GEN-2023-172 345.00] CKT 1 | 3.4564 | FAIL | 47.3162 | PASS | 47216.1763 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 780031 [GEN-2024-102 345.00] CKT 1 | 3.4195 | FAIL | 47.593 | PASS | 47493.0384 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.8] CKT 1 | 3.4284 | FAIL | 47.5145 | PASS | 47414.4613 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 531483 [GRANTTP3 115.00] CKT 1 | 3.4558 | FAIL | 47.3549 | PASS | 47254.8657 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 531494 [ABBK 3 115.00] CKT 1 | 3.4561 | FAIL | 47.3376 | PASS | 47237.5742 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 777931 [GEN-2024-032 115.00] CKT 1 | 3.4554 | FAIL | 47.4077 | PASS | 47307.7256 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 531380 [HUGOTON2 69.00] TO BUS 531261 [HUGOTON1 13.8] CKT 1 | 3.4022 | FAIL | 48.7667 | PASS | 48666.661 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-1 13.8] CKT 1 | 3.4565 | FAIL | 47.3055 | PASS | 47205.4675 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539640 [HAYNE3 115.00] CKT 1 | 3.4556 | FAIL | 47.3448 | PASS | 47244.8345 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539652 [CMRIVTP3 115.00] CKT 1 | 3.4417 | FAIL | 47.2404 | PASS | 47140.4429 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539749 [N-CIMRN3 115.00] CKT 1 | 3.4541 | FAIL | 47.4825 | PASS | 47382.5185 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539780 [CIM PLT1 13.8.00] CKT 1 | 3.4565 | FAIL | 47.3239 | PASS | 47223.8898 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 762471 [GEN-2018-009 115.00] CKT 1 | 3.4563 | FAIL | 47.3229 | PASS | 47222.9367 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 772280 [G23-015-TAP 345.00] TO BUS 772281 [GEN-2023-015 345.00] CKT 1 | 3.4704 | FAIL | 47.3326 | PASS | 47232.6275 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 778320 [G24-045-TAP 230.00] TO BUS 777091 [GEN-2024-046 230.00] CKT 1 | 3.4704 | FAIL | 47.3326 | PASS | 47232.6275 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 778320 [G24-045-TAP 230.00] TO BUS 778321 [GEN-2024-045 230.00] CKT 1 | 3.4986 | FAIL | 47.3275 | PASS | 47227.5157 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 784950 [G24-266_TAP 345.00] TO BUS 784951 [GEN-2024-266 345.00] CKT 1 | 3.4024 | FAIL | 47.3627 | PASS | 47262.6827 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 & 2 | 2.3029 | FAIL | 62.5364 | PASS | 62436.3996 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523084 [SOONER 3 115.00] CKT 1 & 2 | 3.451 | FAIL | 48.1588 | PASS | 48058.7658 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29SP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523158 [PERRYTON 3 115.00] CKT 1 & 2 | 3.4533 | FAIL | 47.4408 | PASS | 47340.8383 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | base | 3.4953 | FAIL | 48.4607 | PASS | 48360.6687 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 3.4971 | FAIL | 49.122 | PASS | 49021.9959 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515634 [PALDR1W7 345.00] CKT 1 | 3.4759 | FAIL | 49.1536 | PASS | 49053.6171 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 3.3599 | FAIL | 49.8925 | PASS | 49792.5335 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 3.3597 | FAIL | 49.8958 | PASS | 49795.8359 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 3.336 | FAIL | 50.8449 | PASS | 50744.9429 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 2 | 3.336 | FAIL | 50.8449 | PASS | 50744.9429 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 515686 [BLUWND 7 345.00] CKT 1 | 3.4868 | FAIL | 48.714 | PASS | 48614.0128 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516074 [PONDRSA7 345.00] CKT 1 | 3.4989 | FAIL | 48.7488 | PASS | 48648.817 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 3.2345 | FAIL | 51.0415 | PASS | 50941.514 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515677 [BADGER 7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 3.2343 | FAIL | 51.0438 | PASS | 50943.8411 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 1 | 3.4872 | FAIL | 48.4918 | PASS | 48391.8041 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 523961 [POTTER_CO 7 345.00] CKT 2 | 3.4872 | FAIL | 48.4919 | PASS | 48391.8916 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523040 [OLYMPIA7 345.00] TO BUS 523041 [FRWLN7 345.00] CKT 1 | 3.4149 | FAIL | 49.0128 | PASS | 48912.8139 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523040 [OLYMPIA7 345.00] TO BUS 523097 [HITCHLAND 7 345.00] CKT 1 | 3.3152 | FAIL | 49.7496 | PASS | 49649.5816 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 523155 [OCHILTREE 6 230.00] CKT 1 | 3.4753 | FAIL | 49.3899 | PASS | 49289.9487 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 778320 [G24-045-TAP 230.00] CKT 1 | 3.3002 | FAIL | 51.3227 | PASS | 51222.7201 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523097 [HITCHLAND 7 345.00] TO BUS 523823 [CARPENTER 7 345.00] CKT 1 | 2.9891 | FAIL | 58.2509 | PASS | 58150.9301 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523097 [HITCHLAND 7 345.00] TO BUS 784950 [G24-266_TAP 345.00] CKT 1 | 2.8577 | FAIL | 60.75 | PASS | 60650.0164 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523103 [NOBLE_WND 3 115.00] TO BUS 523131 [GRPLNS-HV2-3 115.00] CKT 1 | 3.5154 | FAIL | 49.2088 | PASS | 49108.8045 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7 345.00] TO BUS 523853 [FINNEY 7 345.00] CKT 1 | 3.4962 | FAIL | 48.5036 | PASS | 48403.5747 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523130 [GRPLNS-HV4-3 115.00] TO BUS 523131 [GRPLNS-HV2-3 115.00] CKT 1 | 3.5013 | FAIL | 48.7007 | PASS | 48600.7244 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 778320 [G24-045-TAP 230.00] CKT 1 | 3.2947 | FAIL | 51.3467 | PASS | 51246.724 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 531512 [HARBNGR7 345.00] CKT Z1 | 3.4401 | FAIL | 49.8344 | PASS | 49734.4054 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 772280 [G23-015-TAP 345.00] CKT 1 | 3.1469 | FAIL | 52.8213 | PASS | 52721.2866 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523853 [FINNEY 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 3.1296 | FAIL | 52.0491 | PASS | 51949.1252 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523853 [FINNEY 7 345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 3.4955 | FAIL | 48.4542 | PASS | 48354.2145 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523853 [FINNEY 7 345.00] TO BUS 772280 [G23-015-TAP 345.00] CKT 1 | 3.1444 | FAIL | 52.7654 | PASS | 52665.3882 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 525549 [TOLK 7 345.00] CKT 1 | 3.4734 | FAIL | 48.6116 | PASS | 48511.6268 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 784950 [G24-266_TAP 345.00] CKT 1 | 2.7813 | FAIL | 61.4729 | PASS | 61372.9195 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531405 [WALKMYR3 115.00] TO BUS 531481 [HUGOTON3 115.00] CKT 1 | 3.4675 | FAIL | 48.861 | PASS | 48761.0197 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531405 [WALKMYR3 115.00] TO BUS 531510 [HARBNGR3 115.00] CKT 1 | 3.4401 | FAIL | 49.8335 | PASS | 49733.5244 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531405 [WALKMYR3 115.00] TO BUS 539654 [CIM-PLT3 115.00] CKT 1 | 3.4775 | FAIL | 48.9931 | PASS | 48893.0767 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515618 [BALKOW 7 345.00] TO BUS 515615 [BALKOW12 34.5.00] TO BUS 515617 [BALKOWT2 12.5] CKT 1 | 3.4957 | FAIL | 48.7869 | PASS | 48686.8795 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515618 [BALKOW 7 345.00] TO BUS 515614 [BALKOW11 34.5.00] TO BUS 515616 [BALKOWT1 12.5] CKT 1 | 3.4957 | FAIL | 48.7869 | PASS | 48686.8795 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515634 [PALDR1W7 345.00] TO BUS 515591 [PALDRW11 34.5.00] TO BUS 515593 [PALDRWT1 13.2] CKT 1 | 3.4978 | FAIL | 49.0323 | PASS | 48932.262 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515634 [PALDR1W7 345.00] TO BUS 915591 [PALDRW21 34.5.00] TO BUS 915593 [PALDRW2T1 13.8] CKT 1 | 3.4699 | FAIL | 48.5882 | PASS | 48488.1661 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515686 [BLUWND 7 345.00] TO BUS 515680 [BLUWND11 34.5.00] TO BUS 515681 [BLUWDT11 13.8] CKT 1 | 3.4927 | FAIL | 48.5868 | PASS | 48486.8018 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 515686 [BLUWND 7 345.00] TO BUS 515684 [BLUWND21 34.5.00] TO BUS 515685 [BLUWDT21 13.8] CKT 1 | 3.4927 | FAIL | 48.5858 | PASS | 48485.7833 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 511553 [CHISHOLM7 345.00] CKT 1 | 3.4498 | FAIL | 48.6591 | PASS | 48559.0833 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 3.4568 | FAIL | 48.7251 | PASS | 48625.1234 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 515458 [BORDER 7 345.00] CKT 1 | 3.494 | FAIL | 48.4668 | PASS | 48366.7732 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 515458 [BORDER 7 345.00] CKT 2 | 3.494 | FAIL | 48.4668 | PASS | 48366.7732 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516074 [PONDRSA7 345.00] TO BUS 516073 [PDRSAL11 34.5.00] TO BUS 516075 [PDRSAT11 13.8] CKT 1 | 3.4972 | FAIL | 48.758 | PASS | 48658.0333 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 | 3.3497 | FAIL | 49.8241 | PASS | 49724.0779 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 2 | 3.3495 | FAIL | 49.8268 | PASS | 49726.8337 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 516146 [25MILE 7 345.00] CKT 1 | 3.496 | FAIL | 48.4587 | PASS | 48358.6906 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 588560 [GEN-2017-011 345.00] CKT 1 | 3.4957 | FAIL | 48.4593 | PASS | 48359.3159 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523019 [OSLO-SYLVIE7 345.00] TO BUS 523020 [SYLVIE 7 345.00] CKT 1 | 3.3665 | FAIL | 49.3107 | PASS | 49210.7408 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523019 [OSLO-SYLVIE7 345.00] TO BUS 523030 [OLSO 7 345.00] CKT 1 | 3.3533 | FAIL | 49.4311 | PASS | 49331.073 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523040 [OLYMPIA7 345.00] TO BUS 523048 [GRVR_T2 1 34.5.00] TO BUS 523047 [GRVR_TY 1 13.8] CKT 1 | 3.3941 | FAIL | 49.1609 | PASS | 49060.8922 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523041 [FRWLN7 345.00] TO BUS 523043 [FRWLN_T1_L 1 34.5.00] TO BUS 523042 [FRWLN_TY 1 13.8] CKT 1 | 3.4131 | FAIL | 49.026 | PASS | 48926.0456 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523084 [SOONER 3 115.00] CKT 1 | 3.4941 | FAIL | 48.6192 | PASS | 48519.2432 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523084 [SOONER 3 115.00] CKT 2 | 3.4954 | FAIL | 48.5267 | PASS | 48426.7342 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523160 [FRISCO_WND 3 115.00] CKT 1 | 3.4454 | FAIL | 49.2514 | PASS | 49151.4075 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523174 [GOODWELLWND3 115.00] CKT 1 | 3.5031 | FAIL | 48.414 | PASS | 48314.0426 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523195 [HANSFORD 3 115.00] CKT 1 | 3.4308 | FAIL | 49.2079 | PASS | 49107.9497 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523095 [HITCHLAND 6 230.00] TO BUS 523098 [HITCHLD_TR41 13.2] CKT 2 | 3.4766 | FAIL | 49.6348 | PASS | 49534.8042 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523095 [HITCHLAND 6 230.00] TO BUS 523092 [HITCHLD_TR11 13.2] CKT 1 | 3.475 | FAIL | 49.7018 | PASS | 49601.8038 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 523097 [HITCHLAND 7 345.00] TO BUS 523091 [HITCHLD_TR01 13.2] CKT 1 | 3.4481 | FAIL | 50.3858 | PASS | 50285.8393 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523095 [HITCHLAND 6 230.00] TO BUS 523097 [HITCHLAND 7 345.00] TO BUS 523094 [HITCHLD_TR21 13.2] CKT 2 | 3.4347 | FAIL | 50.9443 | PASS | 50844.2564 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523097 [HITCHLAND 7 345.00] TO BUS 523103 [NOBLE_WND 3 115.00] TO BUS 523102 [NOBLE_TR 1 13.8] CKT 1 | 3.5154 | FAIL | 49.2113 | PASS | 49111.3474 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7 345.00] TO BUS 523116 [BUFF_DUNES11 34.5.00] TO BUS 523114 [BUFF_DN_TR11 13.2] CKT 1 | 3.4958 | FAIL | 48.484 | PASS | 48384.0245 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7 345.00] TO BUS 523117 [BUFF_DUNES21 34.5.00] TO BUS 523115 [BUFF_DN_TR21 13.2] CKT 2 | 3.4958 | FAIL | 48.4846 | PASS | 48384.6487 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523130 [GRPLNS-HV4-3 115.00] TO BUS 523127 [GRPLNS-LV4-1 34.5.00] CKT 1 | 3.4999 | FAIL | 48.7081 | PASS | 48608.1263 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523131 [GRPLNS-HV2-3 115.00] TO BUS 523128 [NBLWND-LV2 1 34.5.00] CKT 1 | 3.5073 | FAIL | 48.6602 | PASS | 48560.2227 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523131 [GRPLNS-HV2-3 115.00] TO BUS 523129 [GRPLNS-LV2-1 34.5.00] CKT 1 | 3.4993 | FAIL | 48.6987 | PASS | 48598.6595 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523101 [BULL_CREEK 3 115.00] CKT 1 | 3.4962 | FAIL | 48.4445 | PASS | 48344.4528 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523140 [TXFARMS 3 115.00] CKT 1 | 3.4676 | FAIL | 48.6822 | PASS | 48582.1891 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523145 [WADE_TP 3 115.00] CKT 1 | 3.4891 | FAIL | 48.714 | PASS | 48614.0146 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523158 [PERRYTON 3 115.00] CKT 1 | 3.4953 | FAIL | 48.4607 | PASS | 48360.6941 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523158 [PERRYTON 3 115.00] CKT 2 | 3.4953 | FAIL | 48.4607 | PASS | 48360.6809 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523155 [OCHILTREE 6 230.00] TO BUS 523151 [OCHLTRE_TR11 13.2] CKT 1 | 3.4722 | FAIL | 49.4031 | PASS | 49303.0749 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523221 [XIT_INTG 6 230.00] CKT 1 | 3.4884 | FAIL | 48.5962 | PASS | 48496.1555 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523308 [MOORE_E 3 115.00] CKT 2 | 3.4947 | FAIL | 48.5176 | PASS | 48417.6465 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523323 [MCDWL_CREEK6 230.00] CKT 1 | 3.4519 | FAIL | 48.6499 | PASS | 48549.92 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6 230.00] TO BUS 523308 [MOORE_E 3 115.00] TO BUS 523302 [MOORE_TR1 1 13.2] CKT 1 | 3.4921 | FAIL | 48.518 | PASS | 48418.0403 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 764980 [GEN-2020-008 345.00] CKT 1 | 3.5013 | FAIL | 48.4143 | PASS | 48314.2648 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523823 [CARPENTER 7 345.00] TO BUS 765490 [GEN-2021-021 345.00] CKT 1 | 3.4964 | FAIL | 48.4518 | PASS | 48351.85 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523323 [MCDWL_CREEK6 230.00] CKT 1 | 3.468 | FAIL | 48.5063 | PASS | 48406.3345 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523869 [CHAN+TASCOS6 230.00] CKT 1 | 3.4843 | FAIL | 48.4185 | PASS | 48318.4887 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523979 [HARRNG_EST 6 230.00] CKT 1 | 3.481 | FAIL | 48.4905 | PASS | 48390.5114 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 524010 [ROLLHILLS 6 230.00] CKT 1 | 3.4807 | FAIL | 48.5 | PASS | 48399.9549 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 524267 [BUSHLAND 6 230.00] CKT 1 | 3.49 | FAIL | 48.5257 | PASS | 48425.7136 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 525461 [NEWHART 6 230.00] CKT 1 | 3.489 | FAIL | 48.4934 | PASS | 48393.371 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523961 [POTTER_CO 7 345.00] TO BUS 523958 [POTTER_TR2 1 13.2] CKT 2 | 3.4854 | FAIL | 48.5714 | PASS | 48471.3512 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523959 [POTTER_CO 6 230.00] TO BUS 523961 [POTTER_CO 7 345.00] TO BUS 523957 [POTTER_TR 1 13.2] CKT 1 | 3.4854 | FAIL | 48.5714 | PASS | 48471.3512 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 524296 [SPNSPUR_WND7 345.00] CKT 1 | 3.4986 | FAIL | 48.4957 | PASS | 48395.6657 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523964 [POTTER_TR3 1 13.2] CKT 1 | 3.4946 | FAIL | 48.4711 | PASS | 48371.1199 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523965 [POTTER_TR3 2 13.2] CKT 1 | 3.4946 | FAIL | 48.4711 | PASS | 48371.1199 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523961 [POTTER_CO 7 345.00] TO BUS 523966 [POTTER_CO 9 765.00] TO BUS 523967 [POTTER_TR3 3 13.2] CKT 1 | 3.4946 | FAIL | 48.4711 | PASS | 48371.1199 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523966 [POTTER_CO 9 765.00] TO BUS 515378 [WWRDEHV9 765.00] CKT 1 | 4.5125 | FAIL | Not Converged | PASS | Not Converged | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523966 [POTTER_CO 9 765.00] TO BUS 527669 [CROSSROADS 9 765.00] CKT 1 | 3.3978 | FAIL | 49.2886 | PASS | 49188.5809 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 525549 [TOLK 7 345.00] TO BUS 780240 [G24-109-TAP 345.00] CKT 1 | 3.4938 | FAIL | 48.4414 | PASS | 48341.3983 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 525549 [TOLK 7 345.00] TO BUS 525531 [TOLK 6 230.00] TO BUS 525538 [TOLK_TR2 1 13.2] CKT 2 | 3.4906 | FAIL | 48.462 | PASS | 48362.0309 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 525549 [TOLK 7 345.00] TO BUS 525531 [TOLK 6 230.00] TO BUS 525537 [TOLK_TR 1 13.2] CKT 1 | 3.4906 | FAIL | 48.462 | PASS | 48362.0258 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531404 [WALKMYR2 69.00] TO BUS 531389 [NORTH6T2 69.00] CKT 1 | 3.4951 | FAIL | 48.487 | PASS | 48386.9849 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531404 [WALKMYR2 69.00] TO BUS 531406 [WOODS 2 69.00] CKT 1 | 3.4951 | FAIL | 48.4795 | PASS | 48379.5202 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531404 [WALKMYR2 69.00] TO BUS 531405 [WALKMYR3 115.00] TO BUS 531252 [WALKMYR1 13.8] CKT 1 | 3.4956 | FAIL | 48.5038 | PASS | 48403.8494 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 3.4685 | FAIL | 48.7549 | PASS | 48654.8642 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 3.4735 | FAIL | 48.9049 | PASS | 48804.8949 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 659133 [SIDNEY__-MB3 345.00] CKT 1 | 3.4718 | FAIL | 48.5594 | PASS | 48459.409 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 775421 [GEN-2023-172 345.00] CKT 1 | 3.4954 | FAIL | 48.4554 | PASS | 48355.3735 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 780031 [GEN-2024-102 345.00] CKT 1 | 3.4955 | FAIL | 48.4483 | PASS | 48348.2584 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.8] CKT 1 | 3.47 | FAIL | 48.6067 | PASS | 48506.6779 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 531483 [GRANTTP3 115.00] CKT 1 | 3.4694 | FAIL | 48.644 | PASS | 48544.0037 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 531494 [ABBK 3 115.00] CKT 1 | 3.4946 | FAIL | 48.5308 | PASS | 48430.8289 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 777931 [GEN-2024-032 115.00] CKT 1 | 3.4952 | FAIL | 48.4738 | PASS | 48373.8091 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531481 [HUGOTON3 115.00] TO BUS 531380 [HUGOTON2 69.00] TO BUS 531261 [HUGOTON1 13.8] CKT 1 | 3.4948 | FAIL | 48.5131 | PASS | 48413.0935 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-1 13.8] CKT 1 | 3.4401 | FAIL | 49.8345 | PASS | 49734.5455 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539640 [HAYNE3 115.00] CKT 1 | 3.4948 | FAIL | 48.4552 | PASS | 48355.1931 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539652 [CMRIVTP3 115.00] CKT 1 | 3.4941 | FAIL | 48.4859 | PASS | 48385.8676 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539749 [N-CIMRN3 115.00] CKT 1 | 3.4826 | FAIL | 48.4236 | PASS | 48323.5847 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 539780 [CIM PLT1 13.8.00] CKT 1 | 3.4939 | FAIL | 48.6108 | PASS | 48510.8008 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 539654 [CIM-PLT3 115.00] TO BUS 762471 [GEN-2018-009 115.00] CKT 1 | 3.4959 | FAIL | 48.4598 | PASS | 48359.7892 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 772280 [G23-015-TAP 345.00] TO BUS 772281 [GEN-2023-015 345.00] CKT 1 | 3.4954 | FAIL | 48.466 | PASS | 48366.0293 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 778320 [G24-045-TAP 230.00] TO BUS 777091 [GEN-2024-046 230.00] CKT 1 | 3.4973 | FAIL | 48.4618 | PASS | 48361.8172 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 778320 [G24-045-TAP 230.00] TO BUS 778321 [GEN-2024-045 230.00] CKT 1 | 3.4973 | FAIL | 48.4618 | PASS | 48361.8172 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 784950 [G24-266_TAP 345.00] TO BUS 784951 [GEN-2024-266 345.00] CKT 1 | 3.5167 | FAIL | 48.4652 | PASS | 48365.1905 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516059 [BECKHAM7 345.00] TO BUS 515458 [BORDER 7 345.00] CKT 1 & 2 | 3.4622 | FAIL | 48.5462 | PASS | 48446.1696 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 516106 [BOBCAT 7 345.00] TO BUS 515375 [WWRDEHV7 345.00] CKT 1 & 2 | 2.3421 | FAIL | 66.9998 | PASS | 66899.835 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523093 [HITCHLAND 3 115.00] TO BUS 523084 [SOONER 3 115.00] CKT 1 & 2 | 3.4911 | FAIL | 49.0136 | PASS | 48913.6015 | 133.437 | 133.437
GEN-2026-PR4 PSIS | 05 SOUTHWEST | 29WP | GEN-2026-PR4 | 345kV Bus at SPS Hitchland Substation, Spearman, TX | OPEN LINE FROM BUS 523154 [OCHILTREE 3 115.00] TO BUS 523158 [PERRYTON 3 115.00] CKT 1 & 2 | 3.4926 | FAIL | 48.5664 | PASS | 48466.3897 | 133.437 | 133.437

## WSCR
* WSCR is not applicable to this study.