## Executive Summary
Executive Summary: Group 04 GEN-2026-PR5 Priority Process Study
Interconnection Customer GEN-2026-PR5 (Group 04) has requested a Limited Operation or Interim Availability Interconnection Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR5 generation for total of:
60.4 MW
The minimum cost of interconnecting GEN-2026-PR5 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR5 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 05/29/2026
Costs for Battery Requests were allocated using the 29SP (summer peak) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4617100% | SPP | Draft Report (Missing full SCRCCT data to complete analysis. SPP will repost report once the data has been received.)

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | 0 | 0 | 0 | 0 | 0 | 0 | 60.4 | 60.4 | -37.075 | ER | OG&E | Woodring 345 kV Substation | None
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | None
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | None
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | None
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | None
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 60.4 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 for System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | 60.4 | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 60.4 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 for System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | 60.4 | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 60.4 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 for System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 60.4 | N/A
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 60.4 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 for System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 60.4 | N/A
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 60.4 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 for System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | 60.4 | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 60.4 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 for System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | 60.4 | N/A | N/A | N/A | N/A | 60.4 | 60.4
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 60.4 | 60.4 | None |  | N/A | N/A | N/A | 60.4 | N/A | N/A | N/A | N/A | N/A | 60.4
GEN-2026-PR5 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 60.4 | 60.4 | None | None | N/A | N/A | N/A | 60.4 | N/A | N/A | N/A | N/A | N/A | 60.4

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR5 PSIS | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29SP | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 830 | 830 | 98.74 | 100.44 |  |  |  | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR5 PSIS | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP, 29SP | System Intact | 829 | 829 | 111.55 | 111.88 |  |  |  | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
04ALL | GEN-2026-PR5 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 125.61 | 126.29 |  |  |  | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
04ALL | GEN-2026-PR5 PSIS | ERIS | Thermal | None | 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 26SP | System Intact | 830 | 830 | 107.16 | 108.61 |  |  |  | Viola 345-765 kV New Transformer ckt1
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 26SP, 29SP | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 830 | 830 | 138.49 | 140.1 |  |  |  | Anthem - Viola 765 kV New Line
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 26SP, 29SP | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 830 | 830 | 150.26 | 151.89 |  |  |  | Woodward - Viola 765 kV New Line
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 116.98 | 118.44 |  |  |  | Minco 345-765 kV New Transformer ckt2
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Thermal | None | 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR5 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR5 | GEN-2026-PR5 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 2390 MVA | 0 | 0% | 81488001.7662 | 0.08937
GEN-2026-PR5 | GEN-2026-PR5 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1 | Contingent | Rebuild the existing NEOSHO 7 to G24-240-TAP 345 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | 0 | 0% | 93984002.037 | 0.03136
GEN-2026-PR5 | GEN-2026-PR5 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | Contingent | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1050 MVA* * The minimum required rating has been adjusted to ensure resolution of similar issues identified for the GEN-2026-PR5 and GEN-2026-PR6 projects. | 0 | 0% | 45914000 | 0.21938
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Viola 345-765 kV New Transformer ckt1 | Contingent | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 1 with a rating of 1650 MVA | 0 | 0% | 3304340617.4944 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Viola 345-765 kV New Transformer ckt2 | Contingent | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 2 with a rating of 1650 MVA | 0 | 0% | 3304340617.4944 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Viola 345-765 kV New Transformer ckt3 | Contingent | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 3 with a rating of 1650 MVA | 0 | 0% | 3304340617.4944 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Anthem - Viola 765 kV New Line | Contingent | Build a new ANTHEM9 to VIOLA9 765 kV line 1 (166 miles) to a standard rating of 5300 MVA | 0 | 0% | 3304340617.4944 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Woodward - Viola 765 kV New Line | Contingent | Build a new WWARD9 to VIOLA9 765 kV line 1 (140.8 miles) to a standard rating of 5300 MVA | 0 | 0% | 3304340617.4944 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Minco - Seminole 765 kV New Line ckt1 | Contingent | Build a new MINCO 9 to SEMINOLE9 765 kV line 1 (92.2 miles) to a standard rating of 5300 MVA | 0 | 0% | 2554639896.7884 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Minco 345-765 kV New Transformer ckt1 | Contingent | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 1 with a rating of 1650 MVA | 0 | 0% | 2554639896.7884 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Minco 345-765 kV New Transformer ckt2 | Contingent | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 2 with a rating of 1650 MVA | 0 | 0% | 2554639896.7884 | N/A
GEN-2026-PR5 | GEN-2026-PR5 PSIS | 04 SOUTHEAST | TBD | ERIS | Woodring 345kV Substation GEN-2026-PR5 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR5 (60.4/Storage), into Woodring 345kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR5 | GEN-2026-PR5 PSIS | 04 SOUTHEAST | TBD | ERIS | Woodring 345kV Substation GEN-2026-PR5 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR5 (60.4/Storage), into Woodring 345kV Substation | TBD | 100% | TBD | 1
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR5 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 2390 MVA | WERE | TBD | 81488001.7662
Contingent | GEN-2026-PR5 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1 | TBD | Rebuild the existing NEOSHO 7 to G24-240-TAP 345 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | WERE/AEPW | TBD | 93984002.037
Contingent | GEN-2026-PR5 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR3 PSIS | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1050 MVA* * The minimum required rating has been adjusted to ensure resolution of similar issues identified for the GEN-2026-PR5 and GEN-2026-PR6 projects. | OKGE/WERE | 36 | 45914000
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Viola 345-765 kV New Transformer ckt1 | TBD | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 1 with a rating of 1650 MVA | N/A | 4821400% | 3304340617.4944
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Viola 345-765 kV New Transformer ckt2 | TBD | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 2 with a rating of 1650 MVA | N/A | 4821400% | 3304340617.4944
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Viola 345-765 kV New Transformer ckt3 | TBD | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 3 with a rating of 1650 MVA | N/A | 4821400% | 3304340617.4944
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Anthem - Viola 765 kV New Line | TBD | Build a new ANTHEM9 to VIOLA9 765 kV line 1 (166 miles) to a standard rating of 5300 MVA | N/A | 4821400% | 3304340617.4944
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Woodward - Viola 765 kV New Line | TBD | Build a new WWARD9 to VIOLA9 765 kV line 1 (140.8 miles) to a standard rating of 5300 MVA | N/A | 4821400% | 3304340617.4944
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Minco - Seminole 765 kV New Line ckt1 | TBD | Build a new MINCO 9 to SEMINOLE9 765 kV line 1 (92.2 miles) to a standard rating of 5300 MVA | N/A | 4821400% | 2554639896.7884
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Minco 345-765 kV New Transformer ckt1 | TBD | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 1 with a rating of 1650 MVA | N/A | 4821400% | 2554639896.7884
Contingent | GEN-2026-PR5 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Minco 345-765 kV New Transformer ckt2 | TBD | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 2 with a rating of 1650 MVA | N/A | 4821400% | 2554639896.7884
Interconnection | GEN-2026-PR5 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR5 PSIS | ERIS | Woodring 345kV Substation GEN-2026-PR5 Interconnection (TOIF) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR5 (60.4/Storage), into Woodring 345kV Substation | OGE | TBD | TBD
Interconnection | GEN-2026-PR5 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR5 PSIS | ERIS | Woodring 345kV Substation GEN-2026-PR5 Interconnection (Non-Shared NU) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR5 (60.4/Storage), into Woodring 345kV Substation | OGE | TBD | TBD
24407008781.6403

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV New Line | Build a new WWARD9 to VIOLA9 765 kV line 1 (140.8 miles) to a standard rating of 5300 MVA | 2025 ITP | Yes | N/A | -0.04563 | 4821400% | 3304340617.4944
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504296 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem - Viola 765 kV New Line | Build a new ANTHEM9 to VIOLA9 765 kV line 1 (166 miles) to a standard rating of 5300 MVA | 2025 ITP | Yes | N/A | -0.04922 | 4821400% | 3304340617.4944
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504304 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345-765 kV New Transformer ckt1 | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 1 with a rating of 1650 MVA | 2025 ITP | Yes | N/A | -0.03162 | 4821400% | 3304340617.4944
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504308 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345-765 kV New Transformer ckt2 | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 2 with a rating of 1650 MVA | 2025 ITP | Yes | N/A | -0.03162 | 4821400% | 3304340617.4944
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504311 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 345-765 kV New Transformer ckt3 | Build a new VIOLA9 to VIOLA 7 765-345 kV transformer 3 with a rating of 1650 MVA | 2025 ITP | Yes | N/A | -0.03162 | 4821400% | 3304340617.4944
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504237 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward - Potter Co 765 kV Ckt 1 New Line | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 2025 ITP | Yes | N/A | 0.03711 | 4821400% | 1348925000
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504194 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345-765 kV New Transformer ckt1 | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 1 with a rating of 1650 MVA | 2025 ITP | Yes | N/A | 0.03685 | 4821400% | 2554639896.7884
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504198 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345-765 kV New Transformer ckt2 | Build a new MINCO 9 to MINCO 7 765-345 kV transformer 2 with a rating of 1650 MVA | 2025 ITP | Yes | N/A | 0.03685 | 4821400% | 2554639896.7884
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 504167 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco - Seminole 765 kV New Line ckt1 | Build a new MINCO 9 to SEMINOLE9 765 kV line 1 (92.2 miles) to a standard rating of 5300 MVA | 2025 ITP | Yes | N/A | -0.05002 | 4821400% | 2554639896.7884
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 503353 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Lawton Eastside - Seminole 765 kV New Line Lawton Eastside - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Lawton Eastside 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Lawton Eastside 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.2-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | -0.07266 | 4780500% | 8868059754.3097
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 503392 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Lawton Eastside - Seminole 765 kV New Line Lawton Eastside - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Lawton Eastside 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Lawton Eastside 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Southwest Shreveport 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Southwest Shreveport | 2025 ITP | Yes | N/A | -0.03643 | 4780500% | 8868059754.3097
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | 503396 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Lawton Eastside - Seminole 765 kV New Line Lawton Eastside - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Lawton Eastside 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Lawton Eastside 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Southwest Shreveport 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Southwest Shreveport | 2025 ITP | Yes | N/A | -0.03643 | 4780500% | 8868059754.3097
GEN-2026-PR5 | 04 SOUTHEAST | ER | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | N/A | -0.03069 | 4565800% | 647852
GEN-2026-PR5 | 04 SOUTHEAST | ER | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | N/A | -0.03217
GEN-2026-PR5 | 04 SOUTHEAST | ER | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | N/A | 0.03461 | TBD (36-month lead time) | $ 96,000,000.00 | $ 96,000,000.00

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR5 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00014 | -0.008456 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00412 | -0.24885 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00186 | -0.11234 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00186 | -0.11234 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00098 | -0.059192 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00606 | 0.36602 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.00519 | 0.31348 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -0.00023 | -0.013892 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -0.00023 | -0.013892 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00084 | 0.050736 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00082 | 0.049528 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00255 | 0.15402 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00329 | 0.19872 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00059 | -0.035636 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00059 | -0.035636 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00778 | -0.46991 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.00087 | -0.052548 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00025 | 0.0151 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00025 | 0.0151 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00031 | 0.018724 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00048 | 0.028992 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00021 | 0.012684 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00023 | 0.013892 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.000604 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.000604 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.000604 | No
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.000604 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR5 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR5 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.0892 | 115.19 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR5 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03123 | 103.89 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
Thermal | GEN-2026-PR5 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.08654 | 126.29 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR5 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03102 | 111.88 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
Thermal | GEN-2026-PR5 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22918 | 100.44 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Non-Converged | GEN-2026-PR5 PSIS | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR5 PSIS | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR5 PSIS | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR5 PSIS | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Viola 345-765 kV New Transformer ckt3
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Anthem - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Woodward - Viola 765 kV New Line
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco - Seminole 765 kV New Line ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt1
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.61 | System Intact | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.18945 | 108.56 | System Intact | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.19035 | 118.44 | System Intact | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 120.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 151.89 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 117.21 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 148.19 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.67 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 115.65 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.2 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 146.17 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 114.39 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 144.58 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 113.33 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 143.24 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 112.53 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 142.22 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 140.1 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 139.98 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 108 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.95 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.52 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 136.46 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.33 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 136.22 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.2073 | 107.15 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2073 | 135.41 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.33 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.34 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7388:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 134.22 | p42:345:okge:sb_opky7308:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.78 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 132.66 | p12:345:okge:bkrbkr3572:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.42 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 1050 | 1050 | 0.26362 | 103.8 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 131.3 | p42:345:okge:sb_rard7311:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26362 | 131.21 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.5 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 130.38 | p42:345:okge:sb_rard7381:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.89 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.82 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.77 | p42:345:okge:sb_rard7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 124.71 | p42:345:okge:sb_rard7313:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.8 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.20634 | 123.69 | p12:345:okge:bkrbkr3571:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.47 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR5 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.26344 | 120.37 | p42:345:okge:sb_soer7383:::ehv: | TDF Impact | Minco 345-765 kV New Transformer ckt2
Non-Converged | GEN-2026-PR5 PSIS CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR5 PSIS CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR5 PSIS CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR5 PSIS CF | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR5 PSIS | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR5 PSIS | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR5 PSIS | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR5 PSIS CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR5 PSIS CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR5 PSIS CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 3 cycles and remove reclosing solve the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-239GEN1 (784144), G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OTOETAP4 138.00 (515978) 138 kV Bus a. Apply fault at the OTOETAP4 138.00 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.3. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.5. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.6. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G24-056-TAP (778650) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.3. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip SUNDCG (516022, 516076) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduce the simulation time step to 1/8 cycle solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault, and the same issue is observed in the base case. After reducing the fault clearing time to 4 cycles, the simulation completed successfully, and the protection relay tripped the PRSMNG11 (515955) unit. | Reduce clearing time to 4 cycles and disabling protection relay solve the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER2G (514806). The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-239GEN1 (784144), G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650), REDBDPLNW0 (511974) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029GEN1 (762650) and G21-088-GEN1 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduce the simulation time step to 1/8 cycle solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in G10-055 (560391). The issue is observed in base case. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduce the simulation time step to 1/8 cycle solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), SOONER2G (514806) and G17-141 (760412) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. After reducing the fault clearing time to 4 cycles, the simulation completed successfully, and the protection relay tripped the PRSMNG11 (515955) unit. | Reduce clearing time to 4 cycles and disabling protection relay solve the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduce the simulation time step to 1/8 cycle solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and OMCDLEC1 (529201) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and OMCDLEC1 (529201) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.7. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.9. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on BRECKNR4 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.5. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.6. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.7. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.8. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.7. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.8. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.9. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.10. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.11. PINE ST4 (514829) 138.0 kV to Trip Bus # b.12. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.13. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.14. KINZE 4 (515008) 138.0 kV to Trip Bus # b.15. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.16. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.17. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.18. WHITESB4 (515467) 138.0 kV to Trip Bus # b.19. MARSHAL4 (521006) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | Group4_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active and reactive power outputs of G19-045 (763722). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650), G24-239 (784144) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OTOETAP4 138.00 (515978) 138 kV Bus a. Apply fault at the OTOETAP4 138.00 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.3. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.5. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.6. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G24-056-TAP (778650) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory power output is observed in G17-141 (760412). This behavior was also observed in the base case. | Reduce the simulation time step to 1/8 cycle solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.3. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip SUNDCG (516022, 516076) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-029 (762650) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault, and the same behavior is observed in the base case. After disabling reclosing and reducing the fault clearing time to 2 cycles, an oscillatory response is seen in the output power of G24-334 (786994, 786997), WCGS (532751), and LAC (542955) units. This issue is also present in the base case, and the CQ unit does not appear to have any impact on it. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650), REDBDPLNW0 (511974) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650), G24-239GEN1 (784144), REDBDPLNW0 (511974), G24-239GEN1 (784144) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650) G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650), REDBDPLNW0 (511974) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-029 (762650), REDBDPLNW0 (511974) and G21-088 (766112) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in G10-055 (560391). The issue is observed in base case. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips G18-029 (762650) unit. After disabling protection relay, oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER2G (514806) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-135 (781024, 781027) and G24-134 (780994, 780997) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power outputs of G18-115 (763321, 763324). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips G22-145 (769884) unit. After disabling protection relay, oscillatory response observed in the active power outputs of G24-334 (786994, 786997), LAC G1 (542955) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), LAC G1 (542955) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), LAC G1 (542955) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.7. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.9. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), LAC G1 (542955) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on BRECKNR4 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-145 (769884) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.5. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.6. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.7. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.8. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), LAC G1 (542955) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.7. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.8. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.9. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.10. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.11. PINE ST4 (514829) 138.0 kV to Trip Bus # b.12. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.13. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.14. KINZE 4 (515008) 138.0 kV to Trip Bus # b.15. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.16. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.17. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.18. WHITESB4 (515467) 138.0 kV to Trip Bus # b.19. MARSHAL4 (521006) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | Group4_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G22-111 (769204) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and SOONER (514806, 514805) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OTOETAP4 138.00 (515978) 138 kV Bus a. Apply fault at the OTOETAP4 138.00 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.3. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.5. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.6. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G24-056-TAP (778650) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.3. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-135 (781024, 781027) and G24-134 (780994, 780997) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-135 (781024, 781027) and G24-134 (780994, 780997) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-135 (781024, 781027) and G24-134 (780994, 780997) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.7. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.9. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on BRECKNR4 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.5. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.6. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.7. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.8. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.7. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.8. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.9. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.10. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.11. PINE ST4 (514829) 138.0 kV to Trip Bus # b.12. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.13. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.14. KINZE 4 (515008) 138.0 kV to Trip Bus # b.15. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.16. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.17. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.18. WHITESB4 (515467) 138.0 kV to Trip Bus # b.19. MARSHAL4 (521006) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | Group4_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ENIDINT4 138.00 (515383) 138 kV Bus a. Apply fault at the ENIDINT4 138.00 (515383) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 (514769) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 b.3. ENIDINT4 (515383) 138.0 kV to ENIDIND4 (515737) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OTOETAP4 138.00 (515978) 138 kV Bus a. Apply fault at the OTOETAP4 138.00 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.3. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.5. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.6. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G24-056-TAP (778650) 138.0 kV to MORRISN4 (515006) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on VANCE 2 69.000 (514718) 69 kV Bus a. Apply fault at the VANCE 2 69.000 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on CHSTNTT2 69.000 (515456) 69 kV Bus a. Apply fault at the CHSTNTT2 69.000 (515456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEMLOCK2 (514724) 69.0 kV to HEMLKTP2 (514725) 69.0 kV Transmission Circuit #1 b.2. HEMLKTP2 (514725) 69.0 kV to NE ENID2 (514732) 69.0 kV Transmission Circuit #1 b.3. HEMLKTP2 (514725) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.4. CHSTNUT2 (514726) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on ENID 2 69.000 (514727) 69 kV Bus a. Apply fault at the ENID 2 69.000 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GLENWD 4 138.00 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 138.00 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 (514734) 138.0 kV to NE ENID4 (514769) 138.0 kV Transmission Circuit #1 b.2. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CLEOPLT4 138.00 (515562) 138 kV Bus a. Apply fault at the CLEOPLT4 138.00 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.2. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.3. MENOTAP4 (514789) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 b.4. CLEO PL4 (515553) 138.0 kV to CLEOPLT4 (515562) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on PINE ST4 138.00 (514829) 138 kV Bus a. Apply fault at the PINE ST4 138.00 (514829) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.2. PINE ST4 (514829) 138.0 kV to FITZGRD4 (514830) 138.0 kV Transmission Circuit #1 b.3. FITZGRD4 (514830) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.5. KINZE 4 (515008) 138.0 kV to COYLE 4 (516212) 138.0 kV Transmission Circuit #1 b.6. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on IMO 4 138.00 (514790) 138 kV Bus a. Apply fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on CLEVETP2 69.000 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 69.000 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on GARBER 4 138.00 (520461) 138 kV Bus a. Apply fault at the GARBER 4 138.00 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 (520461) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip GOODWELL (523170, 523171) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.3. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.2. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRECKNR4 138.00 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 138.00 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to ENIDINT4 (515383) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on CTNWOOD4 138.00 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 138.00 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.2. CTNWOOD4 (514827) 138.0 kV to PINE ST4 (514829) 138.0 kV Transmission Circuit #1 b.3. CTNWOOD4 (514827) 138.0 kV to ARCADIA4 (514907) 138.0 kV Transmission Circuit #1 b.4. CTNWOOD4 (514827) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. CTNWOOD4 (514827) 138.0 kV to CRESENT4 (515377) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on IMO 4 138.00 (514790) 138 kV Bus a. Apply Fault at the IMO 4 138.00 (514790) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IMO 2 (514721) 69.0 kV to CLEVETP2 (514722) 69.0 kV Transmission Circuit #1 b.2. IMO 2 (514721) 69.0 kV to GOLTYTP2 (515493) 69.0 kV Transmission Circuit #1 b.3. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.4. GLENWD 4 (514734) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.5. MENOTAP4 (514789) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.6. IMO 2 (514721) 69.0 kV to IMO 4 (514790) 138.0 kV to IMO 1 (515788) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to ARMFTWD4 (515694) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on PLNSMEN4 138.00 (515641) 138 kV Bus a. Apply Fault at the PLNSMEN4 138.00 (515641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 b.2. BRECKNR4 (514815) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. VANCE 2 (514718) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.4. CLEVETP2 (514722) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #1 b.5. ENID 2 (514727) 69.0 kV to SO4TH 2 (514730) 69.0 kV Transmission Circuit #2 b.6. SO4TH 2 (514730) 69.0 kV to CHSTNTT2 (515456) 69.0 kV Transmission Circuit #1 b.7. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.8. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.9. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.3. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OTTER 4 138.00 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 138.00 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply Fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WAUKOMI4 138.00 (514710) 138 kV Bus a. Apply Fault at the WAUKOMI4 138.00 (514710) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to WAUKOMI4 (514710) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FAIRMON4 138.00 (514712) 138 kV Bus a. Apply Fault at the FAIRMON4 138.00 (514712) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRMON4 (514712) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. FAIRMON4 (514712) 138.0 kV to PLNSMEN4 (515641) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply Fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WRVALLY4 (514713) 138.0 kV to OTTER 4 (514708) 138.0 kV Transmission Circuit #1 b.2. WRVALLY4 (514713) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG4 (514714) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SO4TH 4 138.00 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 138.00 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to FRMNTAP4 (514709) 138.0 kV Transmission Circuit #1 b.2. SO4TH 4 (514731) 138.0 kV to SO4TH 2 (514730) 69.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply Fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHL 4 (514733) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HUNTERS7 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on OTTER 4 (514708) 138 kV Bus a. Apply Fault at the OTTER 4 (514708) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDNGTN7 (515875) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on BRECKNR4 (514815) 138 kV Bus a. Apply Fault at the BRECKNR4 (514815) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRECKNR4 (514815) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on WAUKOTP4 (514711) 138 kV Bus a. Apply Fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.5. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.6. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.7. WAUKOTP4 (514711) 138.0 kV to Trip Bus # b.8. FRMNTAP4 (514709) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to Trip Bus # b.5. FRNTWD11 (515689) 34.5 kV to Trip Bus # b.6. FRNTWDC1 (515690) 34.5 kV to Trip Bus # b.7. FRNTWDG1 (515691) 0.6 kV to Trip Bus # b.8. FRNTWDT1 (515692) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to UNVRSTY4 (515181) 138.0 kV Transmission Circuit #1 b.2. KETCH 4 (514834) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.3. CRESENT4 (515377) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.4. KINZE 4 (515008) 138.0 kV to KINZEGR4 (512710) 138.0 kV Transmission Circuit #1 b.5. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.6. ARCADIA4 (514907) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.7. NORTWST4 (514879) 138.0 kV to KETCHTP4 (514828) 138.0 kV Transmission Circuit #1 b.8. MARSHL 4 (514733) 138.0 kV to Trip Bus # b.9. CTNWOOD4 (514827) 138.0 kV to Trip Bus # b.10. KETCHTP4 (514828) 138.0 kV to Trip Bus # b.11. PINE ST4 (514829) 138.0 kV to Trip Bus # b.12. FITZGRD4 (514830) 138.0 kV to Trip Bus # b.13. WATRLOO4 (514831) 138.0 kV to Trip Bus # b.14. KINZE 4 (515008) 138.0 kV to Trip Bus # b.15. UNVRSTY4 (515181) 138.0 kV to Trip Bus # b.16. LBRTYLK4 (515373) 138.0 kV to Trip Bus # b.17. MITCHSB4 (515466) 138.0 kV to Trip Bus # b.18. WHITESB4 (515467) 138.0 kV to Trip Bus # b.19. MARSHAL4 (521006) 138.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | Group4_P4_OKGE_FAULT_005 | Single Phase Fault with Stuck Breaker on SO4TH 4 (514731) 138 kV Bus a. Apply Fault at the SO4TH 4 (514731) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SO4TH 4 (514731) 138.0 kV to IMO 4 (514790) 138.0 kV Transmission Circuit #1 b.2. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 b.4. SO4TH 4 (514731) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.5. SO4TH 2 (514730) 69.0 kV to SO4TH 4 (514731) 138.0 kV to SO4TH 1 (515758) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR5 PSIS CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR5 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 25.3882 | 25.3891 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 301011 | 4REDRCK | 138 | 16.705 | 16.7062 | 0.0012
GEN-2026-PR5 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 21.6482 | 21.6487 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.5006 | 7.5007 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 509741 | CARSN-N4 | 138 | 9.731 | 9.731 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 509743 | DENVR-E4 | 138 | 8.7584 | 8.7584 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 509746 | DENVTAP4 | 138 | 10.3691 | 10.3692 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.2426 | 23.244 | 0.0014
GEN-2026-PR5 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 35.1457 | 35.1466 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.8601 | 8.8602 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 509822 | W.ED.-E4 | 138 | 8.6651 | 8.6651 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 509832 | W.ED.-W4 | 138 | 12.1071 | 12.1072 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 32.1264 | 32.1271 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 30.8072 | 30.8076 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 26.3883 | 26.3902 | 0.0019
GEN-2026-PR5 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.5443 | 12.5444 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 24.1405 | 24.1413 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 45.7196 | 45.7211 | 0.0015
GEN-2026-PR5 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 17.3702 | 17.3707 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.5665 | 15.5666 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 7.0395 | 7.0395 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6771 | 10.6772 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 7.0803 | 7.0803 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511592 | SEVEN7A_HV | 345 | 10.1806 | 10.1807 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511599 | SEVEN7AB2 | 345 | 10.1806 | 10.1807 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511608 | SEVEN7AB3 | 345 | 10.1806 | 10.1807 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511726 | ZONE-5 SUB | 345 | 7.0303 | 7.0303 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511877 | G16133G16146 | 345 | 34.8713 | 34.8721 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 511878 | G16133_765TN | 765 | 9.4698 | 9.4699 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511879 | G16133_765R1 | 765 | 9.4698 | 9.4699 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511880 | G16133_765R2 | 765 | 4.5934 | 4.5934 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511881 | G16133_765R3 | 765 | 3.6602 | 3.6603 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511882 | G16133_765CS | 765 | 3.6602 | 3.6603 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 511883 | G16133_345CS | 345 | 7.9584 | 7.9584 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511884 | ZONE-1 SUB | 345 | 7.0633 | 7.0633 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511893 | ZONE-2 SUB | 345 | 7.0451 | 7.0451 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511902 | ZONE-3 SUB | 345 | 6.9847 | 6.9847 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511911 | ZONE-4 SUB | 345 | 6.5214 | 6.5214 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 511929 | ZONE-6 SUB | 345 | 7.071 | 7.071 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 20.4425 | 20.4471 | 0.0046
GEN-2026-PR5 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 25.3867 | 25.3877 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 514642 | BRCKWND4 | 138 | 8.1962 | 8.1981 | 0.0019
GEN-2026-PR5 | 04 SOUTHEAST | 514701 | BUNCHCK4 | 138 | 6.9756 | 6.9764 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 21.3627 | 21.3647 | 0.002
GEN-2026-PR5 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.7106 | 4.7106 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 12.0096 | 12.0107 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.6873 | 11.6882 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 10.5389 | 10.5411 | 0.0022
GEN-2026-PR5 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 19.4061 | 19.4201 | 0.014
GEN-2026-PR5 | 04 SOUTHEAST | 514710 | WAUKOMI4 | 138 | 11.0237 | 11.0267 | 0.003
GEN-2026-PR5 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 16.7395 | 16.7486 | 0.0091
GEN-2026-PR5 | 04 SOUTHEAST | 514712 | FAIRMON4 | 138 | 14.9449 | 14.9523 | 0.0074
GEN-2026-PR5 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 9.3285 | 9.3295 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 20.8292 | 20.8459 | 0.0167
GEN-2026-PR5 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 20.3509 | 20.4839 | 0.133
GEN-2026-PR5 | 04 SOUTHEAST | 514718 | VANCE 2 | 69 | 7.1205 | 7.1212 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 514720 | GOLTRY 2 | 69 | 3.7652 | 3.7654 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 514721 | IMO 2 | 69 | 12.3955 | 12.3976 | 0.0021
GEN-2026-PR5 | 04 SOUTHEAST | 514722 | CLEVETP2 | 69 | 11.9224 | 11.9244 | 0.002
GEN-2026-PR5 | 04 SOUTHEAST | 514723 | CLEVLND2 | 69 | 9.4723 | 9.4736 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 514724 | HEMLOCK2 | 69 | 7.9562 | 7.9571 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 514726 | CHSTNUT2 | 69 | 11.3998 | 11.4017 | 0.0019
GEN-2026-PR5 | 04 SOUTHEAST | 514727 | ENID 2 | 69 | 10.9044 | 10.9061 | 0.0017
GEN-2026-PR5 | 04 SOUTHEAST | 514730 | SO4TH 2 | 69 | 13.5455 | 13.5481 | 0.0026
GEN-2026-PR5 | 04 SOUTHEAST | 514731 | SO4TH 4 | 138 | 16.3574 | 16.3659 | 0.0085
GEN-2026-PR5 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.3819 | 8.3835 | 0.0016
GEN-2026-PR5 | 04 SOUTHEAST | 514734 | GLENWD 4 | 138 | 10.8814 | 10.8848 | 0.0034
GEN-2026-PR5 | 04 SOUTHEAST | 514737 | OTOE 4 | 138 | 17.0422 | 17.0435 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 18.3749 | 18.3765 | 0.0016
GEN-2026-PR5 | 04 SOUTHEAST | 514766 | ORLANDO2 | 69 | 1.807 | 1.807 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 514768 | WF KAY 2 | 69 | 3.3395 | 3.3396 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 514774 | HENESEY4 | 138 | 9.6288 | 9.6299 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 514789 | MENOTAP4 | 138 | 7.4431 | 7.4442 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 514790 | IMO 4 | 138 | 12.6166 | 12.6211 | 0.0045
GEN-2026-PR5 | 04 SOUTHEAST | 514797 | BRONRD 2 | 69 | 1.672 | 1.672 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 21.4382 | 21.4402 | 0.002
GEN-2026-PR5 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.826 | 11.8267 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 514800 | BRRDTP 2 | 69 | 1.9585 | 1.9585 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 26.6723 | 26.6744 | 0.0021
GEN-2026-PR5 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 32.8235 | 32.8281 | 0.0046
GEN-2026-PR5 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 31.7162 | 31.7377 | 0.0215
GEN-2026-PR5 | 04 SOUTHEAST | 514815 | BRECKNR4 | 138 | 14.7535 | 14.7602 | 0.0067
GEN-2026-PR5 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.9605 | 17.961 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.6033 | 19.6038 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 13.984 | 13.9855 | 0.0015
GEN-2026-PR5 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.7931 | 18.7945 | 0.0014
GEN-2026-PR5 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 30.3405 | 30.3424 | 0.0019
GEN-2026-PR5 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.818 | 12.8186 | 0.0006
GEN-2026-PR5 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.5485 | 9.5488 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.4707 | 15.4714 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 35.1485 | 35.151 | 0.0025
GEN-2026-PR5 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.925 | 28.9264 | 0.0014
GEN-2026-PR5 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 24.5682 | 24.5695 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 35.0562 | 35.0587 | 0.0025
GEN-2026-PR5 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 51.0577 | 51.0637 | 0.006
GEN-2026-PR5 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 39.9091 | 39.9213 | 0.0122
GEN-2026-PR5 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 28.1926 | 28.1984 | 0.0058
GEN-2026-PR5 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 31.0911 | 31.0923 | 0.0012
GEN-2026-PR5 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.3938 | 20.3943 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 49.2256 | 49.2296 | 0.004
GEN-2026-PR5 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 43.5586 | 43.572 | 0.0134
GEN-2026-PR5 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 22.0368 | 22.0373 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 44.3385 | 44.3416 | 0.0031
GEN-2026-PR5 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 34.9332 | 34.9374 | 0.0042
GEN-2026-PR5 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 35.4859 | 35.49 | 0.0041
GEN-2026-PR5 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 30.7807 | 30.7826 | 0.0019
GEN-2026-PR5 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 14.5812 | 14.5821 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.7054 | 14.706 | 0.0006
GEN-2026-PR5 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 34.7928 | 34.7938 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.284 | 3.284 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.914 | 14.9147 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 23.7503 | 23.7516 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.4656 | 26.4662 | 0.0006
GEN-2026-PR5 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.0192 | 10.0197 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 515383 | ENIDINT4 | 138 | 13.7957 | 13.8015 | 0.0058
GEN-2026-PR5 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.3136 | 9.3137 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 9.9973 | 9.9974 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 515400 | DMANCRK4 | 138 | 8.5128 | 8.5131 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 19.1668 | 19.1688 | 0.002
GEN-2026-PR5 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 14.5783 | 14.5793 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 515426 | RDRUNNR4 | 138 | 8.7508 | 8.7519 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 515427 | RCKFALL4 | 138 | 6.3567 | 6.3572 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 26.5539 | 26.556 | 0.0021
GEN-2026-PR5 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.6092 | 14.6101 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 13.0342 | 13.0352 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 515456 | CHSTNTT2 | 69 | 11.6752 | 11.6772 | 0.002
GEN-2026-PR5 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 42.1488 | 42.1515 | 0.0027
GEN-2026-PR5 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.3427 | 22.3434 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.6612 | 13.6962 | 0.035
GEN-2026-PR5 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.6379 | 13.6728 | 0.0349
GEN-2026-PR5 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 43.803 | 43.8273 | 0.0243
GEN-2026-PR5 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.6714 | 12.6871 | 0.0157
GEN-2026-PR5 | 04 SOUTHEAST | 515544 | RENFROW4 | 138 | 14.8906 | 14.8965 | 0.0059
GEN-2026-PR5 | 04 SOUTHEAST | 515546 | GRANTCO4 | 138 | 6.7279 | 6.729 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 515547 | GRANTCO2 | 69 | 7.7878 | 7.7885 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.5936 | 15.5942 | 0.0006
GEN-2026-PR5 | 04 SOUTHEAST | 515553 | CLEO PL4 | 138 | 5.6377 | 5.638 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 515569 | MDFRDTP4 | 138 | 11.923 | 11.9264 | 0.0034
GEN-2026-PR5 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 16.4162 | 16.4187 | 0.0025
GEN-2026-PR5 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 9.0464 | 9.0468 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.6908 | 14.6919 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 11.5512 | 11.5521 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 515605 | GEN-2021-043 | 115 | 12.8914 | 12.8925 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 515610 | GEN-2021-048 | 115 | 18.2963 | 18.2986 | 0.0023
GEN-2026-PR5 | 04 SOUTHEAST | 515621 | GEN-2021-108 | 345 | 14.0255 | 14.0271 | 0.0016
GEN-2026-PR5 | 04 SOUTHEAST | 515641 | PLNSMEN4 | 138 | 14.7803 | 14.7874 | 0.0071
GEN-2026-PR5 | 04 SOUTHEAST | 515646 | GRNTWD 7 | 345 | 11.0977 | 11.1096 | 0.0119
GEN-2026-PR5 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 11.3679 | 11.3681 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 13.5851 | 13.5868 | 0.0017
GEN-2026-PR5 | 04 SOUTHEAST | 515694 | ARMFTWD4 | 138 | 10.5055 | 10.5078 | 0.0023
GEN-2026-PR5 | 04 SOUTHEAST | 515707 | HSL13 4 | 138 | 40.5209 | 40.522 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 515737 | ENIDIND4 | 138 | 10.3474 | 10.3507 | 0.0033
GEN-2026-PR5 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 23.3267 | 23.3273 | 0.0006
GEN-2026-PR5 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 10.7 | 10.7002 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 16.3451 | 16.3459 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.8783 | 6.8783 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 19.0576 | 19.1021 | 0.0445
GEN-2026-PR5 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 19.0527 | 19.0971 | 0.0444
GEN-2026-PR5 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.7044 | 13.708 | 0.0036
GEN-2026-PR5 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.7192 | 10.7195 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 515947 | CONTCBN2 | 69 | 16.9945 | 16.9949 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 12.8556 | 12.8559 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 515957 | GRANRYT2 | 69 | 6.0162 | 6.0167 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 515958 | GRANARY2 | 69 | 5.8589 | 5.8594 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 515960 | BULFOOT4 | 138 | 9.4771 | 9.478 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 14.7405 | 14.741 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 515974 | GEN-2015-066 | 345 | 17.6933 | 17.6988 | 0.0055
GEN-2026-PR5 | 04 SOUTHEAST | 515975 | G15-066T | 345 | 20.5747 | 20.5823 | 0.0076
GEN-2026-PR5 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 17.0898 | 17.0911 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.6936 | 7.6937 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 5.2065 | 5.2132 | 0.0067
GEN-2026-PR5 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.4509 | 17.4933 | 0.0424
GEN-2026-PR5 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.3854 | 17.4276 | 0.0422
GEN-2026-PR5 | 04 SOUTHEAST | 516036 | TRAV3WD7 | 345 | 7.492 | 7.4924 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 516045 | TRAV2WD7 | 345 | 5.9796 | 5.9798 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516054 | TRAV1WD7 | 345 | 5.5302 | 5.5304 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 14.4336 | 14.4337 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 12.4982 | 12.4996 | 0.0014
GEN-2026-PR5 | 04 SOUTHEAST | 516074 | PONDRSA7 | 345 | 9.9147 | 9.9148 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 516086 | TRAV3WZ7 | 345 | 6.9601 | 6.9605 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 516087 | TRAV22Z7 | 345 | 5.6456 | 5.6458 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 33.1441 | 33.1467 | 0.0026
GEN-2026-PR5 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 47.5071 | 47.5089 | 0.0018
GEN-2026-PR5 | 04 SOUTHEAST | 516100 | HORIZON4 | 138 | 6.8278 | 6.828 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 16.466 | 16.4665 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 516107 | TRAV21Z7 | 345 | 5.6459 | 5.6461 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516108 | TRAV11Z7 | 345 | 5.2469 | 5.2471 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516109 | TRAV12Z7 | 345 | 5.2468 | 5.247 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 16.4355 | 16.436 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 16.4057 | 16.4062 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 516192 | WAGNWTIE7 | 345 | 16.447 | 16.4503 | 0.0033
GEN-2026-PR5 | 04 SOUTHEAST | 516198 | WAGNWL7 | 345 | 16.447 | 16.4503 | 0.0033
GEN-2026-PR5 | 04 SOUTHEAST | 516207 | GADWALL7 | 345 | 16.447 | 16.4503 | 0.0033
GEN-2026-PR5 | 04 SOUTHEAST | 516363 | ARMADILLO_HV | 138 | 10.3521 | 10.3543 | 0.0022
GEN-2026-PR5 | 04 SOUTHEAST | 520409 | WFEC_RNFRO4 | 138 | 11.006 | 11.0089 | 0.0029
GEN-2026-PR5 | 04 SOUTHEAST | 520434 | WAKTASW4 | 138 | 6.5295 | 6.5302 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 520441 | HARDY 4 | 138 | 4.1996 | 4.1997 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 520442 | SHIDWFC4 | 138 | 6.5418 | 6.5419 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 520443 | WEBBCTY4 | 138 | 4.6255 | 4.6256 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 520447 | BLUFCRK4 | 138 | 3.9306 | 3.9308 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 520461 | GARBER 4 | 138 | 4.7501 | 4.7503 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 520479 | CASHION4 | 138 | 6.0697 | 6.0699 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 520535 | BULFTTP4 | 138 | 10.0549 | 10.0559 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 520580 | MAVERIK4 | 138 | 5.5305 | 5.5307 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 520836 | BILLING4 | 138 | 6.9106 | 6.9114 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.3819 | 8.3835 | 0.0016
GEN-2026-PR5 | 04 SOUTHEAST | 521007 | MARLAND_138 | 138 | 7.9608 | 7.9612 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 521034 | PERRY 2 | 69 | 2.4061 | 2.4061 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 9.6497 | 9.6501 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 521100 | WARREN 4 | 138 | 6.6268 | 6.6273 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 522397 | MEDFORD4 | 138 | 7.672 | 7.6734 | 0.0014
GEN-2026-PR5 | 04 SOUTHEAST | 522398 | PONDCRK4 | 138 | 5.2578 | 5.2584 | 0.0006
GEN-2026-PR5 | 04 SOUTHEAST | 524296 | SPNSPUR_WND7 | 345 | 6.4323 | 6.4323 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 524299 | SPNSPUR_COL7 | 345 | 6.4323 | 6.4323 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 16.3852 | 16.3877 | 0.0025
GEN-2026-PR5 | 04 SOUTHEAST | 529241 | OMMORANT | 69 | 15.1933 | 15.1935 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 529242 | OMHUFFYT | 69 | 16.3599 | 16.36 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 529243 | OMNWESTT | 69 | 14.6543 | 14.6544 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 529244 | OMNEASTT | 69 | 11.6248 | 11.6249 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 529245 | OMGONTER | 69 | 11.9644 | 11.9645 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 529246 | OMKAWS | 69 | 12.5548 | 12.5549 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 529247 | OMMCCORD | 69 | 8.513 | 8.513 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 529248 | OMPECANT | 69 | 13.373 | 13.3732 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 529249 | OMWW | 69 | 15.2518 | 15.252 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 529251 | OMRIGGS | 69 | 18.0503 | 18.0505 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 529252 | OMKAWH | 69 | 4.8825 | 4.8826 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.097 | 7.0972 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.9237 | 5.9238 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 532785 | PRATTWF7 | 345 | 4.9374 | 4.9375 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 532786 | FR3 WF7 | 345 | 4.465 | 4.4654 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 532790 | EXPED WF7 | 345 | 7.0602 | 7.0603 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 532792 | FR2EAST7 | 345 | 6.6829 | 6.684 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 532795 | FR2WEST7 | 345 | 5.4353 | 5.436 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.7585 | 23.7619 | 0.0034
GEN-2026-PR5 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.9416 | 13.9475 | 0.0059
GEN-2026-PR5 | 04 SOUTHEAST | 532814 | FR4345KV-TAP | 345 | 7.9132 | 7.9149 | 0.0017
GEN-2026-PR5 | 04 SOUTHEAST | 532837 | G15052_T | 345 | 13.3778 | 13.3788 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 533075 | VIOLA 4 | 138 | 25.1521 | 25.1577 | 0.0056
GEN-2026-PR5 | 04 SOUTHEAST | 534109 | GEN-2016-073 | 345 | 5.5583 | 5.5585 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 539676 | MILAN 4 | 138 | 12.1649 | 12.1661 | 0.0012
GEN-2026-PR5 | 04 SOUTHEAST | 539871 | PIXLEY-SOLAR | 345 | 15.8724 | 15.8732 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 35.1457 | 35.1466 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 562020 | PRSCRKII 7 | 345 | 11.6757 | 11.676 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 562900 | G15052_1 | 345 | 13.322 | 13.323 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 585420 | SUBST HS | 345 | 8.1961 | 8.1963 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 588190 | GEN-2021-043 | 115 | 4.9513 | 4.9573 | 0.006
GEN-2026-PR5 | 04 SOUTHEAST | 588560 | GEN-2021-048 | 115 | 13.1758 | 13.1762 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 588810 | GEN-2021-108 | 345 | 20.197 | 20.1971 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.6994 | 20.6995 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 16.5835 | 16.5836 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.4014 | 5.4015 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 760152 | TNOXF2 | 138 | 45.6654 | 45.6669 | 0.0015
GEN-2026-PR5 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 20.6752 | 20.6775 | 0.0023
GEN-2026-PR5 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 25.6552 | 25.6572 | 0.002
GEN-2026-PR5 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 25.7102 | 25.7121 | 0.0019
GEN-2026-PR5 | 04 SOUTHEAST | 761838 | GEN-2017-121 | 138 | 7.5782 | 7.5784 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.9652 | 12.0093 | 0.0441
GEN-2026-PR5 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 8.3362 | 8.3575 | 0.0213
GEN-2026-PR5 | 04 SOUTHEAST | 762493 | GEN-2018-011 | 138 | 10.6481 | 10.6489 | 0.0008
GEN-2026-PR5 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 20.0346 | 20.0347 | 0.0001
GEN-2026-PR5 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 36.334 | 36.3349 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 47.4789 | 47.4804 | 0.0015
GEN-2026-PR5 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.9555 | 6.9557 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 763065 | GEN-2018-071 | 345 | 15.8608 | 15.8631 | 0.0023
GEN-2026-PR5 | 04 SOUTHEAST | 763069 | G18-071-TAP | 345 | 15.9269 | 15.9292 | 0.0023
GEN-2026-PR5 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1273 | 10.1273 | 0
GEN-2026-PR5 | 04 SOUTHEAST | 763417 | GEN-2018-128 | 345 | 10.9495 | 10.9579 | 0.0084
GEN-2026-PR5 | 04 SOUTHEAST | 763421 | G18-128-TAP | 345 | 12.1074 | 12.1177 | 0.0103
GEN-2026-PR5 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 20.529 | 20.53 | 0.001
GEN-2026-PR5 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 16.1337 | 16.1342 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 765470 | GEN-2021-018 | 345 | 7.7334 | 7.7345 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 765480 | GEN-2021-019 | 345 | 13.5529 | 13.5565 | 0.0036
GEN-2026-PR5 | 04 SOUTHEAST | 767221 | GEN-2022-012 | 345 | 23.3704 | 23.3717 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 767301 | GEN-2022-016 | 345 | 23.3926 | 23.3939 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 767321 | GEN-2022-017 | 345 | 23.0275 | 23.0288 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 770081 | GEN-2022-155 | 138 | 42.0543 | 42.0555 | 0.0012
GEN-2026-PR5 | 04 SOUTHEAST | 770101 | GEN-2022-156 | 138 | 17.366 | 17.3663 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 770501 | GEN-2022-176 | 345 | 12.9901 | 12.9903 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 771261 | GEN-2022-214 | 138 | 13.8755 | 13.8767 | 0.0012
GEN-2026-PR5 | 04 SOUTHEAST | 773121 | GEN-2023-057 | 138 | 10.8954 | 10.8956 | 0.0002
GEN-2026-PR5 | 04 SOUTHEAST | 776821 | GEN-2023-102 | 345 | 11.588 | 11.5885 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 777361 | GEN-2024-013 | 345 | 22.5685 | 22.5696 | 0.0011
GEN-2026-PR5 | 04 SOUTHEAST | 777368 | GEN-2024-C1 | 345 | 20.3619 | 20.3628 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 777369 | GEN-2024-C2 | 345 | 20.3619 | 20.3628 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 777841 | GEN-2024-029 | 138 | 9.8587 | 9.8591 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 778650 | G24-056-TAP | 138 | 11.604 | 11.6047 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 778651 | GEN-2024-056 | 138 | 11.4649 | 11.4656 | 0.0007
GEN-2026-PR5 | 04 SOUTHEAST | 778831 | GEN-2024-062 | 138 | 10.6839 | 10.6848 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 780571 | GEN-2024-120 | 138 | 20.9163 | 20.9168 | 0.0005
GEN-2026-PR5 | 04 SOUTHEAST | 780811 | GEN-2024-128 | 345 | 20.0158 | 20.0162 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 780991 | GEN-2024-134 | 345 | 12.133 | 12.1334 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 781021 | GEN-2024-135 | 345 | 12.133 | 12.1334 | 0.0004
GEN-2026-PR5 | 04 SOUTHEAST | 782100 | G24-171-TAP | 345 | 22.4202 | 22.4214 | 0.0012
GEN-2026-PR5 | 04 SOUTHEAST | 782101 | GEN-2024-171 | 345 | 22.3943 | 22.3956 | 0.0013
GEN-2026-PR5 | 04 SOUTHEAST | 784020 | G24-235-TAP | 345 | 13.966 | 13.9684 | 0.0024
GEN-2026-PR5 | 04 SOUTHEAST | 784021 | GEN-2024-235 | 345 | 13.966 | 13.9684 | 0.0024
GEN-2026-PR5 | 04 SOUTHEAST | 784141 | GEN-2024-239 | 345 | 42.8498 | 42.8628 | 0.013
GEN-2026-PR5 | 04 SOUTHEAST | 784530 | GEN-2024-252 | 345 | 38.287 | 38.2974 | 0.0104
GEN-2026-PR5 | 04 SOUTHEAST | 784531 | GEN-2024-252 | 345 | 38.8154 | 38.8259 | 0.0105
GEN-2026-PR5 | 04 SOUTHEAST | 784590 | GEN-2024-254 | 345 | 38.4784 | 38.4971 | 0.0187
GEN-2026-PR5 | 04 SOUTHEAST | 784591 | GEN-2024-254 | 345 | 39.0093 | 39.0283 | 0.019
GEN-2026-PR5 | 04 SOUTHEAST | 784620 | GEN-2024-255 | 345 | 25.8846 | 25.8895 | 0.0049
GEN-2026-PR5 | 04 SOUTHEAST | 784621 | GEN-2024-255 | 345 | 26.249 | 26.2539 | 0.0049
GEN-2026-PR5 | 04 SOUTHEAST | 786601 | GEN-2024-321 | 345 | 33.424 | 33.4249 | 0.0009
GEN-2026-PR5 | 04 SOUTHEAST | 786991 | GEN-2024-334 | 345 | 16.3599 | 16.3623 | 0.0024
GEN-2026-PR5 | 04 SOUTHEAST | 786998 | G24-334-C1 | 345 | 16.2801 | 16.2826 | 0.0025
GEN-2026-PR5 | 04 SOUTHEAST | 786999 | G24-334-C2 | 345 | 16.2964 | 16.2989 | 0.0025
GEN-2026-PR5 | 04 SOUTHEAST | 787170 | G24-340-TAP | 345 | 19.8312 | 19.8315 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 787171 | GEN-2024-340 | 345 | 19.8211 | 19.8214 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 787290 | G24-344-TAP | 345 | 17.3629 | 17.3632 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 787291 | GEN-2024-344 | 345 | 17.3629 | 17.3632 | 0.0003
GEN-2026-PR5 | 04 SOUTHEAST | 852252 | TEST-FR4 | 345 | 7.9132 | 7.9149 | 0.0017
GEN-2026-PR5 | 04 SOUTHEAST | 852253 | TEST-FR5-0 | 345 | 7.9132 | 7.9149 | 0.0017
GEN-2026-PR5 | 04 SOUTHEAST | 914715 | SKELETON__HV | 345 | 6.0194 | 6.1545 | 0.1351
GEN-2026-PR6 | 5 SOUTHEAST | 914720 | SKELETON__HV | 345 | 19.234 | 19.3528 | 0.1188

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR5 | 7.0656 | PASS | TBD | TBD | N/A | N/A | TBD

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | base | 11.0577 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 10.9835 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 10.9819 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 10.9301 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 10.9288 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 515694 [ARMFTWD4 138.00] CKT 1 | 11.0576 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514712 [FAIRMON4 138.00] CKT 1 | 11.0348 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 11.0084 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 11.0484 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514711 [WAUKOTP4 138.00] CKT 1 | 10.9235 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 11.0196 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 11.0559 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514733 [MARSHL 4 138.00] CKT 1 | 10.9283 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.3238 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 7.0704 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 11.1274 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.6895 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 10.9283 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 521006 [MARSHAL4 138.00] CKT Z1 | 11.0575 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515576 [RANCHRD7 345.00] CKT 1 | 10.9529 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515894 [THUNDER7 345.00] CKT 1 | 11.0621 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 10.9843 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.6701 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 10.9439 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 11.0574 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 11.007 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.964 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.9877 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 10.988 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 11.0569 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 11.0568 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 11.0568 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.9468 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 11.0422 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 11.0419 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 11.0605 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.0431 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 11.043 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 11.0678 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 11.06 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515477 [CHSHLMV7 345.00] CKT 1 | 11.0316 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515543 [RENFROW7 345.00] CKT 1 | 9.3242 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 7.0656 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 11.0602 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 11.0431 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515546 [GRANTCO4 138.00] CKT 1 | 11.0543 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 10.9907 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 520409 [WFEC_RNFRO4 138.00] CKT 1 | 10.9942 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 11.0525 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516010 [PINTAIL7 345.00] TO BUS 516019 [KINGWD 7 345.00] CKT Z1 | 11.0602 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 10.5206 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 532814 [FR4345KV-TAP 345.00] CKT 1 | 11.0534 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 11.0514 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 11.0034 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 10.8986 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.5] CKT 1 | 11.0524 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 10.8597 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.8] CKT 1 | 10.9945 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514774 [HENESEY4 138.00] CKT 1 | 10.9239 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514712 [FAIRMON4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 11.035 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 514706 [COWCRK 4 138.00] CKT 1 | 10.9307 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 11.0574 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514715 [WOODRNG7 345.00] TO BUS 515770 [WOODRNG1 13.8] CKT 2 | 9.9992 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 11.0949 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914715 [SKELETON__HV 345.00] CKT 1 | 11.0787 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914720 [SKELETON__HV 345.00] CKT 1 | 11.0583 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514790 [IMO 4 138.00] CKT 1 | 11.0426 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 11.0575 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514730 [SO4TH 2 69.00] TO BUS 515758 [SO4TH 1 13.2] CKT 1 | 11.0563 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514704 [MILLERT4 138.00] CKT 1 | 11.0539 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514707 [PERRY 4 138.00] CKT 1 | 11.043 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514798 [SNRPMPT4 138.00] CKT 1 | 11.055 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514805 [SOONER1G 22.00] CKT 1 | 10.8631 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 11.0584 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514803 [SOONER 7 345.00] TO BUS 515760 [SOONER 1 13.8] CKT 5 | 10.9943 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 514806 [SOONER2G 20.00] CKT 1 | 10.7795 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 10.908 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514829 [PINE ST4 138.00] CKT 1 | 11.0502 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 11.0344 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515373 [LBRTYLK4 138.00] CKT 1 | 11.0464 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515377 [CRESENT4 138.00] CKT 1 | 11.0508 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 11.0608 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.8] CKT 2 | 11.0544 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.8] CKT 3 | 11.0546 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 514885 [NORTWS41 13.8] CKT 4 | 11.0547 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 10.9864 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 11.0659 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 10.9695 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784141 [GEN-2024-239 345.00] CKT 1 | 11.0674 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784530 [GEN-2024-252 345.00] CKT 3 | 11.0626 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784531 [GEN-2024-252 345.00] CKT 1 | 11.0023 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515714 [CIMARO11 13.8] CKT 1 | 11.0495 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515715 [CIMARO21 13.8] CKT 2 | 11.0506 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 11.0352 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 | 11.0581 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 | 11.0581 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 3 | 11.0581 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515703 [ARCADI21 13.8] CKT 2 | 11.0574 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515704 [ARCADI31 13.8] CKT 3 | 11.0572 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515700 [ARCADI41 13.8] CKT 4 | 11.0571 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 787290 [G24-344-TAP 345.00] CKT 1 | 11.0261 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514899 [REDBUD1S 18.00] TO BUS 514910 [REDBUD1G 18] CKT 1 | 11.0322 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514900 [REDBUD2S 18.00] TO BUS 514911 [REDBUD2G 18] CKT 1 | 11.0322 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514905 [REDBUD3S 18.00] TO BUS 514912 [REDBUD3G 18] CKT 1 | 11.0321 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514940 [REDBUD4S 18.00] TO BUS 514942 [REDBUD4G 18] CKT 1 | 11.0322 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 11.0453 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 11.0453 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.0673 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.027 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 11.0514 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 11.0531 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 11.0631 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 11.0602 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 11.0619 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515795 [WWDEHV21 13.8] CKT 2 | 11.0565 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515799 [WWDEHV31 13.8] CKT 3 | 11.056 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515450 [CRSRDW21 34.5.00] TO BUS 515452 [CRSRDWT2 13.8] CKT 2 | 11.0592 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515449 [CRSRDW11 34.5.00] TO BUS 515451 [CRSRDWT1 13.8] CKT 1 | 11.059 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515479 [CHSHMVE1 34.5.00] TO BUS 515482 [CHSHMVET 13.2] CKT 1 | 11.0448 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515484 [CHSHMVW1 34.5.00] TO BUS 515485 [CHSHMVWT 13.2] CKT 1 | 11.0446 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 11.0639 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 10.9715 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.8202 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.8] CKT 2 | 10.8881 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515546 [GRANTCO4 138.00] TO BUS 515547 [GRANTCO2 69.00] TO BUS 515548 [GRANTC11 13.2] CKT 4 | 11.0539 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 515426 [RDRUNNR4 138.00] CKT 1 | 10.9907 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 522397 [MEDFORD4 138.00] CKT 1 | 11.0578 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515621 [OPENSKY7 345.00] CKT 1 | 10.9496 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515688 [FRNTWND7 345.00] CKT 1 | 11.0583 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 529200 [OMCDLEC7 345.00] CKT 1 | 11.0577 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 11.0584 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 786991 [GEN-2024-334 345.00] CKT 1 | 11.0091 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515583 [SLINGW11 34.5.00] TO BUS 515584 [SILNGWT1 13.8] CKT 1 | 11.0621 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515632 [SILNGW21 34.5.00] TO BUS 515633 [SILNGWT2 13.8] CKT 2 | 11.0634 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 515586 [MMTHPW11 34.5.00] TO BUS 515588 [MMTHPWT1 13.8] CKT 2 | 11.0618 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 915586 [MMTHPW21 34.5.00] TO BUS 915588 [MMTHPWT2 13.8] CKT 1 | 11.0559 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515647 [GRNTWD11 34.5.00] TO BUS 515649 [GRNTWDT1 12.5] CKT 1 | 11.0503 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515648 [GRNTWD12 34.5.00] TO BUS 515650 [GRNTWDT2 12.5] CKT 1 | 11.0502 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 516363 [ARMADILLO_HV 138.00] CKT 1 | 11.0565 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 515695 [ARMFTL11 34.5.00] TO BUS 515698 [ARMFTT11 13.8] CKT 1 | 11.0602 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] TO BUS 515884 [RDDRTT11 13.2] CKT 1 | 11.0554 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] TO BUS 515885 [RDDRTT21 13.2] CKT 1 | 11.0549 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765470 [GEN-2021-018 345.00] CKT 1 | 11.0619 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765480 [GEN-2021-019 345.00] CKT 1 | 11.0591 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515891 [THNDRL21 34.5.00] TO BUS 515893 [THNDRT21 12.5] CKT 1 | 11.0597 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515890 [THNDRL11 34.5.00] TO BUS 515892 [THNDRT11 12.5] CKT 1 | 11.0606 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515975 [G15-066T 345.00] TO BUS 515974 [GEN-2015-066 345.00] CKT 1 | 11.0602 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 588190 [GEN-2016-128 345.00] CKT 1 | 11.0948 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 515991 [SKELTL11 34.5.00] TO BUS 515992 [SKELTT11 13.8] CKT 1 | 11.104 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516017 [KNGWDL11 34.5.00] TO BUS 516020 [KNGWDT11 13.2] CKT 1 | 11.0585 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516018 [KNGWDL21 34.5.00] TO BUS 516021 [KNGWDT21 13.2] CKT 1 | 11.0599 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 11.0607 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 11.0581 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516207 [GADWALL7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 10.9595 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516207 [GADWALL7 345.00] TO BUS 516192 [WAGNWTIE7 345.00] CKT 1 | 11.0665 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 520409 [WFEC_RNFRO4 138.00] TO BUS 520434 [WAKTASW4 138.00] CKT 1 | 10.9941 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 11.0079 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 11.0519 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 2 | 11.0515 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532791 [BENTON 7 345.00] CKT 1 | 11.0405 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 11.0092 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.8] CKT 1 | 11.0575 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.8] CKT 1 | 11.0575 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.7924 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.8] CKT 2 | 11.0333 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.8] CKT 1 | 11.0401 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 532792 [FR2EAST7 345.00] CKT 1 | 11.0536 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 765814 [G21-056-XFM1 34.5.00] CKT 1 | 11.0591 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 765817 [G21-056-XFM2 34.5.00] CKT 1 | 11.0586 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 11.0591 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 11.0591 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532984 [SUMNER 4 138.00] CKT 1 | 11.0496 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 533036 [CLEARWT4 138.00] CKT 1 | 11.0373 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 11.0535 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 11.0476 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 11.0386 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 & 2 | 11.0579 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 & 3 | 11.0579 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 & 3 | 11.0579 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 & 2 | 10.9852 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 & 2 | 11.004 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 & 2 | 10.9877 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | base | 11.1041 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 514803 [SOONER 7 345.00] CKT 1 | 11.03 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 11.0286 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 10.9748 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 10.9723 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 515694 [ARMFTWD4 138.00] CKT 1 | 11.1064 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514712 [FAIRMON4 138.00] CKT 1 | 11.0799 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 11.0522 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 11.0944 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514711 [WAUKOTP4 138.00] CKT 1 | 10.9593 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 11.0634 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 11.1021 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514733 [MARSHL 4 138.00] CKT 1 | 10.9705 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 9.4252 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 7.098 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 11.1867 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.6324 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 10.9703 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 521006 [MARSHAL4 138.00] CKT Z1 | 11.1039 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515576 [RANCHRD7 345.00] CKT 1 | 10.9239 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515894 [THUNDER7 345.00] CKT 1 | 11.1215 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 11.0315 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 7.6325 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 10.9833 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 11.1028 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 11.0554 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.0026 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.0323 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 11.0326 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 11.1035 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 11.1034 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 11.1033 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 10.9973 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 11.0808 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 11.0803 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 11.1095 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 11.0826 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 11.0825 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 11.124 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 11.1091 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515477 [CHSHLMV7 345.00] CKT 1 | 11.0736 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515543 [RENFROW7 345.00] CKT 1 | 9.4445 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 7.0985 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 11.122 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 11.0807 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515546 [GRANTCO4 138.00] CKT 1 | 11.1004 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 11.021 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 520409 [WFEC_RNFRO4 138.00] CKT 1 | 11.0406 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT Z1 | 11.1012 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516010 [PINTAIL7 345.00] TO BUS 516019 [KINGWD 7 345.00] CKT Z1 | 11.1036 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 10.6433 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 532814 [FR4345KV-TAP 345.00] CKT 1 | 11.0675 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 11.0896 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 11.0468 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 10.9405 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] TO BUS 509879 [WEKIW1-1 34.5] CKT 1 | 11.0991 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 10.9009 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] TO BUS 512817 [CLEVLND1 13.8] CKT 1 | 11.0456 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514774 [HENESEY4 138.00] CKT 1 | 10.96 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514712 [FAIRMON4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 11.0802 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 514706 [COWCRK 4 138.00] CKT 1 | 10.9768 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 11.1035 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514715 [WOODRNG7 345.00] TO BUS 515770 [WOODRNG1 13.8] CKT 2 | 10.005 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 11.1405 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914715 [SKELETON__HV 345.00] CKT 1 | 11.12 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914720 [SKELETON__HV 345.00] CKT 1 | 11.1046 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514790 [IMO 4 138.00] CKT 1 | 11.089 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 11.1038 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514730 [SO4TH 2 69.00] TO BUS 515758 [SO4TH 1 13.2] CKT 1 | 11.1025 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514704 [MILLERT4 138.00] CKT 1 | 11.0985 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514707 [PERRY 4 138.00] CKT 1 | 11.0901 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514798 [SNRPMPT4 138.00] CKT 1 | 11.0997 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514805 [SOONER1G 22.00] CKT 1 | 10.9329 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 11.1046 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514803 [SOONER 7 345.00] TO BUS 515760 [SOONER 1 13.8] CKT 5 | 11.0422 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 514806 [SOONER2G 20.00] CKT 1 | 10.86 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 10.9405 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514829 [PINE ST4 138.00] CKT 1 | 11.0946 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 11.0811 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515373 [LBRTYLK4 138.00] CKT 1 | 11.0924 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515377 [CRESENT4 138.00] CKT 1 | 11.0969 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 11.1032 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515742 [NORTWS21 13.8] CKT 2 | 11.0998 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 515743 [NORTWS31 13.8] CKT 3 | 11.1 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514879 [NORTWST4 138.00] TO BUS 514885 [NORTWS41 13.8] CKT 4 | 11.1 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 11.0374 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 11.1308 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 11.0171 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784141 [GEN-2024-239 345.00] CKT 1 | 11.1232 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784530 [GEN-2024-252 345.00] CKT 3 | 11.1163 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784531 [GEN-2024-252 345.00] CKT 1 | 11.0741 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515714 [CIMARO11 13.8] CKT 1 | 11.0932 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 514898 [CIMARON4 138.00] TO BUS 515715 [CIMARO21 13.8] CKT 2 | 11.0937 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 11.0831 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 | 11.1013 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 | 11.1013 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 3 | 11.1013 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515703 [ARCADI21 13.8] CKT 2 | 11.1039 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515704 [ARCADI31 13.8] CKT 3 | 11.1038 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514907 [ARCADIA4 138.00] TO BUS 515700 [ARCADI41 13.8] CKT 4 | 11.1037 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 787290 [G24-344-TAP 345.00] CKT 1 | 11.0836 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514899 [REDBUD1S 18.00] TO BUS 514910 [REDBUD1G 18] CKT 1 | 11.0938 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514900 [REDBUD2S 18.00] TO BUS 514911 [REDBUD2G 18] CKT 1 | 11.0938 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514905 [REDBUD3S 18.00] TO BUS 514912 [REDBUD3G 18] CKT 1 | 11.0936 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514940 [REDBUD4S 18.00] TO BUS 514942 [REDBUD4G 18] CKT 1 | 11.0938 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 11.0814 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 11.0814 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 11.1202 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0762 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 11.0997 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 11.0994 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 11.1214 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 11.1119 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 11.1207 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515795 [WWDEHV21 13.8] CKT 2 | 11.103 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] TO BUS 515799 [WWDEHV31 13.8] CKT 3 | 11.1029 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515450 [CRSRDW21 34.5.00] TO BUS 515452 [CRSRDWT2 13.8] CKT 2 | 11.1064 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515449 [CRSRDW11 34.5.00] TO BUS 515451 [CRSRDWT1 13.8] CKT 1 | 11.1052 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515479 [CHSHMVE1 34.5.00] TO BUS 515482 [CHSHMVET 13.2] CKT 1 | 11.0883 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515484 [CHSHMVW1 34.5.00] TO BUS 515485 [CHSHMVWT 13.2] CKT 1 | 11.0879 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 11.1173 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 11.0403 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.3043 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.8] CKT 2 | 10.9127 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515546 [GRANTCO4 138.00] TO BUS 515547 [GRANTCO2 69.00] TO BUS 515548 [GRANTC11 13.2] CKT 4 | 11.1001 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 515426 [RDRUNNR4 138.00] CKT 1 | 11.0211 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 522397 [MEDFORD4 138.00] CKT 1 | 11.1042 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515621 [OPENSKY7 345.00] CKT 1 | 10.3807 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515688 [FRNTWND7 345.00] CKT 1 | 11.1041 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 529200 [OMCDLEC7 345.00] CKT 1 | 11.0604 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 11.1162 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 786991 [GEN-2024-334 345.00] CKT 1 | 11.0691 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515583 [SLINGW11 34.5.00] TO BUS 515584 [SILNGWT1 13.8] CKT 1 | 11.1125 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515632 [SILNGW21 34.5.00] TO BUS 515633 [SILNGWT2 13.8] CKT 2 | 11.117 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 515586 [MMTHPW11 34.5.00] TO BUS 515588 [MMTHPWT1 13.8] CKT 2 | 11.1106 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 915586 [MMTHPW21 34.5.00] TO BUS 915588 [MMTHPWT2 13.8] CKT 1 | 11.1023 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515647 [GRNTWD11 34.5.00] TO BUS 515649 [GRNTWDT1 12.5] CKT 1 | 11.0909 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515648 [GRNTWD12 34.5.00] TO BUS 515650 [GRNTWDT2 12.5] CKT 1 | 11.0909 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 516363 [ARMADILLO_HV 138.00] CKT 1 | 11.1038 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 515695 [ARMFTL11 34.5.00] TO BUS 515698 [ARMFTT11 13.8] CKT 1 | 11.1058 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] TO BUS 515884 [RDDRTT11 13.2] CKT 1 | 11.1019 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] TO BUS 515885 [RDDRTT21 13.2] CKT 1 | 11.1015 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765470 [GEN-2021-018 345.00] CKT 1 | 11.1133 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765480 [GEN-2021-019 345.00] CKT 1 | 11.1106 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515891 [THNDRL21 34.5.00] TO BUS 515893 [THNDRT21 12.5] CKT 1 | 11.1052 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515890 [THNDRL11 34.5.00] TO BUS 515892 [THNDRT11 12.5] CKT 1 | 11.1054 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515975 [G15-066T 345.00] TO BUS 515974 [GEN-2015-066 345.00] CKT 1 | 11.1101 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 588190 [GEN-2016-128 345.00] CKT 1 | 11.15 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 515991 [SKELTL11 34.5.00] TO BUS 515992 [SKELTT11 13.8] CKT 1 | 11.1619 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516017 [KNGWDL11 34.5.00] TO BUS 516020 [KNGWDT11 13.2] CKT 1 | 11.1021 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516018 [KNGWDL21 34.5.00] TO BUS 516021 [KNGWDT21 13.2] CKT 1 | 11.1035 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 11.1215 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 11.1067 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516207 [GADWALL7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 11.0034 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 516207 [GADWALL7 345.00] TO BUS 516192 [WAGNWTIE7 345.00] CKT 1 | 11.1253 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 520409 [WFEC_RNFRO4 138.00] TO BUS 520434 [WAKTASW4 138.00] CKT 1 | 11.0405 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 10.3567 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 11.0967 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 2 | 11.0983 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532791 [BENTON 7 345.00] CKT 1 | 11.0875 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 11.0683 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] TO BUS 532829 [WICH11 1 13.8] CKT 1 | 11.1016 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] TO BUS 532830 [WICH12 1 13.8] CKT 1 | 11.101 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.2896 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.8] CKT 2 | 11.0808 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.8] CKT 1 | 11.079 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 532792 [FR2EAST7 345.00] CKT 1 | 11.0694 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 765814 [G21-056-XFM1 34.5.00] CKT 1 | 11.1043 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 765817 [G21-056-XFM2 34.5.00] CKT 1 | 11.1043 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 852252 [TEST-FR4 345.00] CKT 1 | 11.1044 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532814 [FR4345KV-TAP 345.00] TO BUS 852253 [TEST-FR5-0 345.00] CKT 1 | 11.1043 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 532984 [SUMNER 4 138.00] CKT 1 | 11.0962 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 533036 [CLEARWT4 138.00] CKT 1 | 11.0804 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB4 138.00] CKT 1 | 11.1003 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 4 138.00] CKT 1 | 11.095 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 11.0818 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 & 2 | 11.1004 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 & 3 | 11.1004 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 & 3 | 11.1004 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 & 2 | 10.9514 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 & 2 | 11.0335 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6
GEN-2026-PR5 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR5 | 345kV Bus at OGE Woodring Substation, Goultry County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 & 2 | 10.6827 | PASS | No Data Available | TBD | TBD | 60.4 | 75.6

## WSCR
* WSCR is not applicable for this study.