## Executive Summary
Executive Summary: Group 04 GEN-2026-PR12 Priority Process Study
Interconnection Customer GEN-2026-PR12 (Group 04) has requested an Interconnection Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR12 generation for total of:
11.96 MW
The minimum cost of interconnecting GEN-2026-PR12 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR12 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 07/30/2026
Costs for Wind Requests were allocated using the 29L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4623300% | SPP | Steady State Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR12 | 04 SOUTHEAST | 38 | Priority Process | Wind | 11.96 | 0 | 0 | 0 | 0 | 0 | 0 | 11.96 | 11.96 | -0.1 | ER | OG&E | NARDINS2 69kV | SPECIAL STUDY
GEN-2026-PR11 | 05 SOUTHWEST | 37 | Priority Process | Wind | 30 | [9 empty] | ER | SPS | Lost Draw 3 115kV substation | SPECIAL STUDY
GEN-2026-PR9 | 05 SOUTHWEST | 35 | Priority Process | Wind | 15.99 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | SPECIAL STUDY
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | [9 empty] | ER | MIDW | South Hays 230kV | SPECIAL STUDY
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | SPECIAL STUDY
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | SPECIAL STUDY
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | SPECIAL STUDY
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | SPECIAL STUDY
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 25SP | Stability 25WP
GEN-2026-PR12 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 11.96 | 0 | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 ftlo System Intact | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 11.96 | 11.96
GEN-2026-PR12 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 11.96 | 0 | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 ftlo System Intact | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 11.96 | 11.96
GEN-2026-PR12 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 11.96 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11.96 | N/A
GEN-2026-PR12 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 11.96 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 11.96 | N/A
GEN-2026-PR12 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 11.96 | 0 | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 ftlo System Intact | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 11.96 | 11.96
GEN-2026-PR12 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 11.96 | 0 | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 ftlo System Intact | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 11.96 | 11.96
GEN-2026-PR12 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 11.96 | 11.96 | None | None | N/A | N/A | N/A | 11.96 | N/A | N/A | N/A | N/A | N/A | 11.96
GEN-2026-PR12 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 11.96 | 11.96 | None | None | N/A | N/A | N/A | 11.96 | N/A | N/A | N/A | N/A | N/A | 11.96

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29L | System Intact | 194 | 222 | 107.86 | 108.7 |  |  |  | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29L | P13:138:OKGE:BKRBKR_3W080:::HV: | 194 | 222 | 102.48 | 103.55 |  |  |  | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29L | System Intact | 830 | 830 | 105.08 | 105.47 |  |  |  | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29L | 515621 OPENSKY7 345 560053 G15052_T 345 1 | 830 | 830 | 122.95 | 123.32 |  |  |  | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 121.37 | 121.5 |  |  |  | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29L | System Intact | 830 | 830 | 104.23 | 104.61 |  |  |  | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29L | 515621 OPENSKY7 345 560053 G15052_T 345 1 | 830 | 830 | 122.2 | 122.58 |  |  |  | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR12 PSIS | ERIS | Thermal | None | 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS CF | ERIS | Thermal | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 127.08 | 127.13 |  |  |  | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
04ALL | GEN-2026-PR12 PSIS CF | ERIS | Thermal | None | 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR12 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR12 | GEN-2026-PR12 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | 0 | 0% | 81488001.7662 | 0.06719
GEN-2026-PR12 | GEN-2026-PR12 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | Contingent | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1793 MVA | 0 | 0% | 45914000 | 0.21897
GEN-2026-PR12 | GEN-2026-PR12 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1 | Contingent | Rebuild the existing VIOLA 7 to G18-128-TAP 345 kV line 1 (11.39 miles) to a minimum rating of 1793 MVA | 0 | 0% | 25058000 | 0.21897
GEN-2026-PR12 | GEN-2026-PR12 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1 | Contingent | Rebuild the existing MIDLTNT4 to CRESWLN4 138 kV line 1 (9.08 miles) to a minimum rating of 395 MVA | 0 | 0% | 10896000 | 0.13833
GEN-2026-PR12 | GEN-2026-PR12 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Rebuild the HOYT 7 to JEC N 7 345kV Line 1 | Contingent | Rebuild the existing HOYT 7 to JEC N 7 345 kV line 1 (24.3 miles) to a minimum rating of 1616 MVA | 0 | 0% | 56239874.14 | N/A
GEN-2026-PR12 | GEN-2026-PR12 PSIS | 04 SOUTHEAST | TBD | ERIS | NARDINS2 69kV Substation GEN-2026-PR12 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR12 (11.96/Wind), into NARDINS2 69kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR12 | GEN-2026-PR12 PSIS | 04 SOUTHEAST | TBD | ERIS | NARDINS2 69kV Substation GEN-2026-PR12 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR12 (11.96/Wind), into NARDINS2 69kV Substation | TBD | 100% | TBD | 1
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR12 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | WERE | 36 | 81488001.7662
Contingent | GEN-2026-PR12 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1793 MVA | OKGE/WERE | 36 | 45914000
Contingent | GEN-2026-PR12 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing VIOLA 7 to G18-128-TAP 345 kV line 1 (11.39 miles) to a minimum rating of 1793 MVA | WERE | 36 | 25058000
Contingent | GEN-2026-PR12 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1 | TBD | Rebuild the existing MIDLTNT4 to CRESWLN4 138 kV line 1 (9.08 miles) to a minimum rating of 395 MVA | OKGE/WERE | 36 | 10896000
Contingent | GEN-2026-PR12 PSIS CF | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the HOYT 7 to JEC N 7 345kV Line 1 | TBD | Rebuild the existing HOYT 7 to JEC N 7 345 kV line 1 (24.3 miles) to a minimum rating of 1616 MVA | WERE | TBD | 56239874.14
Interconnection | GEN-2026-PR12 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR12 PSIS | ERIS | NARDINS2 69kV Substation GEN-2026-PR12 Interconnection (TOIF) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR12 (11.96/Wind), into NARDINS2 69kV Substation | OKGE | TBD | TBD
Interconnection | GEN-2026-PR12 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR12 PSIS | ERIS | NARDINS2 69kV Substation GEN-2026-PR12 Interconnection (Non-Shared NU) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR12 (11.96/Wind), into NARDINS2 69kV Substation | OKGE | TBD | TBD
219595875.9062

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504162 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Seminole - Crawfish Draw 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem - Seminole 765 kV Ckt 1 New Line | Build a 131.4-mile 765 kV Ckt 1 line from Anthem to Seminole | 2025 ITP | Yes | N/A | -0.05634 | 4821400% | 762120000
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504237 | Potter Co - Woodward - Crawfish Draw - Phantom 765 kV New Line | Woodward - Potter Co 765 kV Ckt 1 New Line | Build a 207-mile 765 kV Ckt 1 line from Woodward to Potter Co | 2025 ITP | Yes | N/A | 0.04426 | 4821400% | 1200600000
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504279 | Potter Co - Woodward - Crawfish Draw - Phantom 765 kV New Line | Woodward - Crawfish Draw 765 kV Ckt 1 New Line | Build a 263.6-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw | 2025 ITP | Yes | N/A | 0.0336 | 4821400% | 1528880000
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504291 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Seminole - Crawfish Draw 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 152.4-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | -0.09494 | 4821400% | 883920000
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504296 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Seminole - Crawfish Draw 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 180.1-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | 0.06951 | 4821400% | 1044580000
GEN-2026-PR12 | 04 SOUTHEAST | ER | 220767 | 50702 | Device - Wakita 138 kV | Wakita 138 kV Cap Bank | Add 20 Mvar of capacitance at Wakita 138 kV. | 2014 ITPNT | Yes | N/A | -0.06437 | 4288700% | 504000
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 170643 | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at VIOLA 138 kV | DISIS-2021-001 | Yes | N/A | -0.03661 | TBD | 1270333
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504304 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Seminole - Crawfish Draw 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Viola | 2025 ITP | Yes | N/A | -0.05481 | 4821400% | 104567202
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504308 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Seminole - Crawfish Draw 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Viola | 2025 ITP | Yes | N/A | -0.05481 | 4821400% | 104567202
GEN-2026-PR12 | 04 SOUTHEAST | ER | TBD | 504311 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Minco 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Viola 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Viola | 2025 ITP | Yes | N/A | -0.05481 | 4821400% | 104567202

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR12 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00018 | -0.0021528 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00532 | -0.063627 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00239 | -0.028584 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00239 | -0.028584 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00129 | -0.015428 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00774 | 0.09257 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.0068 | 0.081328 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -0.00031 | -0.0037076 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -0.00031 | -0.0037076 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00109 | 0.013036 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00106 | 0.012678 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00324 | 0.03875 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00396 | 0.047362 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00075 | -0.00897 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00075 | -0.00897 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00977 | -0.11685 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.00094 | -0.011242 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00032 | 0.0038272 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00032 | 0.0038272 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00041 | 0.0049036 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00062 | 0.0074152 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00026 | 0.0031096 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00029 | 0.0034684 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 2e-05 | 0.0002392 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 2e-05 | 0.0002392 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 2e-05 | 0.0002392 | NO
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 2e-05 | 0.0002392 | NO

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR12 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR12 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.08679 | 109.19 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 194 | 222 | 0.13674 | 108.7 | System Intact | TDF Impact | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21626 | 107.75 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21572 | 107.15 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21626 | 106.9 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21572 | 106.31 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 106.19 | P12:500:EES-EAI:KEO:WMPEHV | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.47 | System Intact | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 105.35 | P12:500:EES-EAI:KEO:WMPEHV | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.75 | P11:22:EES:1RVR_BND_G1!:1::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.61 | System Intact | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.89 | P11:22:EES:1RVR_BND_G1!:1::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.74 | P11:345:MEC:WSEC:4 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.37 | P13:345:XEL:MNTCE31G:MNTCELO3:1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.36 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 106.2 | P12:500:EES:8HOLND BTM%:8ISES%:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.11 | P11:345:MEC:LOUISA:1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.9 | P11:345:MEC:WSEC:4 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.52 | P13:345:XEL:MNTCE31G:MNTCELO3:1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.52 | P11:345:AMMO::CALLAWAY:1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 105.36 | P12:500:EES:8HOLND BTM%:8ISES%:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.26 | P11:345:MEC:LOUISA:1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.75 | P12:230-21:EES:FCY:RVB | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | P11:25:EES:1WAT U3!:1::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.6 | P11:18:EES:1J472MCPS G2:1::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.58 | P11:24:EES:TURKCOAL:1::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.2 | P11:22:EES:1ANO U2:1::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.88 | P12:230-21:EES:FCY:RVB | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | P11:25:EES:1WAT U3!:1::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.73 | P11:18:EES:1J472MCPS G2:1::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.71 | P11:24:EES:TURKCOAL:1::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.33 | P11:22:EES:1ANO U2:1::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.59 | P11:345:MEC:WSEC:3 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21585 | 106.37 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.34 | P12:25:EES:7CALAWY 1:1CAL G1:1:HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.74 | P11:345:MEC:WSEC:3 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21585 | 105.53 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.49 | P12:25:EES:7CALAWY 1:1CAL G1:1:HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.74 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | P11:25:EES:1WAT U3!:1 & P12:HVEES6EXXON%6DOWNTOWN!1:HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.72 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.62 | P12:24:EES:TURK 4%:TURKCOAL:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21719 | 104.29 | P12:24:EES:MUSKOGE7!:MUSKOG6G:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.25 | P12:22:EES:8ANO%:1ANO U2:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.88 | P11:21:EES:RVB:1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | P11:25:EES:1WAT U3!:1 & P12:HVEES6EXXON%6DOWNTOWN!1:HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.86 | P11:25:EES:WATERF:1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.76 | P12:24:EES:TURK 4%:TURKCOAL:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21719 | 103.42 | P12:24:EES:MUSKOGE7!:MUSKOG6G:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.38 | P12:22:EES:8ANO%:1ANO U2:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.23 | P13:345:XEL:PRIS31G:PRISLD3:1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.22 | P11:20:XEL:PR_ISLD:31G | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.38 | P13:345:XEL:PRIS31G:PRISLD3:1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.38 | P11:20:XEL:PR_ISLD:31G | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.71 | P11:18:EES:1J484LCPS G1:1::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.43 | P12:22:EES:8ANO%:1ANO U1:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.85 | P11:18:EES:1J484LCPS G1:1::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.56 | P12:22:EES:8ANO%:1ANO U1:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21588 | 107.48 | P23:500:EES-EAI:KEO:B4941::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21587 | 107.41 | P23:500:EES-EAI:KEO:B4921::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21583 | 107.31 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.8 | P55:345:XEL:PRI1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.74 | P23:345:MEC:CBEC:905::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21588 | 106.64 | P23:500:EES-EAI:KEO:B4941::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.59 | P23:345:MEC:CBEC:908::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21587 | 106.58 | P23:500:EES-EAI:KEO:B4921::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21583 | 106.48 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21583 | 106.45 | P23:500:EES-EAI:KEO:B4931::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21585 | 106.44 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.37 | P23:345:XEL:8N8 MNN:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.23 | P23:345:XEL:PRISLD3:8H17::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 106.22 | P55:345:MEC:SUB 93 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 106.2 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 106.17 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 106.14 | P23:345:MEC:SUB 93:954::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 106.13 | P23:345:MEC:SUB 93:964::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.95 | P55:345:XEL:PRI1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.89 | P23:345:MEC:CBEC:905::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.74 | P23:345:MEC:CBEC:908::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21583 | 105.61 | P23:500:EES-EAI:KEO:B4931::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21585 | 105.6 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.52 | P23:345:XEL:8N8 MNN:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.38 | P23:345:XEL:PRISLD3:8H17::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 105.38 | P55:345:MEC:SUB 93 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 105.35 | P21:500:EES:8KEO%:CHALKBLUFFPV:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 105.32 | P21:500:EES:CHALKBLUFFPV:8W.MEMPHIS%:1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 105.29 | P23:345:MEC:SUB 93:954::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 105.28 | P23:345:MEC:SUB 93:964::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.75 | P21:230:EES:6FANCY_PT%:6RIVER_BEND:1:HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 104.62 | P55:345:MEC:PONY CREEK OR SOUTHLAND | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21738 | 104.54 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.88 | P21:230:EES:6FANCY_PT%:6RIVER_BEND:1:HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 103.75 | P55:345:MEC:PONY CREEK OR SOUTHLAND | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21738 | 103.67 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2188 | 110.67 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2188 | 109.84 | P12:345:AEPW-GRDA:T.NO.-7:CLEVLND7::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21561 | 106.56 | P12:345:AEPW:WEKIWA-7:T.NO.-7::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21619 | 106.52 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21607 | 106.41 | P12:138:AEPW-WERE:NBVILLE4:DEARING4::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21596 | 106.35 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 106.25 | P12:138:AEPW:MOUNDRD4:SHIDLER4::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 106.19 | P23:500:EES-EAI:MABELV:B5918::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 106.19 | P23:500:EES:ISES:B6110::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 106.11 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21561 | 105.71 | P12:345:AEPW:WEKIWA-7:T.NO.-7::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21619 | 105.67 | P12:345:AEPW-OKGE:R.S.S.-7:PECANCK7::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21607 | 105.56 | P12:138:AEPW-WERE:NBVILLE4:DEARING4::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21596 | 105.5 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 105.4 | P12:138:AEPW:MOUNDRD4:SHIDLER4::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 105.35 | P23:500:EES-EAI:MABELV:B5918::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21582 | 105.34 | P23:500:EES:ISES:B6110::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 105.26 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21583 | 104.63 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.62 | P13:138-24:AEPW:TURK 4:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21647 | 104.6 | P12:345:AEPW:R.S.S.-7:COGENT7::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.58 | P11:24:AEPW:TURKCOAL:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21583 | 103.76 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.76 | P13:138-24:AEPW:TURK 4:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21647 | 103.73 | P12:345:AEPW:R.S.S.-7:COGENT7::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.71 | P11:24:AEPW:TURKCOAL:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21914 | 113.83 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21914 | 113.83 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21914 | 113.01 | P23:345:AEPW:TULSA NORTH CB 3413A NBTB:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21914 | 113.01 | P42:345:AEPW:TULSA NORTH CB 3413A NBTB+FAULT:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21875 | 112.66 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21875 | 112.66 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21875 | 111.84 | P23:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21875 | 111.84 | P42:345:GRDA:CLEVLND CB13280:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.35755 | 111.18 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR0710:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22835 | 110.96 | P12:345:OKGE:BKRBKR0432:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21884 | 110.66 | P23:345:AEPW:TULSA NORTH CB 3421A NBTB:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2188 | 110.67 | P12:345:GRDA:T.NO.--7-CLEVLND7:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.35755 | 110.34 | P12:138:OKGE-WFEC-OMPA-WERE:BKRBKR0710:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22835 | 110.12 | P12:345:OKGE:BKRBKR0432:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2188 | 109.84 | P12:345:GRDA:T.NO.--7-CLEVLND7:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21884 | 109.82 | P23:345:AEPW:TULSA NORTH CB 3421A NBTB:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21717 | 109.64 | P12:345:OKGE:BKRBKR0240:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.24933 | 109.63 | P12:345:OKGE:BKRBKR0442:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21717 | 108.79 | P12:345:OKGE:BKRBKR0240:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.24933 | 108.78 | P12:345:OKGE:BKRBKR0442:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 108.42 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 108.42 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 107.6 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 107.6 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21657 | 107.58 | P12:345:OKGE:BKRBKR0241:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21686 | 107.18 | P42:345:AEPW:WEKIWA CB 3417A NBTB+FAULT:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21686 | 107.18 | P23:345:AEPW:WEKIWA CB 3417A NBTB:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21618 | 107.17 | P12:138:OKGE:BKRBKR0830:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21572 | 107.14 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21572 | 107.14 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21841 | 106.88 | P12:138:OKGE:BKRBKR0370:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22256 | 106.85 | P12:138:OKGE-AEPW:BKRBKR0170:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21657 | 106.73 | P12:345:OKGE:BKRBKR0241:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21686 | 106.33 | P42:345:AEPW:WEKIWA CB 3417A NBTB+FAULT:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21686 | 106.33 | P23:345:AEPW:WEKIWA CB 3417A NBTB:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21572 | 106.31 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21572 | 106.31 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21618 | 106.31 | P12:138:OKGE:BKRBKR0830:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21841 | 106.02 | P12:138:OKGE:BKRBKR0370:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22256 | 106 | P12:138:OKGE-AEPW:BKRBKR0170:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 119.44 | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 119.44 | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 118.66 | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 118.66 | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 118.06 | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 117.27 | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 115.95 | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 115.16 | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 114.58 | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 113.76 | P42:345:OKGE:SB_RARD7381:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2292 | 113.57 | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2292 | 112.75 | P42:345:OKGE:SB_SOER7383:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21737 | 111.7 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 111.19 | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21753 | 110.97 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21737 | 110.77 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 110.45 | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 110.45 | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 110.36 | P42:345:OKGE:SB_RARD7313:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21753 | 110.11 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 109.62 | P12:345:OKGE:BKRBKR3571:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 109.61 | P42:345:OKGE:SB_RARD7383:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21717 | 109 | P42:345:OKGE:SB_MICO7312:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21549 | 108.49 | P12:138:OKGE:BKRBKR3380:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21549 | 108.49 | P13:138:OKGE:BKRBKR3382:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21642 | 108.27 | P42:345:OKGE:SB_SEOL7385:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22489 | 108.13 | P13:138:OKGE:BKRBKR_3W083:::HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21717 | 108.11 | P42:345:OKGE:SB_MICO7312:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21636 | 107.65 | P42:345:OKGE:SB_ARIA7381:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21636 | 107.65 | P12:345:OKGE:BKRBKR3490:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21549 | 107.63 | P12:138:OKGE:BKRBKR3380:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21549 | 107.63 | P13:138:OKGE:BKRBKR3382:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21642 | 107.43 | P42:345:OKGE:SB_SEOL7385:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22489 | 107.28 | P13:138:OKGE:BKRBKR_3W083:::HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21636 | 106.8 | P42:345:OKGE:SB_ARIA7381:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21636 | 106.8 | P12:345:OKGE:BKRBKR3490:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 194 | 222 | 0.20032 | 103.55 | P13:138:OKGE:BKRBKR_3W080:::HV: | TDF Impact | Rebuild the MIDLTNT4 to CRESWLN4 138kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.81 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.95 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 112.86 | P12:138:WERE:CRSW-OGE-138:HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 112.03 | P12:138:WERE:CRSW-OGE-138:HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21591 | 108.65 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.23564 | 108.31 | P12:138:WERE:CRSW-SUMN-138:HV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21591 | 107.83 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21579 | 107.73 | P23:345:WERE:WOLF-345-50:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21675 | 107.69 | P12:345:WERE:BENT-ROSE-345:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 107.65 | P11:345:WERE:WOLFU1-GEN:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.23564 | 107.46 | P12:138:WERE:CRSW-SUMN-138:HV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 107.21 | P51:25:WERE:WOLFCRK7:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21521 | 107.05 | P23:345:WERE:BUFF-345-534:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21521 | 107.05 | P23:345:WERE:BUFF-345-543:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2165 | 106.91 | P12:138:WFEC:MOORLND_OGEWDWRD:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21579 | 106.89 | P23:345:WERE:WOLF-345-50:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21525 | 106.89 | P12:345:PWT:BUFF-THIS-345-1:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21525 | 106.89 | P12:345:PWT:BUFF-THIS-345-2:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21675 | 106.84 | P12:345:WERE:BENT-ROSE-345:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.8 | P11:345:WERE:WOLFU1-GEN:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21598 | 106.43 | P23:345:AECI:7BLACKBERRY:650::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 106.38 | P51:25:WERE:WOLFCRK7:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21521 | 106.21 | P23:345:WERE:BUFF-345-543:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21521 | 106.21 | P23:345:WERE:BUFF-345-534:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2165 | 106.05 | P12:138:WFEC:MOORLND_OGEWDWRD:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21525 | 106.05 | P12:345:PWT:BUFF-THIS-345-1:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21525 | 106.05 | P12:345:PWT:BUFF-THIS-345-2:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.77 | P23:345:KCPL-WERE:237LACYGNE-R1-6:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21598 | 105.59 | P23:345:AECI:7BLACKBERRY:650::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21611 | 104.86 | P12:138:WFEC:WASHITA_BLCANYON:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21542 | 104.84 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21564 | 104.79 | P23:345:KCPL-WERE:239LACYGNE-R9-10:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21856 | 104.79 | P12:138:WFEC:DOVER_OGEHENN:::: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21565 | 104.76 | P23:345:KCPL-WERE:241WGARDNER-R12-13:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21565 | 104.76 | P12:345:WERE:SWIS-WGAR-345:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21611 | 103.99 | P12:138:WFEC:WASHITA_BLCANYON:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21542 | 103.98 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21564 | 103.94 | P23:345:KCPL-WERE:239LACYGNE-R9-10:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21856 | 103.93 | P12:138:WFEC:DOVER_OGEHENN:::: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21565 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 107.73 | GEN532751 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 107.25 | P12:345:SPS:JXX:1:SIDWNDER_GAINES___:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.89 | GEN532751 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.38 | P12:345:SPS:JXX:1:SIDWNDER_GAINES___:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.37 | GEN640009 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.29 | GEN527003 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.09 | GEN530690 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.08 | GEN532653 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.52 | GEN640009 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.42 | GEN527003 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.24 | GEN530690 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.24 | GEN532653 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.83 | GEN515040 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.83 | GEN515903 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.81 | GEN514999 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | GEN515000 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.79 | GEN515587 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | GEN514998 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | GEN515651 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | GEN515652 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.65 | GEN515882 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.65 | GEN514940 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.58 | GEN509416 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.52 | GEN515883 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.49 | GEN515900 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.49 | GEN515902 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.96 | GEN515040 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.96 | GEN515903 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.94 | GEN514999 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.94 | GEN515000 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.93 | GEN515587 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | GEN515651 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | GEN515652 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | GEN514998 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.8 | GEN515882 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.79 | GEN514940 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.71 | GEN509416 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.67 | GEN515883 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.63 | GEN515900 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.62 | GEN515902 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 107.73 | GEN532751 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.89 | GEN532751 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.09 | GEN530690 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.08 | GEN532653 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.24 | GEN530690 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.24 | GEN532653 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.83 | GEN515040 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.83 | GEN515903 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.82 | GEN-2021-025_POI_520999_Generator_outage | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.81 | GEN514999 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | GEN515000 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | GEN-2024-345_POI_510380_Generator_outage | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | GEN-2024-308_POI_786210_Generator_outage | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.79 | GEN515587 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.75 | GEN-2014-056_GEN-2015-057_POI_514801_Generator_outage | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | GEN514998 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | GEN515651 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | GEN515652 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.65 | GEN515882 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.65 | GEN514940 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.63 | GEN-2024-344_POI_787290_Generator_outage | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.58 | GEN509416 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.52 | GEN515883 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.96 | GEN515040 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.96 | GEN515903 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.95 | GEN-2021-025_POI_520999_Generator_outage | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.94 | GEN514999 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.94 | GEN515000 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.94 | GEN-2024-345_POI_510380_Generator_outage | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.93 | GEN-2024-308_POI_786210_Generator_outage | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.93 | GEN515587 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.88 | GEN-2014-056_GEN-2015-057_POI_514801_Generator_outage | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | GEN515651 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | GEN515652 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | GEN514998 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.8 | GEN515882 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.79 | GEN514940 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.76 | GEN-2024-344_POI_787290_Generator_outage | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.71 | GEN509416 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.67 | GEN515883 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.6 | P23:345:KCPL:LACYGNE-R4-5:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.6 | P23:345:KCPL-WERE:236LACYGNE-R4-6:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.6 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.37 | P55:345:XEL:MNN1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.37 | GEN640009 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.29 | GEN527003 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.76 | P23:345:KCPL:LACYGNE-R4-5:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.76 | P23:345:KCPL-WERE:236LACYGNE-R4-6:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.76 | P23:345:KCPL-WERE:236LACYGNE-R4-6:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.53 | P55:345:XEL:MNN1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.52 | GEN640009 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.42 | GEN527003 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 104.64 | P23:345:KCPL-WERE:238LACYGNE-R4-9:EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 104.64 | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 103.78 | P23:345:KCPL-WERE:238LACYGNE-R4-9:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 103.78 | P23:345:KCPL-WERE:238LACYGNE-R4-9:::EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21078 | 110.44 | 509916 ANTHEM9 765 515049 SEMINOLE9 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21815 | 109.89 | 509755 WEKIWA-7 345 784020 G24-235-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21078 | 109.69 | 509916 ANTHEM9 765 515049 SEMINOLE9 765 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21649 | 109.41 | 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21649 | 109.38 | 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21815 | 109.06 | 509755 WEKIWA-7 345 784020 G24-235-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21649 | 108.55 | 509852 T.NO.--7 345 782100 G24-171-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21649 | 108.52 | 509915 ANTHEM7 345 782100 G24-171-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 108.42 | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 107.6 | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22256 | 106.76 | 510376 WEBBTAP4 138 514743 OSAGE 4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21598 | 106.59 | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21605 | 106.53 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22256 | 106.49 | 510376 WEBBTAP4 138 510403 SHIDLER4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.24 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.23 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 106.22 | 510382 WPAWHSK4 138 510403 SHIDLER4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 106.22 | 510382 WPAWHSK4 138 510412 WESTERNWALL4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 106.19 | 510383 DOMES 4 138 510412 WESTERNWALL4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 106.18 | 510383 DOMES 4 138 510435 ELIZACK4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 106.09 | 510395 MOUNDRD4 138 510435 ELIZACK4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21606 | 106.08 | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22256 | 105.91 | 510376 WEBBTAP4 138 514743 OSAGE 4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21598 | 105.74 | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21605 | 105.69 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.22256 | 105.64 | 510376 WEBBTAP4 138 510403 SHIDLER4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.39 | 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.38 | 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 105.37 | 510382 WPAWHSK4 138 510403 SHIDLER4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 105.37 | 510382 WPAWHSK4 138 510412 WESTERNWALL4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 105.34 | 510383 DOMES 4 138 510412 WESTERNWALL4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 105.32 | 510383 DOMES 4 138 510435 ELIZACK4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21831 | 105.24 | 510395 MOUNDRD4 138 510435 ELIZACK4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21606 | 105.23 | 510422 COFFEYT4 138 787350 G24-346-TAP 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.83 | 510380 DELWARE7 345 787321 GEN-2024-345 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.96 | 510380 DELWARE7 345 787321 GEN-2024-345 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21534 | 103.83 | 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21534 | 102.95 | 509915 ANTHEM7 345 785790 G24-294-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 100.78 | 509782 R.S.S.-7 345 588040 G16133G16146 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 123.32 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 122.58 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21825 | 112.57 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21825 | 111.75 | 512694 CLEVLND7 345 560056 G15066_T 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21649 | 110.57 | 514812 MINCO 9 765 526001 CRDRW9 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21825 | 110.56 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21649 | 109.81 | 514812 MINCO 9 765 526001 CRDRW9 765 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21825 | 109.73 | 514803 SOONER 7 345 560056 G15066_T 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 108.71 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.35341 | 108.84 | 514757 CHIKASI4 138 514760 KILDARE4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 108.63 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 108.6 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 108.54 | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21815 | 108.15 | 514803 SOONER 7 345 784020 G24-235-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 107.86 | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.35341 | 107.99 | 514757 CHIKASI4 138 514760 KILDARE4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 107.79 | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 107.75 | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.25625 | 107.69 | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21568 | 107.32 | 514812 MINCO 9 765 515049 SEMINOLE9 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21815 | 107.31 | 514803 SOONER 7 345 784020 G24-235-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21612 | 107.28 | 515852 DGRASSE7 345 539801 THISTLE7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21848 | 106.87 | 515011 STILWTR4 138 515447 MORISNT4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21568 | 106.49 | 514812 MINCO 9 765 515049 SEMINOLE9 765 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21612 | 106.45 | 515852 DGRASSE7 345 539801 THISTLE7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.34252 | 106.45 | 515509 SNCBLKT2 69.0 515528 NARDINS2 69.0 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.34252 | 106.45 | 514756 CHIKASI2 69.0 515509 SNCBLKT2 69.0 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.27 | 511584 O.K.U.2-7 345 525839 G17-151TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.27 | 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.24 | 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 106.16 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21848 | 106.01 | 515011 STILWTR4 138 515447 MORISNT4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.34252 | 105.59 | 515509 SNCBLKT2 69.0 515528 NARDINS2 69.0 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.34252 | 105.59 | 514756 CHIKASI2 69.0 515509 SNCBLKT2 69.0 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.42 | 511584 O.K.U.2-7 345 525839 G17-151TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.41 | 511468 L.E.S.-7 345 783840 G24-229-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.38 | 511607 O.K.U.3-7 345 783840 G24-229-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2158 | 105.32 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21579 | 106.51 | 525839 G17-151TAP 345 526000 CRWFSHDRW7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21606 | 106.27 | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21579 | 105.66 | 525839 G17-151TAP 345 526000 CRWFSHDRW7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21606 | 105.41 | 520999 MOORLND4 138 786210 G24-308-TAP 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21611 | 104.86 | 521089 WASHITA4 138 521103 SLKHILLS 4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21581 | 104.84 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.82 | 520999 MOORLND4 138 765530 GEN-2021-025 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21566 | 104.72 | 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21552 | 104.35 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21611 | 103.99 | 521089 WASHITA4 138 521103 SLKHILLS 4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.95 | 520999 MOORLND4 138 765530 GEN-2021-025 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21566 | 103.87 | 530583 POSTROCK7 345 777450 G24-016-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21552 | 103.55 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 123.3 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21847 | 122.55 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 109.36 | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21616 | 108.55 | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.23564 | 108.31 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.23564 | 108.28 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.23564 | 107.47 | 532981 CRESWLN4 138 532982 OXFORD 4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.23564 | 107.44 | 532982 OXFORD 4 138 532984 SUMNER 4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.64 | 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.61 | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.51 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21604 | 106.25 | 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 106.25 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21877 | 106.09 | 532984 SUMNER 4 138 533063 SC10BEL4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21877 | 106.08 | 533007 MULVANE 4 138 533063 SC10BEL4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.79 | 532793 NEOSHO 7 345 779250 G24-076-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.77 | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.65 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21604 | 105.41 | 532768 EMPEC 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21578 | 105.4 | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21877 | 105.24 | 532984 SUMNER 4 138 533063 SC10BEL4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21877 | 105.23 | 533007 MULVANE 4 138 533063 SC10BEL4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.85 | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.83 | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.83 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.75 | 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.7 | 532773 SUMMIT 7 345 539863 CIRRUS7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 104.64 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 104.64 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21545 | 104.61 | 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21546 | 104.56 | 533047 GILL 4 138 771260 G22-214-TAP 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 103.99 | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 103.98 | 532791 BENTON 7 345 766141 G21-096-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 103.97 | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 103.88 | 539805 ELMCREEK7 345 539863 CIRRUS7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 103.84 | 532773 SUMMIT 7 345 539863 CIRRUS7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 103.79 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21559 | 103.79 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21545 | 103.75 | 539805 ELMCREEK7 345 785610 G24-288-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21546 | 103.71 | 533047 GILL 4 138 771260 G22-214-TAP 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21566 | 104.73 | 640527 MACON 3 345 777450 G24-016-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21566 | 104.71 | 640065 AXTELL 3 345 640527 MACON 3 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.7 | 588046 G16133_345CS 345 588060 ZONE-2 SUB 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.64 | 588046 G16133_345CS 345 588080 ZONE-4 SUB 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.64 | 588046 G16133_345CS 345 588090 ZONE-5 SUB 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.64 | 588046 G16133_345CS 345 588100 ZONE-6 SUB 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21545 | 104.62 | 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.58 | 588046 G16133_345CS 345 588050 ZONE-1 SUB 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21566 | 103.88 | 640527 MACON 3 345 777450 G24-016-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21566 | 103.86 | 640065 AXTELL 3 345 640527 MACON 3 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.83 | 588046 G16133_345CS 345 588060 ZONE-2 SUB 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.77 | 588046 G16133_345CS 345 588080 ZONE-4 SUB 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.77 | 588046 G16133_345CS 345 588090 ZONE-5 SUB 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.77 | 588046 G16133_345CS 345 588100 ZONE-6 SUB 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21545 | 103.75 | 640600 DAYKIN3 345 785610 G24-288-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.71 | 588046 G16133_345CS 345 588050 ZONE-1 SUB 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.67 | 560056 G15066_T 345 563020 G15066_1 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 102.8 | 560056 G15066_T 345 563020 G15066_1 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 100.76 | 588042 G16133_765R1 765 588043 G16133_765R2 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 100.76 | 588041 G16133_765TN 765 588042 G16133_765R1 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 100.73 | 588043 G16133_765R2 765 588044 G16133_765R3 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 100.68 | 588044 G16133_765R3 765 588045 G16133_765CS 765 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 106.62 | 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21598 | 106.58 | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2161 | 105.78 | 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21598 | 105.74 | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.85 | 780720 G24-125-TAP 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | 786210 G24-308-TAP 138 786211 GEN-2024-308 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.67 | 787290 G24-344-TAP 345 787291 GEN-2024-344 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21567 | 104.65 | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2155 | 104.49 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 103.99 | 780720 G24-125-TAP 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.93 | 786210 G24-308-TAP 138 786211 GEN-2024-308 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.9 | 784020 G24-235-TAP 345 784021 GEN-2024-235 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21534 | 103.86 | 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.8 | 787290 G24-344-TAP 345 787291 GEN-2024-344 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21567 | 103.78 | 509915 ANTHEM7 345 510442 GUAVA 4 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2155 | 103.63 | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.46 | 900002 TRAVERSE2 345 900003 TRAVERSE3 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.03 | 784020 G24-235-TAP 345 784021 GEN-2024-235 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21534 | 102.98 | 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 102.59 | 900002 TRAVERSE2 345 900003 TRAVERSE3 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 101.46 | 900001 TRAVERSE1 345 900002 TRAVERSE2 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 100.57 | 900001 TRAVERSE1 345 900002 TRAVERSE2 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21528 | 109.59 | 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21528 | 109.59 | 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21528 | 108.7 | 515378 WWARD9 765 515375 WWRDEHV7 345 2 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21528 | 108.7 | 515378 WWARD9 765 515375 WWRDEHV7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21556 | 106.35 | 515049 SEMINOLE9 765 515045 SEMINOL7 345 2 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21556 | 106.35 | 515049 SEMINOLE9 765 515045 SEMINOL7 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.29 | 527000 GAINES_PLNT7 345 527003 GAINES_GEN_3 18.0 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 106.19 | 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21556 | 105.48 | 515049 SEMINOLE9 765 515045 SEMINOL7 345 2 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21556 | 105.48 | 515049 SEMINOLE9 765 515045 SEMINOL7 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.42 | 527000 GAINES_PLNT7 345 527003 GAINES_GEN_3 18.0 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 105.34 | 629074 ARNOLD1G 22.0 631088 ARNOLD 5 161 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | 515585 MAMTHPW7 345 3WXFMR 524:MMTHPLWB1 2 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.8 | 515582 SLNGWND7 345 3WXFMR 524:SILWINDB1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | 514825 KAYWIND7 345 3WXFMR 524:KAYWINDB1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.73 | 514825 KAYWIND7 345 3WXFMR 524:KAYWINDB2 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.68 | 515877 REDDIRT7 345 3WXFMR REDDIRWDB1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.61 | 516066 FRNT2WD7 345 3WXFMR 524:T1 _5 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.6 | 516066 FRNT2WD7 345 3WXFMR 524:T2 _3 _2 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21679 | 104.55 | 515877 REDDIRT7 345 3WXFMR REDDIRWDB2 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.53 | 515939 MNCWND47 345 3WXFMR 524:MINCO4MPT1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.48 | 515605 CANADN7 345 3WXFMR 524:BANK 1 _6 _1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.48 | 515605 CANADN7 345 3WXFMR 524:BANK 2 _2 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.48 | 515688 FRNTWND7 345 3WXFMR FRNTWNDB1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.11 | 516100 HORIZON4 138 3WXFMR HORIZON4 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.01 | 515444 MCNOWND7 345 3WXFMR 524:MINCO 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.93 | 515585 MAMTHPW7 345 3WXFMR 524:MMTHPLWB1 2 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.93 | 515582 SLNGWND7 345 3WXFMR 524:SILWINDB1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.91 | 587481 G16-071XFMR1 34.5 587480 GEN-2016-071 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | 514825 KAYWIND7 345 3WXFMR 524:KAYWINDB1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.87 | 514825 KAYWIND7 345 3WXFMR 524:KAYWINDB2 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.82 | 515877 REDDIRT7 345 3WXFMR REDDIRWDB1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.74 | 516066 FRNT2WD7 345 3WXFMR 524:T1 _5 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.74 | 516066 FRNT2WD7 345 3WXFMR 524:T2 _3 _2 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21679 | 103.7 | 515877 REDDIRT7 345 3WXFMR REDDIRWDB2 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.65 | 515939 MNCWND47 345 3WXFMR 524:MINCO4MPT1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.62 | 515605 CANADN7 345 3WXFMR 524:BANK 1 _6 _1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.61 | 515605 CANADN7 345 3WXFMR 524:BANK 2 _2 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.61 | 515688 FRNTWND7 345 3WXFMR FRNTWNDB1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.24 | 516100 HORIZON4 138 3WXFMR HORIZON4 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.84 | 936200 ARMADILLO_HV 138 3WXFMR ARMADILLO_T1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.82 | 765534 G21-025-XFM1 34.5 765530 GEN-2021-025 138 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.68 | 784021 GEN-2024-235 345 3WXFMR GEN-2024-235 1_Dup1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.68 | 784021 GEN-2024-235 345 3WXFMR GEN-2024-235 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.66 | 787291 GEN-2024-344 345 787292 G24-344XFMR1 34.5 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.55 | 900001 TRAVERSE1 345 3WXFMR 0 _4 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.54 | 900003 TRAVERSE3 345 3WXFMR 0 _7 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.49 | 900001 TRAVERSE1 345 3WXFMR 0 _3 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.48 | 914715 SKELETON__HV 345 3WXFMR SKELETON__T1 _1 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.47 | 900002 TRAVERSE2 345 3WXFMR 0 _8 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.43 | 900002 TRAVERSE2 345 3WXFMR 0 _5 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.41 | 760053 G17-133-XFM1 34.5 760032 GEN-2017-133 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.38 | 900003 TRAVERSE3 345 3WXFMR 0 _6 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 104.14 | 760074 G17-134-XFM1 34.5 760032 GEN-2017-133 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.98 | 936200 ARMADILLO_HV 138 3WXFMR ARMADILLO_T1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.95 | 765534 G21-025-XFM1 34.5 765530 GEN-2021-025 138 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.91 | 760095 G17-137-XFM1 34.5 760032 GEN-2017-133 345 1 | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.82 | 784021 GEN-2024-235 345 3WXFMR GEN-2024-235 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.82 | 784021 GEN-2024-235 345 3WXFMR GEN-2024-235 1_Dup1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.8 | 787291 GEN-2024-344 345 787292 G24-344XFMR1 34.5 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.69 | 900001 TRAVERSE1 345 3WXFMR 0 _4 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.68 | 900003 TRAVERSE3 345 3WXFMR 0 _7 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.63 | 900001 TRAVERSE1 345 3WXFMR 0 _3 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.62 | 914715 SKELETON__HV 345 3WXFMR SKELETON__T1 _1 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.61 | 900002 TRAVERSE2 345 3WXFMR 0 _8 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.57 | 900002 TRAVERSE2 345 3WXFMR 0 _5 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.54 | 760053 G17-133-XFM1 34.5 760032 GEN-2017-133 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.51 | 900003 TRAVERSE3 345 3WXFMR 0 _6 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.28 | 760074 G17-134-XFM1 34.5 760032 GEN-2017-133 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.21577 | 103.04 | 760095 G17-137-XFM1 34.5 760032 GEN-2017-133 345 1 | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR12 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.08349 | 121.5 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29L | GEN-2026-PR12 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.2154 | 104.01 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Non-Converged | GEN-2026-PR12 PSIS | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR12 PSIS | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR12 PSIS | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR12 PSIS | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR12 PSIS | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR12 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR12 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 830 | 830 | 0.03016 | 111.81 | System Intact | TDF Impact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
Thermal | GEN-2026-PR12 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR12 | TO->FROM | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 830 | 830 | 0.0317 | 127.13 | System Intact | TDF Impact | Rebuild the HOYT 7 to JEC N 7 345kV Line 1
Non-Converged | GEN-2026-PR12 PSIS CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR12 PSIS CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR12 PSIS CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR12 PSIS CF | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR12 PSIS CF | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR12 PSIS CF | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR12 PSIS | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS CF | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR12 PSIS CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 b.3. WEBBTAP4 (510376) 138.0 kV to SHIDWFC4 (520442) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 b.2. 4CORNER2 (514736) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.3. KREMLNT2 (515501) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.4. HILLSDT2 (515638) 69.0 kV to HILLSDL2 (515639) 69.0 kV Transmission Circuit #1 b.5. KREMLIN2 (514717) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.6. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.7. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.8. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 b.3. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.4. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 b.5. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.3. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on OMWW 69.000 (529249) 69 kV Bus a. Apply fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to CONORTH4 (514753) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on CONORTH4 138.00 (514753) 138 kV Bus a. Apply fault at the CONORTH4 138.00 (514753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.3. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 b.4. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.5. KAYCOOP2 (514754) 69.0 kV to BLACKWE2 (520837) 69.0 kV Transmission Circuit #1 b.6. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.7. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.8. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.9. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.10. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.11. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G16-071-GE230 (587483), G16-071-GE250 (587486) | Disabling the voltage protection results in tripping of the same models due to UDM's frequency protection. The violation is observed in base case as well and there is no further impact to system stability.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on BLKWLWD2 69.000 (515478) 69 kV Bus a. Apply fault at the BLKWLWD2 69.000 (515478) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on SINCBLK2 69.000 (514728) 69 kV Bus a. Apply fault at the SINCBLK2 69.000 (514728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CHERKPL2 (514746) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to BRAMAN 2 (520871) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on KAYCOOP2 69.000 (514754) 69 kV Bus a. Apply fault at the KAYCOOP2 69.000 (514754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWKIRK4 138.00 (514759) 138 kV Bus a. Apply fault at the NEWKIRK4 138.00 (514759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NWKRKAT4 138.00 (514764) 138 kV Bus a. Apply fault at the NWKRKAT4 138.00 (514764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NARDINS2 69.000 (515528) 69 kV Bus a. Apply fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on OMHUFFYT 69.000 (529242) 69 kV Bus a. Apply fault at the OMHUFFYT 69.000 (529242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on OMNEASTT 69.000 (529244) 69 kV Bus a. Apply fault at the OMNEASTT 69.000 (529244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNEASTT (529244) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OMGONTER 69.000 (529245) 69 kV Bus a. Apply fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMMCCORD (529247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on OMMCCORD 69.000 (529247) 69 kV Bus a. Apply fault at the OMMCCORD 69.000 (529247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMCCORD (529247) 69.0 kV to OMKAWH (529252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on OMPECANT 69.000 (529248) 69 kV Bus a. Apply fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 4.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 0.75 cycle and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.4. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.4. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. CHIKASI4 (514757) 138.0 kV to CHIKASI2 (514756) 69.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.6. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.6. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.7. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.7. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.8. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.9. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.11. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.4. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on 3SANDS 2 69.000 (514762) 69 kV Bus a. Apply Fault at the 3SANDS 2 69.000 (514762) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.2. NUMAOGE2 (514740) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 b.2. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. CHERPLT2 (514745) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NEWKRKT2 69.000 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 69.000 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to BRMAN 2 (514750) 69.0 kV Transmission Circuit #1 b.2. NEWKRKT2 (514751) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.2. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CONBLKT2 69.000 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 69.000 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 b.2. CONBLKT2 (515402) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. NARDINS2 (515528) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to CLYDE 2 (514719) 69.0 kV Transmission Circuit #1 b.2. GRANTCO2 (515547) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OMMORANT 69.000 (529241) 69 kV Bus a. Apply Fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OMGONTER 69.000 (529245) 69 kV Bus a. Apply Fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 b.2. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OMKAWS 69.000 (529246) 69 kV Bus a. Apply Fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMKAWS (529246) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OMPECANT 69.000 (529248) 69 kV Bus a. Apply Fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OMWW 69.000 (529249) 69 kV Bus a. Apply Fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMWW (529249) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SINCBLK2 (514728) 69 kV Bus a. Apply Fault at the SINCBLK2 (514728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SINCBLK2 (514728) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on MEDFORD2 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUMAOGE2 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on DEERCK 2 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on OSGE 2 (514742) 69 kV Bus a. Apply Fault at the OSGE 2 (514742) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CHILOCO2 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CHERPLT2 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CHERKPL2 (514746) 69 kV Bus a. Apply Fault at the CHERKPL2 (514746) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERKPL2 (514746) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRMAN 2 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEWKRKT2 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BLACKWL2 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CHIKASI2 (514756) 69 kV Bus a. Apply Fault at the CHIKASI2 (514756) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CHIKASI4 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CONBLKT2 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SNCBLKT2 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on NARDINS2 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GRANTCO2 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NUMA 2 (521013) 69 kV Bus a. Apply Fault at the NUMA 2 (521013) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMA 2 (521013) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on OMMORANT (529241) 69 kV Bus a. Apply Fault at the OMMORANT (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on OMGONTER (529245) 69 kV Bus a. Apply Fault at the OMGONTER (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on OMKAWS (529246) 69 kV Bus a. Apply Fault at the OMKAWS (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on OMPECANT (529248) 69 kV Bus a. Apply Fault at the OMPECANT (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OMWW (529249) 69 kV Bus a. Apply Fault at the OMWW (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OMBLKWL2 (529255) 69 kV Bus a. Apply Fault at the OMBLKWL2 (529255) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMBLKWL2 (529255) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PRSMNG11 (515955) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 b.3. WEBBTAP4 (510376) 138.0 kV to SHIDWFC4 (520442) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 b.2. 4CORNER2 (514736) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.3. KREMLNT2 (515501) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.4. HILLSDT2 (515638) 69.0 kV to HILLSDL2 (515639) 69.0 kV Transmission Circuit #1 b.5. KREMLIN2 (514717) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.6. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.7. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.8. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 b.3. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.4. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 b.5. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.3. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on OMWW 69.000 (529249) 69 kV Bus a. Apply fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to CONORTH4 (514753) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on CONORTH4 138.00 (514753) 138 kV Bus a. Apply fault at the CONORTH4 138.00 (514753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.3. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 b.4. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.5. KAYCOOP2 (514754) 69.0 kV to BLACKWE2 (520837) 69.0 kV Transmission Circuit #1 b.6. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.7. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.8. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.9. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.10. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.11. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G16-071-GE230 (587483), G16-071-GE250 (587486) | Disabling the voltage protection results in tripping of the same models due to UDM's frequency protection. The violation is observed in base case as well and there is no further impact to system stability.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on BLKWLWD2 69.000 (515478) 69 kV Bus a. Apply fault at the BLKWLWD2 69.000 (515478) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on SINCBLK2 69.000 (514728) 69 kV Bus a. Apply fault at the SINCBLK2 69.000 (514728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CHERKPL2 (514746) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to BRAMAN 2 (520871) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on KAYCOOP2 69.000 (514754) 69 kV Bus a. Apply fault at the KAYCOOP2 69.000 (514754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWKIRK4 138.00 (514759) 138 kV Bus a. Apply fault at the NEWKIRK4 138.00 (514759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NWKRKAT4 138.00 (514764) 138 kV Bus a. Apply fault at the NWKRKAT4 138.00 (514764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NARDINS2 69.000 (515528) 69 kV Bus a. Apply fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 4.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on OMHUFFYT 69.000 (529242) 69 kV Bus a. Apply fault at the OMHUFFYT 69.000 (529242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on OMNEASTT 69.000 (529244) 69 kV Bus a. Apply fault at the OMNEASTT 69.000 (529244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNEASTT (529244) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OMGONTER 69.000 (529245) 69 kV Bus a. Apply fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMMCCORD (529247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on OMMCCORD 69.000 (529247) 69 kV Bus a. Apply fault at the OMMCCORD 69.000 (529247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMCCORD (529247) 69.0 kV to OMKAWH (529252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on OMPECANT 69.000 (529248) 69 kV Bus a. Apply fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.1. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.1. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 1.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.4. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.4. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. CHIKASI4 (514757) 138.0 kV to CHIKASI2 (514756) 69.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.6. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.6. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.7. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.7. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.8. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.9. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.11. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.4. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on 3SANDS 2 69.000 (514762) 69 kV Bus a. Apply Fault at the 3SANDS 2 69.000 (514762) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.2. NUMAOGE2 (514740) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 b.2. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. CHERPLT2 (514745) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NEWKRKT2 69.000 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 69.000 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to BRMAN 2 (514750) 69.0 kV Transmission Circuit #1 b.2. NEWKRKT2 (514751) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.2. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CONBLKT2 69.000 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 69.000 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 b.2. CONBLKT2 (515402) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. NARDINS2 (515528) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to CLYDE 2 (514719) 69.0 kV Transmission Circuit #1 b.2. GRANTCO2 (515547) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OMMORANT 69.000 (529241) 69 kV Bus a. Apply Fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OMGONTER 69.000 (529245) 69 kV Bus a. Apply Fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 b.2. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OMKAWS 69.000 (529246) 69 kV Bus a. Apply Fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMKAWS (529246) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OMPECANT 69.000 (529248) 69 kV Bus a. Apply Fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OMWW 69.000 (529249) 69 kV Bus a. Apply Fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMWW (529249) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SINCBLK2 (514728) 69 kV Bus a. Apply Fault at the SINCBLK2 (514728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SINCBLK2 (514728) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on MEDFORD2 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUMAOGE2 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on DEERCK 2 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on OSGE 2 (514742) 69 kV Bus a. Apply Fault at the OSGE 2 (514742) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CHILOCO2 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CHERPLT2 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CHERKPL2 (514746) 69 kV Bus a. Apply Fault at the CHERKPL2 (514746) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERKPL2 (514746) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRMAN 2 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEWKRKT2 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BLACKWL2 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CHIKASI2 (514756) 69 kV Bus a. Apply Fault at the CHIKASI2 (514756) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CHIKASI4 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CONBLKT2 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SNCBLKT2 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on NARDINS2 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GRANTCO2 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NUMA 2 (521013) 69 kV Bus a. Apply Fault at the NUMA 2 (521013) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMA 2 (521013) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on OMMORANT (529241) 69 kV Bus a. Apply Fault at the OMMORANT (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on OMGONTER (529245) 69 kV Bus a. Apply Fault at the OMGONTER (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on OMKAWS (529246) 69 kV Bus a. Apply Fault at the OMKAWS (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on OMPECANT (529248) 69 kV Bus a. Apply Fault at the OMPECANT (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OMWW (529249) 69 kV Bus a. Apply Fault at the OMWW (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OMBLKWL2 (529255) 69 kV Bus a. Apply Fault at the OMBLKWL2 (529255) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMBLKWL2 (529255) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 b.3. WEBBTAP4 (510376) 138.0 kV to SHIDWFC4 (520442) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 b.2. 4CORNER2 (514736) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.3. KREMLNT2 (515501) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.4. HILLSDT2 (515638) 69.0 kV to HILLSDL2 (515639) 69.0 kV Transmission Circuit #1 b.5. KREMLIN2 (514717) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.6. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.7. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.8. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 b.3. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.4. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 b.5. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.3. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on OMWW 69.000 (529249) 69 kV Bus a. Apply fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to CONORTH4 (514753) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on CONORTH4 138.00 (514753) 138 kV Bus a. Apply fault at the CONORTH4 138.00 (514753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.3. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 b.4. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.5. KAYCOOP2 (514754) 69.0 kV to BLACKWE2 (520837) 69.0 kV Transmission Circuit #1 b.6. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.7. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.8. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.9. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.10. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.11. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on BLKWLWD2 69.000 (515478) 69 kV Bus a. Apply fault at the BLKWLWD2 69.000 (515478) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on SINCBLK2 69.000 (514728) 69 kV Bus a. Apply fault at the SINCBLK2 69.000 (514728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CHERKPL2 (514746) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to BRAMAN 2 (520871) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on KAYCOOP2 69.000 (514754) 69 kV Bus a. Apply fault at the KAYCOOP2 69.000 (514754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWKIRK4 138.00 (514759) 138 kV Bus a. Apply fault at the NEWKIRK4 138.00 (514759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.7. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NWKRKAT4 138.00 (514764) 138 kV Bus a. Apply fault at the NWKRKAT4 138.00 (514764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NARDINS2 69.000 (515528) 69 kV Bus a. Apply fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on OMHUFFYT 69.000 (529242) 69 kV Bus a. Apply fault at the OMHUFFYT 69.000 (529242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on OMNEASTT 69.000 (529244) 69 kV Bus a. Apply fault at the OMNEASTT 69.000 (529244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNEASTT (529244) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OMGONTER 69.000 (529245) 69 kV Bus a. Apply fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMMCCORD (529247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on OMMCCORD 69.000 (529247) 69 kV Bus a. Apply fault at the OMMCCORD 69.000 (529247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMCCORD (529247) 69.0 kV to OMKAWH (529252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on OMPECANT 69.000 (529248) 69 kV Bus a. Apply fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 4.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 0.5 cycle and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed when clearing the fault. The issue is identified to be due to fault proximity to KAYWNDG1 (515651) and KAYWNDG2 (515652) controllers and proximity of the fault. This was also observed in the base case and the CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.4. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.4. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. CHIKASI4 (514757) 138.0 kV to CHIKASI2 (514756) 69.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.6. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.6. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.7. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.7. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.8. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.9. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.11. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.4. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on 3SANDS 2 69.000 (514762) 69 kV Bus a. Apply Fault at the 3SANDS 2 69.000 (514762) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.2. NUMAOGE2 (514740) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 b.2. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. CHERPLT2 (514745) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NEWKRKT2 69.000 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 69.000 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to BRMAN 2 (514750) 69.0 kV Transmission Circuit #1 b.2. NEWKRKT2 (514751) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.2. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CONBLKT2 69.000 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 69.000 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 b.2. CONBLKT2 (515402) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. NARDINS2 (515528) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to CLYDE 2 (514719) 69.0 kV Transmission Circuit #1 b.2. GRANTCO2 (515547) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OMMORANT 69.000 (529241) 69 kV Bus a. Apply Fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OMGONTER 69.000 (529245) 69 kV Bus a. Apply Fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 b.2. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OMKAWS 69.000 (529246) 69 kV Bus a. Apply Fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMKAWS (529246) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OMPECANT 69.000 (529248) 69 kV Bus a. Apply Fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OMWW 69.000 (529249) 69 kV Bus a. Apply Fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMWW (529249) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SINCBLK2 (514728) 69 kV Bus a. Apply Fault at the SINCBLK2 (514728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SINCBLK2 (514728) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on MEDFORD2 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUMAOGE2 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on DEERCK 2 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on OSGE 2 (514742) 69 kV Bus a. Apply Fault at the OSGE 2 (514742) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CHILOCO2 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CHERPLT2 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CHERKPL2 (514746) 69 kV Bus a. Apply Fault at the CHERKPL2 (514746) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERKPL2 (514746) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRMAN 2 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEWKRKT2 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BLACKWL2 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CHIKASI2 (514756) 69 kV Bus a. Apply Fault at the CHIKASI2 (514756) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CHIKASI4 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CONBLKT2 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SNCBLKT2 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on NARDINS2 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GRANTCO2 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NUMA 2 (521013) 69 kV Bus a. Apply Fault at the NUMA 2 (521013) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMA 2 (521013) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on OMMORANT (529241) 69 kV Bus a. Apply Fault at the OMMORANT (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on OMGONTER (529245) 69 kV Bus a. Apply Fault at the OMGONTER (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on OMKAWS (529246) 69 kV Bus a. Apply Fault at the OMKAWS (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on OMPECANT (529248) 69 kV Bus a. Apply Fault at the OMPECANT (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OMWW (529249) 69 kV Bus a. Apply Fault at the OMWW (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OMBLKWL2 (529255) 69 kV Bus a. Apply Fault at the OMBLKWL2 (529255) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMBLKWL2 (529255) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips PRSMNG11 (515955) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 b.3. WEBBTAP4 (510376) 138.0 kV to SHIDWFC4 (520442) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 b.4. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.5. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.6. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.8. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on MILLERT4 138.00 (514704) 138 kV Bus a. Apply fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.3. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.5. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.6. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 b.2. 4CORNER2 (514736) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.3. KREMLNT2 (515501) 69.0 kV to HILLSDT2 (515638) 69.0 kV Transmission Circuit #1 b.4. HILLSDT2 (515638) 69.0 kV to HILLSDL2 (515639) 69.0 kV Transmission Circuit #1 b.5. KREMLIN2 (514717) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.6. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.7. NE ENID2 (514732) 69.0 kV to KREMLNT2 (515501) 69.0 kV Transmission Circuit #1 b.8. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 b.3. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.4. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 b.5. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.3. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on OMWW 69.000 (529249) 69 kV Bus a. Apply fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to CONORTH4 (514753) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on CONORTH4 138.00 (514753) 138 kV Bus a. Apply fault at the CONORTH4 138.00 (514753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.3. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 b.4. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.5. KAYCOOP2 (514754) 69.0 kV to BLACKWE2 (520837) 69.0 kV Transmission Circuit #1 b.6. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.7. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.8. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.9. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.10. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.11. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashed following the event. Increasing the acceleration factor to 0.7 simulated event successfully. Then observed the voltage protection trips G16-071-GE230 (587483), G16-071-GE250 (587486) | Increased acceleration factor to 0.7. Disabling the voltage protection results in tripping of the same models due to UDM's frequency protection. The violation is observed in base case as well and there is no further impact to system stability.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on BLKWLWD2 69.000 (515478) 69 kV Bus a. Apply fault at the BLKWLWD2 69.000 (515478) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to 4CORNER2 (514736) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on CLYDE 2 69.000 (514719) 69 kV Bus a. Apply fault at the CLYDE 2 69.000 (514719) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on SINCBLK2 69.000 (514728) 69 kV Bus a. Apply fault at the SINCBLK2 69.000 (514728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCBLK2 (514728) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 (514740) 69.0 kV to NUMA 2 (521013) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CHERKPL2 (514746) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMAN 2 (514750) 69.0 kV to BRAMAN 2 (520871) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on TONKAWA2 69.000 (514752) 69 kV Bus a. Apply fault at the TONKAWA2 69.000 (514752) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONKAWA2 (514752) 69.0 kV to OMOWEN 2 (529320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on KAYCOOP2 69.000 (514754) 69 kV Bus a. Apply fault at the KAYCOOP2 69.000 (514754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAYCOOP2 (514754) 69.0 kV to BLACKWL2 (514755) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHIKASI2 69.000 (514756) 69 kV Bus a. Apply fault at the CHIKASI2 69.000 (514756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWKIRK4 138.00 (514759) 138 kV Bus a. Apply fault at the NEWKIRK4 138.00 (514759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on KILDARE4 138.00 (514760) 138 kV Bus a. Apply fault at the KILDARE4 138.00 (514760) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on NWKRKAT4 138.00 (514764) 138 kV Bus a. Apply fault at the NWKRKAT4 138.00 (514764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on MARLNDT4 138.00 (514770) 138 kV Bus a. Apply fault at the MARLNDT4 138.00 (514770) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NARDINS2 69.000 (515528) 69 kV Bus a. Apply fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 4.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on OMHUFFYT 69.000 (529242) 69 kV Bus a. Apply fault at the OMHUFFYT 69.000 (529242) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on OMNWESTT 69.000 (529243) 69 kV Bus a. Apply fault at the OMNWESTT 69.000 (529243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNWESTT (529243) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on OMNEASTT 69.000 (529244) 69 kV Bus a. Apply fault at the OMNEASTT 69.000 (529244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMNEASTT (529244) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OMGONTER 69.000 (529245) 69 kV Bus a. Apply fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMMCCORD (529247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on OMKAWS 69.000 (529246) 69 kV Bus a. Apply fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on OMMCCORD 69.000 (529247) 69 kV Bus a. Apply fault at the OMMCCORD 69.000 (529247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMMCCORD (529247) 69.0 kV to OMKAWH (529252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on OMPECANT 69.000 (529248) 69 kV Bus a. Apply fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.1. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Decrease acceleration factor to 0.1. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on KAYWIND7 345.00 (514825) 345 kV Bus a. Apply fault at the KAYWIND7 345.00 (514825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_053 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_054 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_055 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_056 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_057 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_058 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_059 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_060 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_062 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_063 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_066 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_067 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 1.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case where the same clearing time was seen to be needed. CQ unit did not impact the behavior. | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_070 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to GEN-2023-102 (776821) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_071 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_072 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.4. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.4. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. CHIKASI4 (514757) 138.0 kV to CHIKASI2 (514756) 69.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.6. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.3. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.4. CHIKASI2 (514756) 69.0 kV to OMBLKWL2 (529255) 69.0 kV Transmission Circuit #1 b.5. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.6. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.7. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #4 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.5. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.7. OSAGE 4 (514743) 138.0 kV to OSGE 2 (514742) 69.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.8. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.9. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.11. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.3. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. BLKWLWD2 (515478) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.3. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.4. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on 3SANDS 2 69.000 (514762) 69 kV Bus a. Apply Fault at the 3SANDS 2 69.000 (514762) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 b.2. TONKAWA2 (514752) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MEDFORD2 69.000 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 69.000 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NUMAOGE2 69.000 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 69.000 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 b.2. NUMAOGE2 (514740) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on DEERCK 2 69.000 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 69.000 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. DEERCK 2 (514741) 69.0 kV to NUMAOGE2 (514740) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on CHILOCO2 69.000 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 69.000 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 b.2. CHILOCO2 (514744) 69.0 kV to 3SANDS 2 (514762) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CHERPLT2 69.000 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 69.000 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. CHERPLT2 (514745) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on BRMAN 2 69.000 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 69.000 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 b.2. BRMAN 2 (514750) 69.0 kV to NEWKRKT2 (514751) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NEWKRKT2 69.000 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 69.000 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to BRMAN 2 (514750) 69.0 kV Transmission Circuit #1 b.2. NEWKRKT2 (514751) 69.0 kV to CHILOCO2 (514744) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BLACKWL2 69.000 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 69.000 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to KAYCOOP2 (514754) 69.0 kV Transmission Circuit #1 b.2. BLACKWL2 (514755) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to CHIKASI4 (514757) 138.0 kV to CHIKASI1 (515713) 13.2 kV Three Winding #2 b.2. CHIKASI2 (514756) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CHIKASI4 138.00 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 138.00 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CONBLKT2 69.000 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 69.000 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 b.2. CONBLKT2 (515402) 69.0 kV to CHERPLT2 (514745) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on SNCBLKT2 69.000 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 69.000 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to NARDINS2 (515528) 69.0 kV Transmission Circuit #1 b.2. SNCBLKT2 (515509) 69.0 kV to CHIKASI2 (514756) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NARDINS2 69.000 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to SNCBLKT2 (515509) 69.0 kV Transmission Circuit #1 b.2. NARDINS2 (515528) 69.0 kV to DEERCK 2 (514741) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to CLYDE 2 (514719) 69.0 kV Transmission Circuit #1 b.2. GRANTCO2 (515547) 69.0 kV to MEDFORD2 (514739) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OMMORANT 69.000 (529241) 69 kV Bus a. Apply Fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OMGONTER 69.000 (529245) 69 kV Bus a. Apply Fault at the OMGONTER 69.000 (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to OMNEASTT (529244) 69.0 kV Transmission Circuit #1 b.2. OMGONTER (529245) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OMKAWS 69.000 (529246) 69 kV Bus a. Apply Fault at the OMKAWS 69.000 (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMKAWS (529246) 69.0 kV to OMGONTER (529245) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OMPECANT 69.000 (529248) 69 kV Bus a. Apply Fault at the OMPECANT 69.000 (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to OMKAWS (529246) 69.0 kV Transmission Circuit #1 b.2. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OMWW 69.000 (529249) 69 kV Bus a. Apply Fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.2. OMWW (529249) 69.0 kV to OSGE 2 (514742) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SINCBLK2 (514728) 69 kV Bus a. Apply Fault at the SINCBLK2 (514728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SINCBLK2 (514728) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on MEDFORD2 (514739) 69 kV Bus a. Apply Fault at the MEDFORD2 (514739) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUMAOGE2 (514740) 69 kV Bus a. Apply Fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMAOGE2 (514740) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on DEERCK 2 (514741) 69 kV Bus a. Apply Fault at the DEERCK 2 (514741) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEERCK 2 (514741) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on OSGE 2 (514742) 69 kV Bus a. Apply Fault at the OSGE 2 (514742) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CHILOCO2 (514744) 69 kV Bus a. Apply Fault at the CHILOCO2 (514744) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHILOCO2 (514744) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CHERPLT2 (514745) 69 kV Bus a. Apply Fault at the CHERPLT2 (514745) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERPLT2 (514745) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CHERKPL2 (514746) 69 kV Bus a. Apply Fault at the CHERKPL2 (514746) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERKPL2 (514746) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BRMAN 2 (514750) 69 kV Bus a. Apply Fault at the BRMAN 2 (514750) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMAN 2 (514750) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEWKRKT2 (514751) 69 kV Bus a. Apply Fault at the NEWKRKT2 (514751) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWKRKT2 (514751) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BLACKWL2 (514755) 69 kV Bus a. Apply Fault at the BLACKWL2 (514755) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLACKWL2 (514755) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CHIKASI2 (514756) 69 kV Bus a. Apply Fault at the CHIKASI2 (514756) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI2 (514756) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CHIKASI4 (514757) 138 kV Bus a. Apply Fault at the CHIKASI4 (514757) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CONBLKT2 (515402) 69 kV Bus a. Apply Fault at the CONBLKT2 (515402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONBLKT2 (515402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SNCBLKT2 (515509) 69 kV Bus a. Apply Fault at the SNCBLKT2 (515509) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNCBLKT2 (515509) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on NARDINS2 (515528) 69 kV Bus a. Apply Fault at the NARDINS2 (515528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NARDINS2 (515528) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GRANTCO2 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on NUMA 2 (521013) 69 kV Bus a. Apply Fault at the NUMA 2 (521013) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUMA 2 (521013) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on OMMORANT (529241) 69 kV Bus a. Apply Fault at the OMMORANT (529241) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMMORANT (529241) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on OMGONTER (529245) 69 kV Bus a. Apply Fault at the OMGONTER (529245) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMGONTER (529245) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on OMKAWS (529246) 69 kV Bus a. Apply Fault at the OMKAWS (529246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMKAWS (529246) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on OMPECANT (529248) 69 kV Bus a. Apply Fault at the OMPECANT (529248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMPECANT (529248) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OMWW (529249) 69 kV Bus a. Apply Fault at the OMWW (529249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMWW (529249) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OMBLKWL2 (529255) 69 kV Bus a. Apply Fault at the OMBLKWL2 (529255) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMBLKWL2 (529255) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7ESSEX (300038) 345 kV Bus a. Apply Fault at the 7ESSEX (300038) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.3. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.5. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 b.8. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.9. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.10. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.4. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 b.4. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. BORDER 7 (515458) 345.0 kV to G17-151TAP (525839) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.4. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.4. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.5. FTSMTHW5 (515301) 161.0 kV to Switched Shunt Device #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply Fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to remove bus # b.3. GRVR_COL2 1 (523049) 34.5 kV to remove bus # b.4. GRVR_T2 1 (523048) 34.5 kV to remove bus # b.5. GRVR_TY 1 (523047) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.3. CROCKET7 (509241) 345.0 kV to CROCKET4 (509240) 138.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKET4 (509240) 138.0 kV to GRAPLND4 (509322) 138.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 b.3. 7ROCKYCRK% (334197) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_152 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.3. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.4. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.5. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.6. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips LEBROCS1 (506754), LEBROCG1 (506752), LEBROCG2 (506753) | Protection disabled with no impact on stability
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_153 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.4. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 b.5. LONGWD 7 (508809) 345.0 kV to LONGWD 4 (508808) 138.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_154 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_155 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LIEBERM4 (508806) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.3. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.4. LONGWD 4 (508808) 138.0 kV to G22-038-TAP (767740) 138.0 kV Transmission Circuit #1 b.5. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 b.6. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.7. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.8. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.9. LONGWD 7 (508809) 345.0 kV to GEN-2018-050 (762845) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_156 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_157 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_158 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 b.3. CENTRTN5 (506952) 161.0 kV to SHIPERD5 (506980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 b.4. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.5. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_160 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_161 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENMOTR4 (507732) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.2. POWELL 4 (507748) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.3. S SHV 4 (507755) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.4. SPRIDGE4 (507757) 138.0 kV to SW SHV 4 (507759) 138.0 kV Transmission Circuit #1 b.5. SW SHV 4 (507759) 138.0 kV to LEASIDE 4 (507793) 138.0 kV Transmission Circuit #1 b.6. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 b.7. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.8. DOLHILL7 (500250) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.9. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.10. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G23-059GEN2 (773167) and G23-059GEN3 (773166) | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.3. WILKES 7 (508841) 345.0 kV to GEN-2022-111 (769201) 345.0 kV Transmission Circuit #1 b.4. WILKES 7 (508841) 345.0 kV to WILKES 4 (508840) 138.0 kV to WILKES-1 (508826) 13.2 kV Three Winding #1 b.5. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #1 b.6. WILKES 7 (508841) 345.0 kV to WILKE3-1 (509409) 22.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_164 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_165 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_166 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.3. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.4. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.5. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.6. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_167 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_168 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.4. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 b.5. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.6. O.K.U.-7 (511456) 345.0 kV to Switched Shunt Device #2 b.7. DCEAST (599893) 345.0 kV to ERCOTMAINBUS (599894) 345.0 kV Transmission Circuit #z1 b.8. OKLAUN 7 (599891) 345.0 kV to OKLAUN2 (599892) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.3. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.4. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.7. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.11. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.12. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_170 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.4. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.5. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (534109) 345.0 kV Transmission Circuit #1 b.6. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.8. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 b.9. BUFFALO7 (532782) 345.0 kV to BUFFALO4 (533069) 138.0 kV to BUFFALO11 1 (532820) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_171 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.3. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.4. NEOSHO 7 (532793) 345.0 kV to GEN-2021-006 (765350) 345.0 kV Transmission Circuit #1 b.5. NEOSHO 7 (532793) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.6. NEOSHO 7 (532793) 345.0 kV to N345 3 4 (533023) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.7. NEOSHO 7 (532793) 345.0 kV to N345 4 5 (532939) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_173 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_174 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Decrease acceleration factor to 0.3. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_175 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_177 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_178 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_179 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_181 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_182 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_183 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashed following the event. | Increase acceleration factor to 0.9. Observed no stability issues.
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_184 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_185 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_186 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_187 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_188 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_189 | Single Phase Fault with Stuck Breaker on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTSMITH7 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_191 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_193 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_194 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_195 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_196 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_197 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 4.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 0.75 cycle and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29S | Base | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWKIRK4 138.00 (514759) 138 kV Bus a. Apply fault at the NEWKIRK4 138.00 (514759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on NARDINS2 69.000 (515528) 69 kV Bus a. Apply fault at the NARDINS2 69.000 (515528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NARDINS2 (515528) 69.0 kV to BLACKWELL_HV (915528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 4.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 2.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_039 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 2 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Switched Shunt Device #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_052 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_064 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to DVRSION-WIND (511999) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_065 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_068 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 1.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_069 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashed following the event. This was also observed in the base case and CQ unit did not impact the behavior | Clearing time was reduced to 0.5 cycles and issue is resolved.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P1_REGIONAL_FAULT_073 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Switched Shunt Device #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power oscillations observed at G18-115-GEN10.63 (763321), and G18-115-GEN20.69 (763324). This was also observed in the base case and CQ unit did not impact the behavior. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.
04 SOUTHEAST | PSIS-2026-PR12 | 29W | Base | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Internal UDM voltage protection trips G17-061 (512788). The violation is observed in base case as well and there is no further impact to system stability. | No mitigation required.

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR12 | 04 SOUTHEAST | 915528 | BLACKWELL_HV69.000 | 69 | 4.9725 | 5.1246 | 0.1521
GEN-2026-PR12 | 04 SOUTHEAST | 515478 | BLKWLWD2 69.000 | 69 | 5.1148 | 5.2304 | 0.1156
GEN-2026-PR12 | 04 SOUTHEAST | 515509 | SNCBLKT2 69.000 | 69 | 7.2216 | 7.3263 | 0.1047
GEN-2026-PR12 | 04 SOUTHEAST | 514728 | SINCBLK2 69.000 | 69 | 7.2053 | 7.3095 | 0.1042
GEN-2026-PR12 | 04 SOUTHEAST | 514756 | CHIKASI2 69.000 | 69 | 9.797 | 9.8841 | 0.0871
GEN-2026-PR12 | 04 SOUTHEAST | 514750 | BRMAN 2 69.000 | 69 | 8.2847 | 8.347 | 0.0623
GEN-2026-PR12 | 04 SOUTHEAST | 514755 | BLACKWL2 69.000 | 69 | 8.4733 | 8.534 | 0.0607
GEN-2026-PR12 | 04 SOUTHEAST | 529255 | OMBLKWL2 69.000 | 69 | 8.0246 | 8.083 | 0.0584
GEN-2026-PR12 | 04 SOUTHEAST | 514741 | DEERCK 2 69.000 | 69 | 4.7353 | 4.7881 | 0.0528
GEN-2026-PR12 | 04 SOUTHEAST | 514740 | NUMAOGE2 69.000 | 69 | 4.779 | 4.8237 | 0.0447
GEN-2026-PR12 | 04 SOUTHEAST | 521013 | NUMA 2 69.000 | 69 | 4.5649 | 4.6057 | 0.0408
GEN-2026-PR12 | 04 SOUTHEAST | 514757 | CHIKASI4 138.00 | 138 | 9.4519 | 9.4838 | 0.0319
GEN-2026-PR12 | 04 SOUTHEAST | 514739 | MEDFORD2 69.000 | 69 | 5.6698 | 5.6987 | 0.0289
GEN-2026-PR12 | 04 SOUTHEAST | 514754 | KAYCOOP2 69.000 | 69 | 6.2133 | 6.2384 | 0.0251
GEN-2026-PR12 | 04 SOUTHEAST | 520837 | BLACKWE2 69.000 | 69 | 6.1992 | 6.2242 | 0.025
GEN-2026-PR12 | 04 SOUTHEAST | 515547 | GRANTCO2 69.000 | 69 | 7.7832 | 7.8071 | 0.0239
GEN-2026-PR12 | 04 SOUTHEAST | 514760 | KILDARE4 138.00 | 138 | 11.7528 | 11.7728 | 0.02
GEN-2026-PR12 | 04 SOUTHEAST | 515581 | COYOTE 4 138.00 | 138 | 8.5675 | 8.5874 | 0.0199
GEN-2026-PR12 | 04 SOUTHEAST | 520871 | BRAMAN 2 69.000 | 69 | 4.5599 | 4.5787 | 0.0188
GEN-2026-PR12 | 04 SOUTHEAST | 514764 | NWKRKAT4 138.00 | 138 | 11.4012 | 11.4195 | 0.0183
GEN-2026-PR12 | 04 SOUTHEAST | 515544 | RENFROW4 138.00 | 138 | 14.8533 | 14.8711 | 0.0178
GEN-2026-PR12 | 04 SOUTHEAST | 521012 | NEWKIR-WFEC4138.00 | 138 | 10.7768 | 10.7931 | 0.0163
GEN-2026-PR12 | 04 SOUTHEAST | 515426 | RDRUNNR4 138.00 | 138 | 8.7419 | 8.7569 | 0.015
GEN-2026-PR12 | 04 SOUTHEAST | 515569 | MDFRDTP4 138.00 | 138 | 11.9007 | 11.9148 | 0.0141
GEN-2026-PR12 | 04 SOUTHEAST | 514752 | TONKAWA2 69.000 | 69 | 5.221 | 5.2325 | 0.0115
GEN-2026-PR12 | 04 SOUTHEAST | 529320 | OMOWEN 2 69.000 | 69 | 5.2053 | 5.2167 | 0.0114
GEN-2026-PR12 | 04 SOUTHEAST | 515546 | GRANTCO4 138.00 | 138 | 6.7205 | 6.7313 | 0.0108
GEN-2026-PR12 | 04 SOUTHEAST | 514751 | NEWKRKT2 69.000 | 69 | 3.4922 | 3.5029 | 0.0107
GEN-2026-PR12 | 04 SOUTHEAST | 514759 | NEWKIRK4 138.00 | 138 | 9.8505 | 9.8612 | 0.0107
GEN-2026-PR12 | 04 SOUTHEAST | 514761 | WHEAGLE4 138.00 | 138 | 17.1975 | 17.2082 | 0.0107
GEN-2026-PR12 | 04 SOUTHEAST | 529290 | OMNUKRK4 138.00 | 138 | 9.7392 | 9.7497 | 0.0105
GEN-2026-PR12 | 04 SOUTHEAST | 514743 | OSAGE 4 138.00 | 138 | 18.3395 | 18.349 | 0.0095
GEN-2026-PR12 | 04 SOUTHEAST | 520409 | WFEC_RNFRO4 138.00 | 138 | 10.9839 | 10.9926 | 0.0087
GEN-2026-PR12 | 04 SOUTHEAST | 514762 | 3SANDS 2 69.000 | 69 | 5.1612 | 5.1696 | 0.0084
GEN-2026-PR12 | 04 SOUTHEAST | 515427 | RCKFALL4 138.00 | 138 | 6.3524 | 6.3597 | 0.0073
GEN-2026-PR12 | 04 SOUTHEAST | 514748 | CONTEMP4 138.00 | 138 | 14.727 | 14.734 | 0.007
GEN-2026-PR12 | 04 SOUTHEAST | 522397 | MEDFORD4 138.00 | 138 | 7.6628 | 7.6686 | 0.0058
GEN-2026-PR12 | 04 SOUTHEAST | 514719 | CLYDE 2 69.000 | 69 | 4.6068 | 4.6125 | 0.0057
GEN-2026-PR12 | 04 SOUTHEAST | 514745 | CHERPLT2 69.000 | 69 | 13.3315 | 13.337 | 0.0055
GEN-2026-PR12 | 04 SOUTHEAST | 514744 | CHILOCO2 69.000 | 69 | 11.4539 | 11.4591 | 0.0052
GEN-2026-PR12 | 04 SOUTHEAST | 514802 | SOONER 4 138.00 | 138 | 32.5897 | 32.5946 | 0.0049
GEN-2026-PR12 | 04 SOUTHEAST | 520447 | BLUFCRK4 138.00 | 138 | 3.929 | 3.9332 | 0.0042
GEN-2026-PR12 | 04 SOUTHEAST | 515646 | GRNTWD 7 345.00 | 345 | 11.0449 | 11.0487 | 0.0038
GEN-2026-PR12 | 04 SOUTHEAST | 763421 | G18-128-TAP 345.00 | 345 | 12.0534 | 12.0568 | 0.0034
GEN-2026-PR12 | 04 SOUTHEAST | 514746 | CHERKPL2 69.000 | 69 | 10.3399 | 10.3432 | 0.0033
GEN-2026-PR12 | 04 SOUTHEAST | 515412 | DMNCRKT4 138.00 | 138 | 14.544 | 14.5473 | 0.0033
GEN-2026-PR12 | 04 SOUTHEAST | 515476 | HUNTERS7 345.00 | 345 | 13.5454 | 13.5484 | 0.003
GEN-2026-PR12 | 04 SOUTHEAST | 515477 | CHSHLMV7 345.00 | 345 | 13.5226 | 13.5255 | 0.0029
GEN-2026-PR12 | 04 SOUTHEAST | 763417 | GEN-2018-128345.00 | 345 | 10.9053 | 10.9081 | 0.0028
GEN-2026-PR12 | 04 SOUTHEAST | 522398 | PONDCRK4 138.00 | 138 | 5.2534 | 5.2562 | 0.0028
GEN-2026-PR12 | 04 SOUTHEAST | 533075 | VIOLA 4 138.00 | 138 | 25.0858 | 25.0884 | 0.0026
GEN-2026-PR12 | 04 SOUTHEAST | 514715 | WOODRNG7 345.00 | 345 | 19.9804 | 19.9829 | 0.0025
GEN-2026-PR12 | 04 SOUTHEAST | 914720 | SKELETON__HV345.00 | 345 | 18.9141 | 18.9164 | 0.0023
GEN-2026-PR12 | 04 SOUTHEAST | 532798 | VIOLA 7 345.00 | 345 | 13.8901 | 13.8924 | 0.0023
GEN-2026-PR12 | 04 SOUTHEAST | 514736 | 4CORNER2 69.000 | 69 | 3.8426 | 3.8447 | 0.0021
GEN-2026-PR12 | 04 SOUTHEAST | 514714 | WOODRNG4 138.00 | 138 | 20.7223 | 20.7241 | 0.0018
GEN-2026-PR12 | 04 SOUTHEAST | 520434 | WAKTASW4 138.00 | 138 | 6.5177 | 6.5194 | 0.0017
GEN-2026-PR12 | 04 SOUTHEAST | 514803 | SOONER 7 345.00 | 345 | 29.4776 | 29.4792 | 0.0016
GEN-2026-PR12 | 04 SOUTHEAST | 532796 | WICHITA7 345.00 | 345 | 23.6618 | 23.6632 | 0.0014
GEN-2026-PR12 | 04 SOUTHEAST | 516010 | PINTAIL7 345.00 | 345 | 17.0478 | 17.049 | 0.0012
GEN-2026-PR12 | 04 SOUTHEAST | 533062 | ROSEHIL4 138.00 | 138 | 31.8483 | 31.8495 | 0.0012
GEN-2026-PR12 | 04 SOUTHEAST | 516019 | KINGWD 7 345.00 | 345 | 16.9855 | 16.9866 | 0.0011
GEN-2026-PR12 | 04 SOUTHEAST | 515400 | DMANCRK4 138.00 | 138 | 8.5012 | 8.5023 | 0.0011
GEN-2026-PR12 | 04 SOUTHEAST | 532782 | BUFFALO7 345.00 | 345 | 20.6762 | 20.6773 | 0.0011
GEN-2026-PR12 | 04 SOUTHEAST | 515875 | REDNGTN7 345.00 | 345 | 18.3889 | 18.3899 | 0.001
GEN-2026-PR12 | 04 SOUTHEAST | 533069 | BUFFALO4 138.00 | 138 | 31.9445 | 31.9455 | 0.001
GEN-2026-PR12 | 04 SOUTHEAST | 760284 | GEN-2017-220345.00 | 345 | 20.562 | 20.563 | 0.001
GEN-2026-PR12 | 04 SOUTHEAST | 515877 | REDDIRT7 345.00 | 345 | 18.3843 | 18.3852 | 0.0009
GEN-2026-PR12 | 04 SOUTHEAST | 532791 | BENTON 7 345.00 | 345 | 19.604 | 19.6048 | 0.0008
GEN-2026-PR12 | 04 SOUTHEAST | 762321 | GEN-2017-164345.00 | 345 | 11.8413 | 11.8421 | 0.0008
GEN-2026-PR12 | 04 SOUTHEAST | 515497 | MATHWSN7 345.00 | 345 | 37.667 | 37.6678 | 0.0008
GEN-2026-PR12 | 04 SOUTHEAST | 515975 | G15-066T 345.00 | 345 | 20.2356 | 20.2363 | 0.0007
GEN-2026-PR12 | 04 SOUTHEAST | 532794 | ROSEHIL7 345.00 | 345 | 19.2114 | 19.2121 | 0.0007
GEN-2026-PR12 | 04 SOUTHEAST | 532814 | FR4345KV-TAP345.00 | 345 | 7.8987 | 7.8993 | 0.0006
GEN-2026-PR12 | 04 SOUTHEAST | 852252 | TEST-FR4 345.00 | 345 | 7.8987 | 7.8993 | 0.0006
GEN-2026-PR12 | 04 SOUTHEAST | 852253 | TEST-FR5-0 345.00 | 345 | 7.8987 | 7.8993 | 0.0006
GEN-2026-PR12 | 04 SOUTHEAST | 532792 | FR2EAST7 345.00 | 345 | 6.6732 | 6.6737 | 0.0005
GEN-2026-PR12 | 04 SOUTHEAST | 515974 | GEN-2015-066345.00 | 345 | 17.4439 | 17.4444 | 0.0005
GEN-2026-PR12 | 04 SOUTHEAST | 762342 | GEN-2017-178345.00 | 345 | 8.2763 | 8.2767 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 514795 | KNOBHIL4 138.00 | 138 | 10.185 | 10.1854 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 515853 | DGRASSE4 138.00 | 138 | 15.8767 | 15.8771 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 520430 | NOELSW 4 138.00 | 138 | 10.2529 | 10.2533 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 539801 | THISTLE7 345.00 | 345 | 16.2502 | 16.2506 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 763769 | GEN-2019-045138.00 | 138 | 15.8767 | 15.8771 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 915975 | WILLOW_CR_HV345.00 | 345 | 17.3232 | 17.3236 | 0.0004
GEN-2026-PR12 | 04 SOUTHEAST | 515852 | DGRASSE7 345.00 | 345 | 15.2948 | 15.2951 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 520436 | ROSEVLY4 138.00 | 138 | 11.9324 | 11.9327 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 765480 | GEN-2021-019345.00 | 345 | 13.1678 | 13.1681 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 774061 | GEN-2023-104138.00 | 138 | 11.1329 | 11.1332 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 515576 | RANCHRD7 345.00 | 345 | 15.3192 | 15.3195 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 515894 | THUNDER7 345.00 | 345 | 13.3106 | 13.3109 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 516192 | WAGNWTIE7 345.00 | 345 | 15.7645 | 15.7648 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 516198 | WAGNWL7 345.00 | 345 | 15.7645 | 15.7648 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 516207 | GADWALL7 345.00 | 345 | 15.7645 | 15.7648 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 529200 | OMCDLEC7 345.00 | 345 | 15.2925 | 15.2928 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 532837 | G15052_T 345.00 | 345 | 13.141 | 13.1413 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 539804 | THISTLE4 138.00 | 138 | 18.015 | 18.0153 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 539871 | PIXLEY-SOLAR345.00 | 345 | 15.5427 | 15.543 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 562900 | G15052_1 345.00 | 345 | 13.0872 | 13.0875 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 763065 | GEN-2018-071345.00 | 345 | 14.8405 | 14.8408 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 763069 | G18-071-TAP 345.00 | 345 | 14.898 | 14.8983 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 767301 | GEN-2022-016345.00 | 345 | 22.5988 | 22.5991 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 774060 | G23-104-TAP 138.00 | 138 | 11.2176 | 11.2179 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 914715 | SKELETON__HV345.00 | 345 | 5.9866 | 5.9869 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 767221 | GEN-2022-012345.00 | 345 | 22.5773 | 22.5776 | 0.0003
GEN-2026-PR12 | 04 SOUTHEAST | 509852 | T.NO.--7 345.00 | 345 | 25.3812 | 25.3814 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 539638 | FLATRDG4 138.00 | 138 | 16.0543 | 16.0545 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 516066 | FRNT2WD7 345.00 | 345 | 11.8709 | 11.8711 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 514794 | KNOBHIL2 69.000 | 69 | 9.1654 | 9.1656 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 514825 | KAYWIND7 345.00 | 345 | 13.3986 | 13.3988 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 515375 | WWRDEHV7 345.00 | 345 | 22.9315 | 22.9317 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 515407 | TATONGA7 345.00 | 345 | 18.5377 | 18.5379 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 515990 | SKELTON7 345.00 | 345 | 5.1876 | 5.1878 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 532795 | FR2WEST7 345.00 | 345 | 5.4293 | 5.4295 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 767321 | GEN-2022-017345.00 | 345 | 22.2582 | 22.2584 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 515688 | FRNTWND7 345.00 | 345 | 12.8317 | 12.8319 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 763527 | GEN-2019-012345.00 | 345 | 19.9169 | 19.9171 | 0.0002
GEN-2026-PR12 | 04 SOUTHEAST | 512805 | SALNCRK5 161.00 | 161 | 19.6898 | 19.6899 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 515376 | WWRDEHV4 138.00 | 138 | 26.1558 | 26.1559 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 515785 | WINDFRM4 138.00 | 138 | 21.8256 | 21.8257 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532797 | WOLFCRK7 345.00 | 345 | 21.2861 | 21.2862 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532939 | N345 4 5 161.00 | 161 | 22.9583 | 22.9584 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 511592 | SEVEN7A_HV 345.00 | 345 | 9.6571 | 9.6572 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 511599 | SEVEN7AB2 345.00 | 345 | 9.6571 | 9.6572 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 511608 | SEVEN7AB3 345.00 | 345 | 9.6571 | 9.6572 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 512651 | CLARMR 5 161.00 | 161 | 13.8301 | 13.8302 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 515585 | MAMTHPW7 345.00 | 345 | 14.3238 | 14.3239 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 515825 | GRTWSRN7 345.00 | 345 | 10.5569 | 10.557 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 523040 | OLYMPIA7 345.00 | 345 | 12.5605 | 12.5606 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532778 | NEOSHORDGWF7345.00 | 345 | 11.1628 | 11.1629 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532800 | LATHAMS7 345.00 | 345 | 10.4159 | 10.416 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532801 | ELKRVR17 345.00 | 345 | 9.1828 | 9.1829 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7345.00 | 345 | 10.9298 | 10.9299 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 763677 | G19-030-TAP 345.00 | 345 | 9.8253 | 9.8254 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 770500 | G22-176-TAP 345.00 | 345 | 12.9403 | 12.9404 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 770501 | GEN-2022-176345.00 | 345 | 12.9071 | 12.9072 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 776821 | GEN-2023-102345.00 | 345 | 11.0496 | 11.0497 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 511911 | ZONE-4 SUB 345.00 | 345 | 6.5047 | 6.5048 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 514788 | GLASMTN4 138.00 | 138 | 5.4197 | 5.4198 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 516087 | TRAV22Z7 345.00 | 345 | 5.585 | 5.5851 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 520601 | AVARD 4 138.00 | 138 | 6.7914 | 6.7915 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 588190 | GEN-2016-128345.00 | 345 | 4.9344 | 4.9345 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 509834 | COGENT 7 345.00 | 345 | 30.869 | 30.8691 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 509836 | OEC 7 345.00 | 345 | 30.4019 | 30.402 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 510406 | N.E.S.-7 345.00 | 345 | 17.1714 | 17.1715 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 511553 | CHISHOLM7 345.00 | 345 | 12.8795 | 12.8796 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 515961 | GUTHRIE7 345.00 | 345 | 14.452 | 14.4521 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 516106 | BOBCAT 7 345.00 | 345 | 16.159 | 16.1591 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 516109 | TRAV12Z7 345.00 | 345 | 5.1959 | 5.196 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 516146 | 25MILE 7 345.00 | 345 | 16.1296 | 16.1297 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 516159 | 25MILZ 7 345.00 | 345 | 16.101 | 16.1011 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 520462 | ASPEN 4 138.00 | 138 | 21.6854 | 21.6855 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 520999 | MOORLND4 138.00 | 138 | 22.534 | 22.5341 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532777 | NRSS7 345.00 | 345 | 12.0748 | 12.0749 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532783 | KINGMAN7 345.00 | 345 | 7.0868 | 7.0869 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532786 | FR3 WF7 345.00 | 345 | 4.461 | 4.4611 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 534109 | GEN-2016-073345.00 | 345 | 5.5501 | 5.5502 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 585420 | SUBST HS 345.00 | 345 | 8.1157 | 8.1158 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 588560 | GEN-2017-011345.00 | 345 | 12.9785 | 12.9786 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 763670 | GEN-2019-030345.00 | 345 | 8.1996 | 8.1997 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 763890 | GEN-2019-058345.00 | 345 | 10.7385 | 10.7386 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 765350 | GEN-2021-006345.00 | 345 | 17.8919 | 17.892 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 765470 | GEN-2021-018345.00 | 345 | 7.6136 | 7.6137 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 765720 | GEN-2021-047345.00 | 345 | 15.7771 | 15.7772 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 767241 | GEN-2022-013345.00 | 345 | 11.3484 | 11.3485 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 512629 | DRYGULCH5 161.00 | 161 | 15.8957 | 15.8958 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 532781 | CANEYWF7 345.00 | 345 | 9.4202 | 9.4203 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 539631 | FLATRWD4 138.00 | 138 | 10.8122 | 10.8123 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 539840 | GEN-2011-008345.00 | 345 | 9.1007 | 9.1008 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 562020 | PRSCRKII 7 345.00 | 345 | 11.4972 | 11.4973 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 509755 | WEKIWA-7 345.00 | 345 | 22.7944 | 22.7945 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 509782 | R.S.S.-7 345.00 | 345 | 33.3755 | 33.3756 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 511877 | G16133G16146345.00 | 345 | 33.3755 | 33.3756 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 533023 | N345 3 4 138.00 | 138 | 24.4537 | 24.4538 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 588810 | GEN-2017-040345.00 | 345 | 20.0127 | 20.0128 | 0.0001
GEN-2026-PR12 | 04 SOUTHEAST | 45193 | J1519 SUB 345.00 | 345 | 13.9547 | 13.9547 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 45194 | J1519 POI 345.00 | 345 | 13.9547 | 13.9547 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 48723 | J1872 SUB 500.00 | 500 | 23.6697 | 23.6697 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 48733 | J1873 SUB 500.00 | 500 | 23.6697 | 23.6697 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300035 | 8NEWMAD 500.00 | 500 | 13.3969 | 13.3969 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300038 | 7ESSEX 345.00 | 345 | 15.0957 | 15.0957 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300045 | 7MORGAN 345.00 | 345 | 13.4659 | 13.4659 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300046 | 7NEWMAD 345.00 | 345 | 23.2235 | 23.2235 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300048 | 7STFRAN 345.00 | 345 | 11.9314 | 11.9314 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300054 | 7GOBKNOB 345.00 | 345 | 8.7195 | 8.7195 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300069 | 5CHOTEAU1 161.00 | 161 | 42.8238 | 42.8238 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300075 | 5ESSEX 161.00 | 161 | 18.9026 | 18.9026 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300116 | 5STFRNB3 161.00 | 161 | 20.0007 | 20.0007 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300739 | 7BLACKBERRY 345.00 | 345 | 16.1212 | 16.1212 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300740 | 7SPORTSMAN 345.00 | 345 | 24.7937 | 24.7937 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300741 | 5SPORTSMAN 161.00 | 161 | 41.1743 | 41.1743 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300949 | 7JASPER 345.00 | 345 | 13.03 | 13.03 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300955 | 2COWETA 69.000 | 69 | 2.5442 | 2.5442 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300958 | 2HIGHLND 69.000 | 69 | 1.9517 | 1.9517 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 300972 | 2WAGNERW 69.000 | 69 | 4.7249 | 4.7249 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301348 | 5CHOTEAU2 161.00 | 161 | 42.8238 | 42.8238 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301406 | 8WNEWMADRID 500.00 | 500 | 13.4657 | 13.4657 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301416 | 7WNWMADRID1B345.00 | 345 | 22.6179 | 22.6179 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301417 | 7WNWMADRID1C345.00 | 345 | 22.736 | 22.736 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301418 | 7WNWMADRID2 345.00 | 345 | 22.4036 | 22.4036 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301529 | 7NEWMADXF34 345.00 | 345 | 23.0406 | 23.0406 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301530 | 7NEWMADXF12 345.00 | 345 | 23.0576 | 23.0576 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301533 | 5ESSEXGSU1 161.00 | 161 | 18.8247 | 18.8247 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301535 | 5STFRNGSU2 161.00 | 161 | 19.7644 | 19.7644 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 301537 | 7NEWMADGSU2 345.00 | 345 | 23.069 | 23.069 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 334028 | 7GRIMES% 345.00 | 345 | 5.69 | 5.69 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 334029 | 7FRONTR 345.00 | 345 | 5.4643 | 5.4643 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 334197 | 7ROCKYCRK% 345.00 | 345 | 5.986 | 5.986 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 334198 | 6ROCKYCRK 230.00 | 230 | 7.5036 | 7.5036 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337361 | 3MINDEN_LA! 115.00 | 115 | 6.9145 | 6.9145 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337362 | 3LA_ORD_PLNT115.00 | 115 | 4.5242 | 4.5242 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337363 | 3SAREPTA! 115.00 | 115 | 20.4182 | 20.4182 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337364 | 3CULLEN 115.00 | 115 | 8.6972 | 8.6972 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337365 | 3SPRINGHILL 115.00 | 115 | 9.9946 | 9.9946 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337366 | 3HAYNESVILLE115.00 | 115 | 6.0501 | 6.0501 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337376 | 7SAREPTA% 345.00 | 345 | 10.1806 | 10.1806 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337561 | 8EL DORADO% 500.00 | 500 | 28.3403 | 28.3403 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337562 | 7EL DORADO 345.00 | 345 | 14.3094 | 14.3094 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337808 | 8MABELVALE% 500.00 | 500 | 27.259 | 27.259 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337909 | 8ANO% 500.00 | 500 | 18.641 | 18.641 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337912 | 5ANO% 161.00 | 161 | 18.2129 | 18.2129 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 337922 | 8P.HILL% 500.00 | 500 | 15.5786 | 15.5786 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338187 | 8DELL% 500.00 | 500 | 22.0025 | 22.0025 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338340 | 8CC_DELL 500.00 | 500 | 22.0025 | 22.0025 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338440 | 8PANDA% 500.00 | 500 | 28.2751 | 28.2751 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338596 | 5DELL# 161.00 | 161 | 16.4096 | 16.4096 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338796 | 5AECC-DL-SS#161.00 | 161 | 16.3337 | 16.3337 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338807 | 5NUC-YAM-S# 161.00 | 161 | 9.8909 | 9.8909 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 338808 | 5NUCOR-II-S#161.00 | 161 | 8.2047 | 8.2047 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 344974 | 7LUTESVIL 345.00 | 345 | 17.1051 | 17.1051 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 345014 | 7J1107 SUB 345.00 | 345 | 15.7732 | 15.7732 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 345015 | 7ADNA 345.00 | 345 | 15.8006 | 15.8006 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 345434 | 7HERITAGE 345.00 | 345 | 12.23 | 12.23 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 345588 | 5RCHLND 1 161.00 | 161 | 10.484 | 10.484 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 345791 | 5RICHLAND_TP161.00 | 161 | 17.4834 | 17.4834 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 500250 | DOLHILL7 345.00 | 345 | 8.3137 | 8.3137 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 500260 | DOLHILL6 230.00 | 230 | 12.2571 | 12.2571 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 504010 | ELMSPRGS 5 161.00 | 161 | 18.2746 | 18.2746 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 504011 | ELMSPG_1 2 69.000 | 69 | 5.7141 | 5.7141 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 504013 | ELMSPG_2 2 69.000 | 69 | 7.9319 | 7.9319 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 504182 | BEVERLY5 161.00 | 161 | 21.7937 | 21.7937 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 504201 | GENTRY 5 161.00 | 161 | 27.0081 | 27.0081 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 504202 | SILOAMSP 5 161.00 | 161 | 19.9798 | 19.9798 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 505434 | IDALIA 5 161.00 | 161 | 18.7579 | 18.7579 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506926 | DYESS 2 69.000 | 69 | 16.3887 | 16.3887 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506927 | DYESS 5 161.00 | 161 | 17.2963 | 17.2963 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506934 | FLINTCR5 161.00 | 161 | 33.722 | 33.722 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506935 | FLINTCR7 345.00 | 345 | 15.803 | 15.803 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506944 | CHAMSPR5 161.00 | 161 | 23.6327 | 23.6327 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506945 | CHAMSPR7 345.00 | 345 | 10.3838 | 10.3838 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506948 | SILOAM 5 161.00 | 161 | 22.4995 | 22.4995 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506950 | SPRDALE2 69.000 | 69 | 12.2184 | 12.2184 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506951 | SPRDALT2 69.000 | 69 | 11.4249 | 11.4249 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506952 | CENTRTN5 161.00 | 161 | 15.192 | 15.192 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506957 | TONTITN5 161.00 | 161 | 22.1055 | 22.1055 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506959 | TONTITN7 345.00 | 345 | 9.2769 | 9.2769 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506960 | BEN279_5 161.00 | 161 | 13.4222 | 13.4222 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506973 | SILOAM 2 69.000 | 69 | 11.5158 | 11.5158 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506978 | MATTISN5 161.00 | 161 | 21.6609 | 21.6609 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506979 | SHIPERD7 345.00 | 345 | 10.5818 | 10.5818 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506980 | SHIPERD5 161.00 | 161 | 15.7115 | 15.7115 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 506991 | BRUSHCRK_5 161.00 | 161 | 16.1061 | 16.1061 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507711 | ARSHILL4 138.00 | 138 | 25.9141 | 25.9141 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507727 | FLOURNY4 138.00 | 138 | 17.2345 | 17.2345 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507732 | GENMOTR4 138.00 | 138 | 18.4037 | 18.4037 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507748 | POWELL 4 138.00 | 138 | 20.0878 | 20.0878 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507749 | RAINES 4 138.00 | 138 | 16.395 | 16.395 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507755 | S SHV 4 138.00 | 138 | 24.0554 | 24.0554 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507757 | SPRIDGE4 138.00 | 138 | 12.1934 | 12.1934 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507759 | SW SHV 4 138.00 | 138 | 31.4124 | 31.4124 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507760 | SW SHV 7 345.00 | 345 | 15.4032 | 15.4032 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507774 | NORAM 4 138.00 | 138 | 17.1121 | 17.1121 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507788 | MINDEN-3 115.00 | 115 | 5.5853 | 5.5853 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507789 | STLGENS4 138.00 | 138 | 25.5042 | 25.5042 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 507793 | LEASIDE 4 138.00 | 138 | 23.2003 | 23.2003 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508064 | MUNZCTY4 138.00 | 138 | 7.6801 | 7.6801 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508072 | NWTXARK7 345.00 | 345 | 14.977 | 14.977 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508090 | WATLANT4 138.00 | 138 | 7.8341 | 7.8341 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508297 | LSSOUTH4 138.00 | 138 | 16.9161 | 16.9161 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508359 | WELSH 7 345.00 | 345 | 24.6167 | 24.6167 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508562 | PIRKEY 4 138.00 | 138 | 34.07 | 34.07 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508563 | PIRKEY 7 345.00 | 345 | 16.3169 | 16.3169 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508567 | SCOTTSV4 138.00 | 138 | 11.7732 | 11.7732 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508572 | LEBROCK7 345.00 | 345 | 15.3743 | 15.3743 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508586 | TENGEN 7 345.00 | 345 | 7.9968 | 7.9968 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508805 | LIEBERM2 69.000 | 69 | 9.5483 | 9.5483 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508806 | LIEBERM4 138.00 | 138 | 17.8019 | 17.8019 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508808 | LONGWD 4 138.00 | 138 | 27.1445 | 27.1445 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508816 | OAKPH 4 138.00 | 138 | 20.9586 | 20.9586 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508831 | DIANA 4 138.00 | 138 | 30.3589 | 30.3589 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508832 | DIANA 7 345.00 | 345 | 19.9319 | 19.9319 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508833 | IPCJEFF4 138.00 | 138 | 12.9795 | 12.9795 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508835 | JEFFRSN4 138.00 | 138 | 14.3899 | 14.3899 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508840 | WILKES 4 138.00 | 138 | 31.3781 | 31.3781 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508841 | WILKES 7 345.00 | 345 | 16.5358 | 16.5358 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508847 | WELSHDC1 345.00 | 345 | 23.6536 | 23.6536 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508848 | SPPMAINBUS 345.00 | 345 | 23.6536 | 23.6536 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508860 | DIXIEMAZE4 138.00 | 138 | 10.2408 | 10.2408 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 508861 | AVINGTP4 138.00 | 138 | 19.3146 | 19.3146 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509240 | CROCKET4 138.00 | 138 | 6.928 | 6.928 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509241 | CROCKET7 345.00 | 345 | 5.5147 | 5.5147 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509322 | GRAPLND4 138.00 | 138 | 4.6548 | 4.6548 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509600 | AVINGER4 138.00 | 138 | 18.9124 | 18.9124 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509601 | BETHLHM2 69.000 | 69 | 5.0791 | 5.0791 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509606 | DIAN 2 69.000 | 69 | 9.108 | 9.108 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509607 | DIAN 4 138.00 | 138 | 12.0369 | 12.0369 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509608 | EASTMNT2 69.000 | 69 | 2.9528 | 2.9528 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509610 | GETHSMA2 69.000 | 69 | 1.7382 | 1.7382 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509613 | GLENWOD2 69.000 | 69 | 3.5009 | 3.5009 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509614 | HALL 2 69.000 | 69 | 1.7669 | 1.7669 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509615 | HALLSVL4 138.00 | 138 | 4.5121 | 4.5121 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509616 | HARLETT2 69.000 | 69 | 3.6704 | 3.6704 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509617 | HARLETN2 69.000 | 69 | 2.9539 | 2.9539 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509621 | JEFERSN2 69.000 | 69 | 2.279 | 2.279 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509623 | LAKEPIN2 69.000 | 69 | 7.7051 | 7.7051 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509624 | LAKEPIN4 138.00 | 138 | 7.827 | 7.827 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509627 | NESBIT 2 69.000 | 69 | 3.3875 | 3.3875 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509628 | NOONDAY4 138.00 | 138 | 6.067 | 6.067 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509629 | ORECITY2 69.000 | 69 | 3.2089 | 3.2089 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509633 | SHADYSH2 69.000 | 69 | 2.3749 | 2.3749 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509635 | VICTORY2 69.000 | 69 | 2.7378 | 2.7378 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509638 | STEEL 2 69.000 | 69 | 3.1145 | 3.1145 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509639 | DIANASW4 138.00 | 138 | 12.5327 | 12.5327 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509745 | CLARKSV7 345.00 | 345 | 22.1125 | 22.1125 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 509807 | ONETA--7 345.00 | 345 | 30.5067 | 30.5067 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 510379 | DELWARE4 138.00 | 138 | 11.5434 | 11.5434 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511467 | L.E.S.-4 138.00 | 138 | 26.8612 | 26.8612 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511468 | L.E.S.-7 345.00 | 345 | 15.5126 | 15.5126 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511557 | CHISHOLM6 230.00 | 230 | 12.7235 | 12.7235 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7345.00 | 345 | 5.5613 | 5.5613 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511584 | O.K.U.2-7 345.00 | 345 | 5.5774 | 5.5774 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511587 | MATO 7 345.00 | 345 | 10.1321 | 10.1321 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511607 | O.K.U.3-7 345.00 | 345 | 5.5774 | 5.5774 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511726 | ZONE-5 SUB 345.00 | 345 | 7.0106 | 7.0106 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511878 | G16133_765TN765.00 | 765 | 9.2438 | 9.2438 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511879 | G16133_765R1765.00 | 765 | 9.2438 | 9.2438 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511880 | G16133_765R2765.00 | 765 | 4.5569 | 4.5569 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511881 | G16133_765R3765.00 | 765 | 3.6459 | 3.6459 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511882 | G16133_765CS765.00 | 765 | 3.6459 | 3.6459 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511883 | G16133_345CS345.00 | 345 | 7.9324 | 7.9324 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511884 | ZONE-1 SUB 345.00 | 345 | 7.0434 | 7.0434 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511893 | ZONE-2 SUB 345.00 | 345 | 7.0252 | 7.0252 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511902 | ZONE-3 SUB 345.00 | 345 | 6.965 | 6.965 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511929 | ZONE-6 SUB 345.00 | 345 | 7.051 | 7.051 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511983 | OXBOW 4 138.00 | 138 | 10.1471 | 10.1471 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 511999 | DVRSION-WIND345.00 | 345 | 3.8652 | 3.8652 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512625 | MAIDTP2 69.000 | 69 | 12.2803 | 12.2803 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512626 | MAID 2 69.000 | 69 | 14.9379 | 14.9379 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512635 | KERR GR5 161.00 | 161 | 30.6337 | 30.6337 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512638 | CATSAGR5 161.00 | 161 | 27.5693 | 27.5693 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512640 | OKAYGR 5 161.00 | 161 | 10.2879 | 10.2879 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512643 | SILMCTY5 161.00 | 161 | 20.4105 | 20.4105 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512648 | MAID 5 161.00 | 161 | 45.9446 | 45.9446 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512650 | GRDA1 7 345.00 | 345 | 27.2003 | 27.2003 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512656 | GRDA1 5 161.00 | 161 | 45.3458 | 45.3458 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512683 | AMERCAST N2 69.000 | 69 | 8.6159 | 8.6159 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512685 | CASTING TAP269.000 | 69 | 9.5968 | 9.5968 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512686 | SALINA 5 161.00 | 161 | 19.0244 | 19.0244 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512697 | WAGNOR 2 69.000 | 69 | 7.3339 | 7.3339 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512698 | REDDEN 2 69.000 | 69 | 10.9639 | 10.9639 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512700 | WAGNOR 5 161.00 | 161 | 9.9863 | 9.9863 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512727 | GRDA1 2 69.000 | 69 | 12.6875 | 12.6875 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512728 | ARKLIN2 69.000 | 69 | 4.2349 | 4.2349 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512730 | SSSWES2 69.000 | 69 | 11.7662 | 11.7662 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512734 | FARML 4 138.00 | 138 | 7.6267 | 7.6267 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512735 | COFCTY2 69.000 | 69 | 6.6105 | 6.6105 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512737 | SSSWTP2 69.000 | 69 | 12.866 | 12.866 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512742 | WMAIN ST5 161.00 | 161 | 28.6145 | 28.6145 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512744 | SSMOSS2 69.000 | 69 | 10.6104 | 10.6104 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512745 | SSLINC2 69.000 | 69 | 3.1046 | 3.1046 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512746 | SSNORT2 69.000 | 69 | 3.1697 | 3.1697 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512747 | SSNEWN2 69.000 | 69 | 3.4611 | 3.4611 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512750 | TONECE7 345.00 | 345 | 15.5762 | 15.5762 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512751 | TONECE5 161.00 | 161 | 15.7674 | 15.7674 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512753 | TONNEC2 69.000 | 69 | 5.6453 | 5.6453 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512756 | TONECESTR2 69.000 | 69 | 4.3741 | 4.3741 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512757 | NWMAID5 161.00 | 161 | 28.3868 | 28.3868 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512759 | WAGCTY22 69.000 | 69 | 5.9145 | 5.9145 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512760 | GERALDGAY5 161.00 | 161 | 29.759 | 29.759 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512785 | GEN-2017-061161.00 | 161 | 20.8924 | 20.8924 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512801 | WAGCTY12 69.000 | 69 | 5.5451 | 5.5451 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512820 | SILMCTY2 69.000 | 69 | 13.7944 | 13.7944 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512858 | GEN-2017-073161.00 | 161 | 14.7498 | 14.7498 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 512865 | GREC TAP7 345.00 | 345 | 25.985 | 25.985 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513050 | LOCSTGV 5 161.00 | 161 | 13.8001 | 13.8001 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513570 | CHOUTEAUCRK5161.00 | 161 | 20.8936 | 20.8936 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513589 | CUSTDAY2 5 161.00 | 161 | 16.4689 | 16.4689 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513590 | CUSTDAY1 5 161.00 | 161 | 16.4703 | 16.4703 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513591 | HERRON 5 161.00 | 161 | 17.2872 | 17.2872 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513593 | IGLOOV1 5 161.00 | 161 | 17.4848 | 17.4848 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513595 | IGLOOV2 5 161.00 | 161 | 17.4848 | 17.4848 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 513596 | IGLOOV 7 345.00 | 345 | 20.6047 | 20.6047 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 514785 | WOODWRD4 138.00 | 138 | 14.6639 | 14.6639 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 514796 | IODINE-4 138.00 | 138 | 7.8228 | 7.8228 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515045 | SEMINOL7 345.00 | 345 | 30.4235 | 30.4235 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515224 | MUSKOGE7 345.00 | 345 | 33.7779 | 33.7779 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515233 | PECANCK4 138.00 | 138 | 14.575 | 14.575 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515234 | PECANCK5 161.00 | 161 | 21.9154 | 21.9154 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515235 | PECANCK7 345.00 | 345 | 25.1429 | 25.1429 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515299 | BEVYTAP5 161.00 | 161 | 22.7209 | 22.7209 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515300 | FTSMTHE5 161.00 | 161 | 26.0416 | 26.0416 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515301 | FTSMTHW5 161.00 | 161 | 25.9074 | 25.9074 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515305 | FTSMITH8 500.00 | 500 | 10.5238 | 10.5238 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515306 | ARKOMA 5 161.00 | 161 | 17.3959 | 17.3959 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515308 | 3RDST 5 161.00 | 161 | 16.5589 | 16.5589 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515310 | QUANXTP5 161.00 | 161 | 19.2463 | 19.2463 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515345 | COLONY 5 161.00 | 161 | 20.1277 | 20.1277 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515363 | CENT 4 138.00 | 138 | 3.2821 | 3.2821 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515394 | KEENAN 4 138.00 | 138 | 9.2788 | 9.2788 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515398 | OUSPRT 4 138.00 | 138 | 9.9555 | 9.9555 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515422 | C-RIVER7 345.00 | 345 | 12.0861 | 12.0861 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515425 | WWDPST 4 138.00 | 138 | 18.9701 | 18.9701 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515448 | CRSRDSW7 345.00 | 345 | 12.7466 | 12.7466 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515458 | BORDER 7345.00 | 345 | 10.2409 | 10.2409 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515474 | QUANEXS5 161.00 | 161 | 18.1903 | 18.1903 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515582 | SLNGWND7 345.00 | 345 | 8.9133 | 8.9133 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515618 | BALKOW 7 345.00 | 345 | 10.7018 | 10.7018 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515634 | PALDR1W7 345.00 | 345 | 9.317 | 9.317 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515677 | BADGER 7 345.00 | 345 | 12.4622 | 12.4622 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515686 | BLUWND 7 345.00 | 345 | 11.2879 | 11.2879 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515778 | GRIFFIN7 345.00 | 345 | 24.045 | 24.045 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515786 | FPLWIND4 138.00 | 138 | 6.6021 | 6.6021 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 515951 | PERSIMN7 345.00 | 345 | 12.6386 | 12.6386 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516036 | TRAV3WD7 345.00 | 345 | 7.3645 | 7.3645 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516045 | TRAV2WD7 345.00 | 345 | 5.9111 | 5.9111 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516054 | TRAV1WD7 345.00 | 345 | 5.4732 | 5.4732 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516059 | BECKHAM7 345.00 | 345 | 12.9209 | 12.9209 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516074 | PONDRSA7 345.00 | 345 | 9.8548 | 9.8548 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516086 | TRAV3WZ7 345.00 | 345 | 6.8509 | 6.8509 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516091 | OKTAHA 7 345.00 | 345 | 18.367 | 18.367 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516092 | OKTAHA 5 161.00 | 161 | 11.24 | 11.24 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516107 | TRAV21Z7 345.00 | 345 | 5.5853 | 5.5853 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516108 | TRAV11Z7 345.00 | 345 | 5.1961 | 5.1961 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 516210 | RAVEN 7 345.00 | 345 | 20.5057 | 20.5057 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 520425 | PIC4 138.00 | 138 | 8.54 | 8.54 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 520553 | SEILING4 138.00 | 138 | 7.5569 | 7.5569 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 520957 | IODINE 4 138.00 | 138 | 8.2831 | 8.2831 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 520995 | MOORLND2 69.000 | 69 | 9.0399 | 9.0399 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 521127 | BOILSPR4 138.00 | 138 | 8.0906 | 8.0906 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523019 | OSLO-SYLVIE7345.00 | 345 | 9.1223 | 9.1223 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523020 | SYLVIE 7 345.00 | 345 | 9.1223 | 9.1223 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523030 | OLSO 7 345.00 | 345 | 9.1223 | 9.1223 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523041 | FRWLN7 345.00 | 345 | 10.3937 | 10.3937 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523093 | HITCHLAND 3115.00 | 115 | 16.0833 | 16.0833 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523095 | HITCHLAND 6230.00 | 230 | 13.4088 | 13.4088 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523097 | HITCHLAND 7345.00 | 345 | 12.7797 | 12.7797 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523103 | NOBLE_WND 3115.00 | 115 | 9.8587 | 9.8587 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523130 | GRPLNS-HV4-3115.00 | 115 | 6.8517 | 6.8517 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523131 | GRPLNS-HV2-3115.00 | 115 | 9.0655 | 9.0655 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523155 | OCHILTREE 6230.00 | 230 | 4.2271 | 4.2271 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523174 | GOODWELLWND3115.00 | 115 | 6.1198 | 6.1198 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523309 | MOORE_CNTY 6230.00 | 230 | 8.16 | 8.16 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523823 | CARPENTER 7345.00 | 345 | 6.5005 | 6.5005 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523959 | POTTER_CO 6230.00 | 230 | 27.2975 | 27.2975 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523961 | POTTER_CO 7345.00 | 345 | 18.5013 | 18.5013 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 523966 | POTTER_CO 9765.00 | 765 | 8.1188 | 8.1188 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 524296 | SPNSPUR_WND7345.00 | 345 | 6.4272 | 6.4272 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 524299 | SPNSPUR_COL7345.00 | 345 | 6.4272 | 6.4272 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525213 | SWISHER 6230.00 | 230 | 10.6579 | 10.6579 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525531 | TOLK 6230.00 | 230 | 28.7136 | 28.7136 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525549 | TOLK 7345.00 | 345 | 13.777 | 13.777 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525722 | OXY_ANTN_TP269.000 | 69 | 2.0615 | 2.0615 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525723 | CNTYLINE_TP269.000 | 69 | 2.3121 | 2.3121 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525724 | COUNTYLINE 269.000 | 69 | 2.0573 | 2.0573 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525730 | SP-ABTHY+ 269.000 | 69 | 2.9594 | 2.9594 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525731 | SP-ABERNTH+269.000 | 69 | 3.1607 | 3.1607 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525732 | SP-ABERNTHY269.000 | 69 | 3.1586 | 3.1586 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525733 | SP-CNTYLINE269.000 | 69 | 1.8975 | 1.8975 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525734 | SP-CTN_CNTR269.000 | 69 | 1.8189 | 1.8189 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525738 | HALECENTER 269.000 | 69 | 2.6265 | 2.6265 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525744 | LH-HALECTR 269.000 | 69 | 1.2936 | 1.2936 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525745 | LH-HALECTR+269.000 | 69 | 1.5569 | 1.5569 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525750 | G18-015-TAP 345.00 | 345 | 4.9171 | 4.9171 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525816 | TUCO_INT2 269.000 | 69 | 4.8872 | 4.8872 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525826 | TUCO_INT 269.000 | 69 | 8.2526 | 8.2526 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525828 | TUCO_INT 3115.00 | 115 | 20.3986 | 20.3986 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525830 | TUCO_INT 6230.00 | 230 | 23.8611 | 23.8611 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525831 | TUCO_SVC 6230.00 | 230 | 23.8611 | 23.8611 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525832 | TUCO_INT 7345.00 | 345 | 15.2173 | 15.2173 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525839 | G17-151TAP 345.00 | 345 | 8.4174 | 8.4174 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525840 | ANTELOPE_1 6230.00 | 230 | 23.666 | 23.666 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525850 | ELK_CT1 345.00 | 345 | 15.0954 | 15.0954 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525851 | ELK_CT3 7345.00 | 345 | 15.0666 | 15.0666 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525853 | LH-WIL&ELN+269.000 | 69 | 2.6685 | 2.6685 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525854 | LH-WILSON 269.000 | 69 | 2.0649 | 2.0649 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525855 | LH-ELLEN 269.000 | 69 | 1.4524 | 1.4524 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525859 | SP-BECTON+ 269.000 | 69 | 1.756 | 1.756 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525860 | SP-BECTONTP269.000 | 69 | 2.3681 | 2.3681 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525885 | SP-NEWDEAL 269.000 | 69 | 3.8814 | 3.8814 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525891 | WHITEHEAD 269.000 | 69 | 3.065 | 3.065 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525892 | MONROE 269.000 | 69 | 3.1707 | 3.1707 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525898 | SP-SHALLWTR269.000 | 69 | 2.4284 | 2.4284 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525899 | SP-SHALWTR+269.000 | 69 | 2.56 | 2.56 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 525957 | HALE_WNDCL16230.00 | 230 | 11.3301 | 11.3301 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 526073 | STANTON_N 269.000 | 69 | 2.0992 | 2.0992 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 526161 | CARLISLE 6230.00 | 230 | 11.0254 | 11.0254 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 526337 | JONES 6230.00 | 230 | 17.4896 | 17.4896 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 526936 | YOAKUM_345 345.00 | 345 | 12.0978 | 12.0978 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 531512 | HARBNGR7 345.00 | 345 | 6.4948 | 6.4948 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 532780 | CANEYRV7 345.00 | 345 | 9.7877 | 9.7877 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 532784 | NINN1WF7 345.00 | 345 | 5.917 | 5.917 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 532785 | PRATTWF7 345.00 | 345 | 4.933 | 4.933 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 532793 | NEOSHO 7 345.00 | 345 | 17.9597 | 17.9597 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 532937 | NEOSHO 5 161.00 | 161 | 23.1106 | 23.1106 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 533021 | NEOSHO 4 138.00 | 138 | 24.8503 | 24.8503 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539813 | TRANSFORMER 345.00 | 345 | 9.4366 | 9.4366 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539816 | SADDLE7 345.00 | 345 | 9.8038 | 9.8038 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539823 | IRONSTAR7 345.00 | 345 | 8.6262 | 8.6262 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539824 | IRS7 115 KV 115.00 | 115 | 12.6158 | 12.6158 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539841 | G-2011-008-1345.00 | 345 | 7.8188 | 7.8188 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539855 | G-2011-008-2345.00 | 345 | 7.7692 | 7.7692 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 539857 | G-2011-008-3345.00 | 345 | 7.2769 | 7.2769 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 542981 | LACYGNE7 345.00 | 345 | 26.235 | 26.235 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 543023 | LACYGNE_LK2 69.000 | 69 | 2.674 | 2.674 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 543629 | LACYGNE11_7 345.00 | 345 | 25.5787 | 25.5787 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 543632 | LACYGNE22_7 345.00 | 345 | 25.5787 | 25.5787 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 543659 | LACYGNE2 69.000 | 69 | 2.8127 | 2.8127 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 547484 | DEC392 5 161.00 | 161 | 15.6376 | 15.6376 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 547504 | GENTRY 161.00 | 161 | 20.6924 | 20.6924 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 549969 | BROOKLINE 5161.00 | 161 | 26.8898 | 26.8898 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 549984 | BROOKLINE 7345.00 | 345 | 11.9017 | 11.9017 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 580555 | MONETT345 345.00 | 345 | 9.5864 | 9.5864 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 588838 | G17-092-SWYD345.00 | 345 | 20.5057 | 20.5057 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 589300 | GEN-2017-092345.00 | 345 | 16.4601 | 16.4601 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 760389 | GEN-2017-140345.00 | 345 | 1.9351 | 1.9351 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 760393 | G17-140-BUS 345.00 | 345 | 1.9218 | 1.9218 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 760938 | G17-171-TAP 345.00 | 345 | 12.4167 | 12.4167 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 760939 | GEN-2017-171345.00 | 345 | 12.3432 | 12.3432 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762132 | GEN-2017-158230.00 | 230 | 12.4876 | 12.4876 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762217 | GEN-2017-151345.00 | 345 | 5.9675 | 5.9675 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762460 | GEN-2018-015345.00 | 345 | 4.9073 | 4.9073 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762592 | GEN-2018-024345.00 | 345 | 19.8534 | 19.8534 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762823 | GEN-2018-048345.00 | 345 | 18.027 | 18.027 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762834 | GEN-2018-049345.00 | 345 | 6.8915 | 6.8915 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762845 | GEN-2018-050345.00 | 345 | 15.7792 | 15.7792 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 762999 | GEN-2018-06469.000 | 69 | 4.3947 | 4.3947 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 763109 | GEN-2018-079138.00 | 138 | 7.0285 | 7.0285 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 763113 | G18-079-TAP 138.00 | 138 | 9.5689 | 9.5689 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 763318 | GEN-2018-115345.00 | 345 | 15.2023 | 15.2023 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 763472 | GEN-2019-002161.00 | 161 | 42.6461 | 42.6461 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 763516 | GEN-2019-011345.00 | 345 | 11.1937 | 11.1937 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 764120 | GEN-2020-081345.00 | 345 | 8.0459 | 8.0459 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 764550 | G20-087-TAP 345.00 | 345 | 15.1701 | 15.1701 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 764555 | GEN-2020-087345.00 | 345 | 15.1597 | 15.1597 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 764935 | GEN-2020-067345.00 | 345 | 6.5505 | 6.5505 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 764945 | G20-067-TAP 345.00 | 345 | 8.1085 | 8.1085 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 764980 | GEN-2020-008345.00 | 345 | 6.5005 | 6.5005 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 765190 | GEN-2020-090345.00 | 345 | 8.9058 | 8.9058 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 765200 | G20-090-TAP 345.00 | 345 | 10.2995 | 10.2995 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 765490 | GEN-2021-021345.00 | 345 | 6.1421 | 6.1421 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 765530 | GEN-2021-025138.00 | 138 | 17.8513 | 17.8513 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 765660 | GEN-2021-038345.00 | 345 | 22.7554 | 22.7554 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 765721 | G21-047-TAP 345.00 | 345 | 16.1137 | 16.1137 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 766120 | GEN-2021-090345.00 | 345 | 12.0226 | 12.0226 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 767101 | GEN-2022-006161.00 | 161 | 18.8191 | 18.8191 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 767240 | G22-013-TAP 345.00 | 345 | 11.3558 | 11.3558 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 767740 | G22-038-TAP 138.00 | 138 | 16.3601 | 16.3601 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 767741 | GEN-2022-038138.00 | 138 | 15.3492 | 15.3492 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 768061 | GEN-2022-054345.00 | 345 | 9.1346 | 9.1346 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 769201 | GEN-2022-111345.00 | 345 | 16.1557 | 16.1557 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 769761 | GEN-2022-139345.00 | 345 | 15.6956 | 15.6956 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 772280 | G23-015-TAP 345.00 | 345 | 8.1636 | 8.1636 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 772281 | GEN-2023-015345.00 | 345 | 7.7524 | 7.7524 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 773081 | GEN-2023-055161.00 | 161 | 29.8853 | 29.8853 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 776060 | G23-204-TAP 345.00 | 345 | 18.2312 | 18.2312 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 776061 | GEN-2023-204345.00 | 345 | 18.2151 | 18.2151 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 800101 | NBRAN161 161.00 | 161 | 19.4615 | 19.4615 | 0
GEN-2026-PR12 | 04 SOUTHEAST | 800102 | NBRAN345 345.00 | 345 | 6.7025 | 6.7025 | 0

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR12 | 2.7844 | FAIL | 0.6695 | PASS | N/A | N/A | Yes

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | Base Case | 8.3198 | PASS | 0.71307 | PASS | 613.0652 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514719 [CLYDE 2 69.00] TO BUS 514736 [4CORNER2 69.00] CKT 1 | 8.1713 | PASS | 0.71385 | PASS | 613.8544 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514719 [CLYDE 2 69.00] TO BUS 515547 [GRANTCO2 69.00] CKT 1 | 8.1705 | PASS | 0.71408 | PASS | 614.0765 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514728 [SINCBLK2 69.00] TO BUS 515509 [SNCBLKT2 69.00] CKT 1 | 8.3178 | PASS | 0.71324 | PASS | 613.2391 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514739 [MEDFORD2 69.00] TO BUS 514740 [NUMAOGE2 69.00] CKT 1 | 5.8582 | PASS | 0.71556 | PASS | 615.5645 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514739 [MEDFORD2 69.00] TO BUS 515547 [GRANTCO2 69.00] CKT 1 | 5.7522 | PASS | 0.72227 | PASS | 622.2723 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514740 [NUMAOGE2 69.00] TO BUS 514741 [DEERCK 2 69.00] CKT 1 | 5.8418 | PASS | 0.71631 | PASS | 616.3067 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514740 [NUMAOGE2 69.00] TO BUS 521013 [NUMA 2 69.00] CKT 1 | 8.3141 | PASS | 0.71356 | PASS | 613.5637 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514741 [DEERCK 2 69.00] TO BUS 515528 [NARDINS2 69.00] CKT 1 | 5.8424 | PASS | 0.71587 | PASS | 615.8711 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514750 [BRMAN 2 69.00] TO BUS 514751 [NEWKRKT2 69.00] CKT 1 | 8.3203 | PASS | 0.713 | PASS | 613.0039 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514750 [BRMAN 2 69.00] TO BUS 514756 [CHIKASI2 69.00] CKT 1 | 8.3206 | PASS | 0.71296 | PASS | 612.9568 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514750 [BRMAN 2 69.00] TO BUS 520871 [BRAMAN 2 69.00] CKT 1 | 8.3201 | PASS | 0.71303 | PASS | 613.0261 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514752 [TONKAWA2 69.00] TO BUS 514754 [KAYCOOP2 69.00] CKT 1 | 7.8407 | PASS | 0.71451 | PASS | 614.5095 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514754 [KAYCOOP2 69.00] TO BUS 514755 [BLACKWL2 69.00] CKT 1 | 7.8394 | PASS | 0.71474 | PASS | 614.7359 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514754 [KAYCOOP2 69.00] TO BUS 520837 [BLACKWE2 69.00] CKT 1 | 8.3185 | PASS | 0.71332 | PASS | 613.3226 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514755 [BLACKWL2 69.00] TO BUS 514756 [CHIKASI2 69.00] CKT 1 | 7.8395 | PASS | 0.71473 | PASS | 614.7258 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514756 [CHIKASI2 69.00] TO BUS 515509 [SNCBLKT2 69.00] CKT 1 | 2.8263 | FAIL | 0.71996 | PASS | 619.9597 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514756 [CHIKASI2 69.00] TO BUS 529255 [OMBLKWL2 69.00] CKT 1 | 8.3116 | PASS | 0.71451 | PASS | 614.507 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 514760 [KILDARE4 138.00] CKT 1 | 7.12 | PASS | 0.71237 | PASS | 612.3668 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 515581 [COYOTE 4 138.00] CKT 1 | 8.0432 | PASS | 0.71258 | PASS | 612.5848 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514759 [NEWKIRK4 138.00] TO BUS 514764 [NWKRKAT4 138.00] CKT 1 | 8.1668 | PASS | 0.71313 | PASS | 613.1336 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514759 [NEWKIRK4 138.00] TO BUS 515381 [PECKHMT4 138.00] CKT 1 | 8.1671 | PASS | 0.71298 | PASS | 612.9821 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514759 [NEWKIRK4 138.00] TO BUS 529290 [OMNUKRK4 138.00] CKT 1 | 8.3196 | PASS | 0.71316 | PASS | 613.1557 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 7.7921 | PASS | 0.71043 | PASS | 610.4262 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514764 [NWKRKAT4 138.00] CKT 1 | 8.1661 | PASS | 0.71331 | PASS | 613.3086 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514764 [NWKRKAT4 138.00] TO BUS 521012 [NEWKIR-WFEC4 138.00] CKT 1 | 8.3194 | PASS | 0.71323 | PASS | 613.2276 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515426 [RDRUNNR4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 8.0376 | PASS | 0.71333 | PASS | 613.333 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515426 [RDRUNNR4 138.00] TO BUS 515581 [COYOTE 4 138.00] CKT 1 | 8.0422 | PASS | 0.7128 | PASS | 612.8006 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515478 [BLKWLWD2 69.00] TO BUS 515528 [NARDINS2 69.00] CKT 1 | 8.1617 | PASS | 0.6695 | PASS | 569.5002 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515509 [SNCBLKT2 69.00] TO BUS 515528 [NARDINS2 69.00] CKT 1 | 2.8223 | FAIL | 0.72012 | PASS | 620.1217 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515546 [GRANTCO4 138.00] CKT 1 | 7.0089 | PASS | 0.71564 | PASS | 615.6397 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 8.0363 | PASS | 0.71336 | PASS | 613.3613 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 520409 [WFEC_RNFRO4 138.00] CKT 1 | 8.2602 | PASS | 0.71328 | PASS | 613.2788 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515581 [COYOTE 4 138.00] TO BUS 520447 [BLUFCRK4 138.00] CKT 1 | 8.3202 | PASS | 0.713 | PASS | 613.0034 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514736 [4CORNER2 69.00] TO BUS 515638 [HILLSDT2 69.00] CKT 1 | 8.1719 | PASS | 0.71361 | PASS | 613.6107 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514752 [TONKAWA2 69.00] TO BUS 514762 [3SANDS 2 69.00] CKT 1 | 7.8457 | PASS | 0.71378 | PASS | 613.7849 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514752 [TONKAWA2 69.00] TO BUS 529320 [OMOWEN 2 69.00] CKT 1 | 8.3174 | PASS | 0.71361 | PASS | 613.6057 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514756 [CHIKASI2 69.00] TO BUS 514757 [CHIKASI4 138.00] TO BUS 515713 [CHIKASI1 13.2] CKT 2 | 4.9386 | PASS | 0.71038 | PASS | 610.3802 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 514743 [OSAGE 4 138.00] CKT 1 | 8.3003 | PASS | 0.71304 | PASS | 613.0361 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 514748 [CONTEMP4 138.00] CKT 1 | 8.3143 | PASS | 0.71322 | PASS | 613.2237 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 8.2532 | PASS | 0.71259 | PASS | 612.5945 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515381 [PECKHMT4 138.00] TO BUS 514804 [MIDLTNT4 138.00] CKT 1 | 8.1673 | PASS | 0.71294 | PASS | 612.9391 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515381 [PECKHMT4 138.00] TO BUS 520450 [NWBRAMN4 138.00] CKT 1 | 8.3198 | PASS | 0.71311 | PASS | 613.1122 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515426 [RDRUNNR4 138.00] TO BUS 515427 [RCKFALL4 138.00] CKT 1 | 8.3252 | PASS | 0.71461 | PASS | 614.611 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515478 [BLKWLWD2 69.00] TO BUS 515483 [BLKWLWD1 34.5.00] TO BUS 515498 [BLKWLWDT 6.9] CKT 1 | 8.1615 | PASS | 0.66974 | PASS | 569.7376 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 8.1935 | PASS | 0.70613 | PASS | 606.1259 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 8.3183 | PASS | 0.71213 | PASS | 612.1308 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 8.2268 | PASS | 0.71379 | PASS | 613.7909 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.8] CKT 2 | 7.5386 | PASS | 0.71313 | PASS | 613.1301 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515546 [GRANTCO4 138.00] TO BUS 515547 [GRANTCO2 69.00] TO BUS 515548 [GRANTC11 13.2] CKT 4 | 6.9887 | PASS | 0.71716 | PASS | 617.1575 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 522397 [MEDFORD4 138.00] CKT 1 | 8.3199 | PASS | 0.71305 | PASS | 613.0484 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 520409 [WFEC_RNFRO4 138.00] TO BUS 520434 [WAKTASW4 138.00] CKT 1 | 8.2601 | PASS | 0.7133 | PASS | 613.2975 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | Base Case | 8.218 | PASS | 0.68598 | PASS | 585.9826 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514719 [CLYDE 2 69.00] TO BUS 514736 [4CORNER2 69.00] CKT 1 | 8.0699 | PASS | 0.68646 | PASS | 586.461 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514719 [CLYDE 2 69.00] TO BUS 515547 [GRANTCO2 69.00] CKT 1 | 8.0693 | PASS | 0.68663 | PASS | 586.626 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514728 [SINCBLK2 69.00] TO BUS 515509 [SNCBLKT2 69.00] CKT 1 | 8.2163 | PASS | 0.68612 | PASS | 586.1226 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514739 [MEDFORD2 69.00] TO BUS 514740 [NUMAOGE2 69.00] CKT 1 | 5.7718 | PASS | 0.68595 | PASS | 585.9488 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514739 [MEDFORD2 69.00] TO BUS 515547 [GRANTCO2 69.00] CKT 1 | 5.6574 | PASS | 0.69268 | PASS | 592.6787 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514740 [NUMAOGE2 69.00] TO BUS 514741 [DEERCK 2 69.00] CKT 1 | 5.7669 | PASS | 0.68609 | PASS | 586.094 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514740 [NUMAOGE2 69.00] TO BUS 521013 [NUMA 2 69.00] CKT 1 | 8.2164 | PASS | 0.68611 | PASS | 586.1057 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514741 [DEERCK 2 69.00] TO BUS 515528 [NARDINS2 69.00] CKT 1 | 5.7731 | PASS | 0.68522 | PASS | 585.2192 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514750 [BRMAN 2 69.00] TO BUS 514751 [NEWKRKT2 69.00] CKT 1 | 8.2184 | PASS | 0.68592 | PASS | 585.9236 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514750 [BRMAN 2 69.00] TO BUS 514756 [CHIKASI2 69.00] CKT 1 | 8.2188 | PASS | 0.68588 | PASS | 585.8782 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514750 [BRMAN 2 69.00] TO BUS 520871 [BRAMAN 2 69.00] CKT 1 | 8.2182 | PASS | 0.68594 | PASS | 585.945 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514752 [TONKAWA2 69.00] TO BUS 514754 [KAYCOOP2 69.00] CKT 1 | 7.7483 | PASS | 0.68755 | PASS | 587.5478 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514754 [KAYCOOP2 69.00] TO BUS 514755 [BLACKWL2 69.00] CKT 1 | 7.7494 | PASS | 0.6875 | PASS | 587.5033 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514754 [KAYCOOP2 69.00] TO BUS 520837 [BLACKWE2 69.00] CKT 1 | 8.218 | PASS | 0.68601 | PASS | 586.0071 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514755 [BLACKWL2 69.00] TO BUS 514756 [CHIKASI2 69.00] CKT 1 | 7.7494 | PASS | 0.68749 | PASS | 587.4936 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514756 [CHIKASI2 69.00] TO BUS 515509 [SNCBLKT2 69.00] CKT 1 | 2.7875 | FAIL | 0.68969 | PASS | 589.6916 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514756 [CHIKASI2 69.00] TO BUS 529255 [OMBLKWL2 69.00] CKT 1 | 8.2135 | PASS | 0.68674 | PASS | 586.736 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 514760 [KILDARE4 138.00] CKT 1 | 7.022 | PASS | 0.68489 | PASS | 584.8919 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 515581 [COYOTE 4 138.00] CKT 1 | 7.9425 | PASS | 0.68632 | PASS | 586.3158 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514759 [NEWKIRK4 138.00] TO BUS 514764 [NWKRKAT4 138.00] CKT 1 | 8.0635 | PASS | 0.68584 | PASS | 585.8437 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514759 [NEWKIRK4 138.00] TO BUS 515381 [PECKHMT4 138.00] CKT 1 | 8.0637 | PASS | 0.6858 | PASS | 585.7955 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514759 [NEWKIRK4 138.00] TO BUS 529290 [OMNUKRK4 138.00] CKT 1 | 8.2178 | PASS | 0.68603 | PASS | 586.0329 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 7.6958 | PASS | 0.6845 | PASS | 584.504 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514764 [NWKRKAT4 138.00] CKT 1 | 8.0633 | PASS | 0.68593 | PASS | 585.9293 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514764 [NWKRKAT4 138.00] TO BUS 521012 [NEWKIR-WFEC4 138.00] CKT 1 | 8.2178 | PASS | 0.68606 | PASS | 586.0598 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515426 [RDRUNNR4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 7.9346 | PASS | 0.68613 | PASS | 586.131 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515426 [RDRUNNR4 138.00] TO BUS 515581 [COYOTE 4 138.00] CKT 1 | 7.9412 | PASS | 0.68658 | PASS | 586.5845 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515478 [BLKWLWD2 69.00] TO BUS 515528 [NARDINS2 69.00] CKT 1 | 8.1837 | PASS | 0.69759 | PASS | 597.5874 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515509 [SNCBLKT2 69.00] TO BUS 515528 [NARDINS2 69.00] CKT 1 | 2.7844 | FAIL | 0.68981 | PASS | 589.8108 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515546 [GRANTCO4 138.00] CKT 1 | 6.9027 | PASS | 0.68775 | PASS | 587.7508 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 7.9328 | PASS | 0.68616 | PASS | 586.1553 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 520409 [WFEC_RNFRO4 138.00] CKT 1 | 8.1577 | PASS | 0.68616 | PASS | 586.1558 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515581 [COYOTE 4 138.00] TO BUS 520447 [BLUFCRK4 138.00] CKT 1 | 8.2185 | PASS | 0.68591 | PASS | 585.9111 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514736 [4CORNER2 69.00] TO BUS 515638 [HILLSDT2 69.00] CKT 1 | 8.0703 | PASS | 0.68631 | PASS | 586.3114 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514752 [TONKAWA2 69.00] TO BUS 514762 [3SANDS 2 69.00] CKT 1 | 7.7512 | PASS | 0.6871 | PASS | 587.0972 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514752 [TONKAWA2 69.00] TO BUS 529320 [OMOWEN 2 69.00] CKT 1 | 8.2162 | PASS | 0.68632 | PASS | 586.3226 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514756 [CHIKASI2 69.00] TO BUS 514757 [CHIKASI4 138.00] TO BUS 515713 [CHIKASI1 13.2] CKT 2 | 4.8279 | PASS | 0.68322 | PASS | 583.2226 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 514743 [OSAGE 4 138.00] CKT 1 | 8.1993 | PASS | 0.68593 | PASS | 585.9342 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 514748 [CONTEMP4 138.00] CKT 1 | 8.2127 | PASS | 0.68614 | PASS | 586.1353 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 8.1498 | PASS | 0.68586 | PASS | 585.8599 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515381 [PECKHMT4 138.00] TO BUS 514804 [MIDLTNT4 138.00] CKT 1 | 8.0636 | PASS | 0.68582 | PASS | 585.8219 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515381 [PECKHMT4 138.00] TO BUS 520450 [NWBRAMN4 138.00] CKT 1 | 8.218 | PASS | 0.68598 | PASS | 585.9764 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515426 [RDRUNNR4 138.00] TO BUS 515427 [RCKFALL4 138.00] CKT 1 | 8.2259 | PASS | 0.6886 | PASS | 588.6014 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515478 [BLKWLWD2 69.00] TO BUS 515483 [BLKWLWD1 34.5.00] TO BUS 515498 [BLKWLWDT 6.9] CKT 1 | 8.1835 | PASS | 0.69784 | PASS | 597.8382 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 8.0932 | PASS | 0.68286 | PASS | 582.8597 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 8.2175 | PASS | 0.68568 | PASS | 585.6812 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 8.1344 | PASS | 0.68637 | PASS | 586.3658 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.8] CKT 2 | 7.4342 | PASS | 0.68482 | PASS | 584.8203 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515546 [GRANTCO4 138.00] TO BUS 515547 [GRANTCO2 69.00] TO BUS 515548 [GRANTC11 13.2] CKT 4 | 6.8888 | PASS | 0.68875 | PASS | 588.7538 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 522397 [MEDFORD4 138.00] CKT 1 | 8.2181 | PASS | 0.68596 | PASS | 585.9603 | 11.96 | 14.1
GEN-2026-PR12 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR12 | 69kV Bus at OGE NARDINS Substation, Kay County, OK | OPEN LINE FROM BUS 520409 [WFEC_RNFRO4 138.00] TO BUS 520434 [WAKTASW4 138.00] CKT 1 | 8.1575 | PASS | 0.68617 | PASS | 586.1739 | 11.96 | 14.1

## WSCR
* WSCR is not applicable for this study.