## Executive Summary
Executive Summary: Group 04 GEN-2026-PR13 Priority Process Study
Interconnection Customer GEN-2026-PR13 (Group 04) has requested an Interconnection Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR13 generation for total of:
25.96 MW
The minimum cost of interconnecting GEN-2026-PR13 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Light: 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR13 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 07/30/2026
Costs for Wind Requests were allocated using the 29L (light load) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4623300% | SPP | Steady State Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR13 | 04 SOUTHEAST | 34 | Priority Process | Wind | 25.96 | 0 | 0 | 0 | 0 | 0 | 0 | 25.96 | 25.96 | -20.21 | ER | OG&E | Minco 345kV Substation | SPECIAL STUDY
GEN-2026-PR12 | 04 SOUTHEAST | 33 | Priority Process | Wind | 11.96 | [9 empty] | ER | OG&E | NARDINS2 69kV | SPECIAL STUDY
GEN-2026-PR11 | 05 SOUTHWEST | 37 | Priority Process | Wind | 30 | [9 empty] | ER | SPS | Lost Draw 3 115kV substation | SPECIAL STUDY
GEN-2026-PR9 | 05 SOUTHWEST | 35 | Priority Process | Wind | 15.99 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | SPECIAL STUDY
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | [9 empty] | ER | MIDW | South Hays 230kV | SPECIAL STUDY
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | SPECIAL STUDY
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | SPECIAL STUDY
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | SPECIAL STUDY
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | SPECIAL STUDY
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | SPECIAL STUDY
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 25SP | Stability 25WP
GEN-2026-PR13 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 25.96 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 25.96 | 25.96
GEN-2026-PR13 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 25.96 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 25.96 | 25.96
GEN-2026-PR13 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 25.96 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 25.96 | N/A
GEN-2026-PR13 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 25.96 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 25.96 | N/A
GEN-2026-PR13 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 25.96 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 25.96 | 25.96
GEN-2026-PR13 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 25.96 | 0 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 ftlo System Intact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 25.96 | 25.96
GEN-2026-PR13 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 25.96 | 25.96 | None | N/A | N/A | N/A | N/A | 25.96 | N/A | N/A | N/A | N/A | N/A | 25.96
GEN-2026-PR13 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 25.96 | 25.96 | None | N/A | N/A | N/A | N/A | 25.96 | N/A | N/A | N/A | N/A | N/A | 25.96

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR13 PSIS | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | System Intact | 829 | 829 | 100.8 | 100.95 |  |  |  | Rebuild the DELWARE7 to G24-240-TAP 345kV Line 1
04ALL | GEN-2026-PR13 PSIS | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP, 29SP | System Intact | 829 | 829 | 113.22 | 113.36 |  |  |  | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
04ALL | GEN-2026-PR13 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 127.86 | 128.11 |  |  |  | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
04ALL | GEN-2026-PR13 PSIS | ERIS | Thermal | None | 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS CF | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 26SP, 29L, 29SP | System Intact | 830 | 830 | 121.07 | 121.36 |  |  |  | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR13 PSIS CF | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 26SP, 29L, 29SP | System Intact | 830 | 830 | 121.03 | 121.32 |  |  |  | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
04ALL | GEN-2026-PR13 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS CF | ERIS | Thermal | None | 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None
04ALL | GEN-2026-PR13 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR13 | GEN-2026-PR13 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | 0 | 0% | 81488001.7662 | 0.05162
GEN-2026-PR13 | GEN-2026-PR13 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1 | Contingent | Rebuild the existing NEOSHO 7 to G24-240-TAP 345 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | 0 | 0% | 93984000 | 0.0195
GEN-2026-PR13 | GEN-2026-PR13 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the DELWARE7 to G24-240-TAP 345kV Line 1 | Contingent | Rebuild the existing DELWARE7 to G24-240-TAP 345 kV line 1 (5.3 miles) to a minimum rating of 1793 MVA | 0 | 0% | 11660000 | 0.0195
GEN-2026-PR13 | GEN-2026-PR13 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | Contingent | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1793 MVA | 0 | 0% | 81488001.7662 | 0.0139
GEN-2026-PR13 | GEN-2026-PR13 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1 | Contingent | Rebuild the existing VIOLA 7 to G18-128-TAP 345 kV line 1 (11.39 miles) to a minimum rating of 1793 MVA | 0 | 0% | 93984000 | 0.0139
GEN-2026-PR13 | GEN-2026-PR13 PSIS | 04 SOUTHEAST | TBD | ERIS | MInco 345kV Substation GEN-2026-PR13 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR13 (25.96/Wind), into Minco 345kV Substation | TBD | 100% | TBD | 1
GEN-2026-PR13 | GEN-2026-PR13 PSIS | 04 SOUTHEAST | TBD | ERIS | Minco 345kV Substation GEN-2026-PR13 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR13 (25.96/Wind), into Minco 345kV Substation | TBD | 100% | TBD | 1
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR13 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | WERE | 36 | 81488001.7662
Contingent | GEN-2026-PR13 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1 | TBD | Rebuild the existing NEOSHO 7 to G24-240-TAP 345 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | WERE/AEPW | 36 | 93984000
Contingent | GEN-2026-PR13 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the DELWARE7 to G24-240-TAP 345kV Line 1 | TBD | Rebuild the existing DELWARE7 to G24-240-TAP 345 kV line 1 (5.3 miles) to a minimum rating of 1793 MVA | AEPW | 36 | 11660000
Contingent | GEN-2026-PR13 PSIS CF | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing RENFROW7 to G18-128-TAP 345 kV line 1 (20.87 miles) to a minimum rating of 1793 MVA | OKGE/WERE | 36 | 81488001.7662
Contingent | GEN-2026-PR13 PSIS CF | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1 | TBD | Rebuild the existing VIOLA 7 to G18-128-TAP 345 kV line 1 (11.39 miles) to a minimum rating of 1793 MVA | WERE | 36 | 93984000
Interconnection | GEN-2026-PR13 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR13 PSIS | ERIS | MInco 345kV Substation GEN-2026-PR13 Interconnection (TOIF) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR13 (25.96/Wind), into Minco 345kV Substation | OKGE | TBD | TBD
Interconnection | GEN-2026-PR13 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR13 PSIS | ERIS | Minco 345kV Substation GEN-2026-PR13 Interconnection (Non-Shared NU) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR13 (25.96/Wind), into Minco 345kV Substation | OKGE | TBD | TBD
362604003.5324

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504194 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Minco 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Minco 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Minco | 2025 ITP | Yes | N/A | 0.18448 | 4821400% | 61500000
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504237 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Minco 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Minco 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Minco | 2025 ITP | Yes | N/A | 0.18448 | 4821400% | 1200600000
GEN-2026-PR13 | 04 SOUTHEAST | ER | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | N/A | 0.04642 | 4644600% | 16516041
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504296 | Build a 314.2-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole Install new 345/765 Ckt 1 & 2 transformers at Southwest Shreveport Install 765 kV substation at Southwest Shreveport Install 765 kV substation at Seminole Install new 345/765 Ckt 1 & 2 transformers at Seminole | Southwest Shreveport - Seminole 765 kV Ckt 1 New Line | Build a 314.2-mile 765 kV Ckt 1 line from Southwest Shreveport to Seminole | 2025 ITP | Yes | N/A | 0.05005 | 4690500% | 1044580000
GEN-2026-PR13 | 04 SOUTHEAST | ER | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | N/A | 0.04428 | 4600200% | 9509992
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504304 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward 345 kV Reactor | Install 225 MVAR reactor at Woodward 345 kV substation | 2025 ITP | Yes | N/A | 0.03139 | 4821400% | 104567202
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504308 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Minco - Seminole 765 kV Ckt 1 New Line | Build a 100-mile 765 kV Ckt 1 line from Minco to Seminole | 2025 ITP | Yes | N/A | 0.24727 | 4821400% | 104567202
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 170114 | Line - Woodward EHV - Beckham County 345 kV Ckt 1 New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | N/A | -0.03144 | 4821400% | 121500000
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504172 | Southwest Shreveport - Seminole 765 kV New Line Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Southwest Shreveport 765 kV New Substation Anthem 765 kV New Substation Minco 765 kV New Substation Seminole 765 kV New Substation Woodward 765 kV New Substation Crawfish Draw 765 kV New Substation Viola 765 kV New Substation Southwest Shreveport 345/765 kV New Transformer Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Seminole 345/765 kV New Transformer Viola 345/765 kV New Transformer | Minco - Crawfish Draw 765 kV Ckt 1 New Line | Build a 283.9-mile 765 kV Ckt 1 line from Minco to Crawfish Draw | 2025 ITP | Yes | N/A | 0.12169 | 4821400% | 1646620000
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504162 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem - Seminole 765 kV Ckt 1 New Line | Build a 131.4-mile 765 kV Ckt 1 line from Anthem to Seminole | 2025 ITP | Yes | N/A | 0.14194 | 4821400% | 762120000
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504279 | Woodward - Potter Co 765 kV New Line Woodward - Crawfish Draw 765 kV New Line Woodward 765 kV New Substation Woodward 345 kV New Reactor Woodward 765 kV New Reactor Potter Co 765 kV New Reactor Woodward 345/765 kV New Transformer | Woodward - Crawfish Draw 765 kV Ckt 1 New Line | Build a 263.6-mile 765 kV Ckt 1 line from Woodward to Crawfish Draw | 2025 ITP | Yes | N/A | -0.04638 | 4821400% | 1528880000
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504291 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 152.4-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | 0.03679 | 4821500% | 883920000
GEN-2026-PR13 | 04 SOUTHEAST | ER | TBD | 504296 | Anthem - Seminole 765 kV New Line Anthem - Viola 765 kV New Line Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Woodward - Viola 765 kV New Line Anthem 765 kV New Substation Minco 765 kV New Substation Viola 765 kV New Substation Anthem 345/765 kV New Transformer Minco 345/765 kV New Transformer Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 180.1-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | -0.05198 | 4821600% | 1044580000

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR13 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | -0.00054 | -0.014018 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00255 | -0.030498 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00093 | -0.0279 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00093 | -0.014871 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00032 | -0.012723 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00385 | 0.19142 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.00252 | 0.15221 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -5e-05 | -0.006578 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -5e-05 | -0.002484 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.00042 | 0.017594 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00041 | 0.021578 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00143 | 0.024453 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00155 | 0.0465 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00032 | -0.025536 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00032 | -0.032 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00469 | -0.22507 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | -0.00133 | -0.11438 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00011 | 0.014474 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00011 | 0.0132 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00014 | 0.01106 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00021 | 0.021462 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00012 | 0.0096 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00013 | 0.06448 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.0028 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.003 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.00062 | NO
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.00031 | NO

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR13 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR13 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.07068 | 115.71 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR13 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03262 | 104.66 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR13 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.06971 | 128.11 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR13 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.03195 | 113.36 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR13 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.0324 | 100.95 | System Intact | TDF Impact | Rebuild the DELWARE7 to G24-240-TAP 345kV Line 1
Non-Converged | GEN-2026-PR13 PSIS | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR13 PSIS | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR13 PSIS | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR13 PSIS | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR13 PSIS | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR13 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.0821 | 105.48 | System Intact | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 26SP | GEN-2026-PR13 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.0821 | 105.42 | System Intact | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR13 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.04418 | 121.36 | System Intact | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 29L | GEN-2026-PR13 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.04418 | 121.32 | System Intact | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR13 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.08095 | 115.31 | System Intact | TDF Impact | Rebuild the RENFROW7 to G18-128-TAP 345kV Line 1
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR13 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.08095 | 115.23 | System Intact | TDF Impact | Rebuild the VIOLA 7 to G18-128-TAP 345kV Line 1
Non-Converged | GEN-2026-PR13 PSIS CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR13 PSIS CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR13 PSIS CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR13 PSIS CF | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR13 PSIS CF | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR13 PSIS | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS CF | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR13 PSIS CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G23-229 (776564, 776567) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to 112GORE4 (511488) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on VERDEN 4 138.00 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 138.00 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 (511421) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 b.2. VERDEN 4 (511421) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 b.3. CORNVIL4 (511449) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMDUNCN4 138.00 (529304) 138 kV Bus a. Apply fault at the OMDUNCN4 138.00 (529304) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780817, 780814, 780820), WCGS U1 (532751) and COM2-1 (511825) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763321, 763324) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763321, 763324) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of KNGFRG21 (515665) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-362GEN2 (787837) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of KNGFRG21 (515665) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of KNGFRG21 (515665) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on OMEGA 4 138.00 (515962) 138 kV Bus a. Apply fault at the OMEGA 4 138.00 (515962) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.2. ROMNOSE4 (514823) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) and KNGFRG21 (515665)units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on JENSEN 4 138.00 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 138.00 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 (514821) 138.0 kV to EL RENO4 (520893) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the HSL 8G (514939) and MSTNG (515672, 515673, 515670, 515671 ) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the HSL 8G (514939) and MSTNG (515672, 515673, 515670, 515671 ) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-026 (762617) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of KNGFRG21 (515665) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WESTMOR4 138.00 (514887) 138 kV Bus a. Apply fault at the WESTMOR4 138.00 (514887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. WESTMOR4 (514887) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 b.3. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-026 (762617) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on OU TAP 4 138.00 (514931) 138 kV Bus a. Apply fault at the OU TAP 4 138.00 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 (514903) 138.0 kV to OU TAP 4 (514931) 138.0 kV Transmission Circuit #1 b.2. OU TAP 4 (514931) 138.0 kV to MLENIUM4 (514932) 138.0 kV Transmission Circuit #1 b.3. OU TAP 4 (514931) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.4. MLENIUM4 (514932) 138.0 kV to STUBMAN4 (514952) 138.0 kV Transmission Circuit #1 b.5. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on INDNHIL4 138.00 (514954) 138 kV Bus a. Apply fault at the INDNHIL4 138.00 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 (514904) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.2. HOLLYWD4 (514953) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.3. INDNHIL4 (514954) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 b.4. MOORE 4 (514955) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 b.5. MOORE 4 (514955) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SANTAFE4 138.00 (514926) 138 kV Bus a. Apply fault at the SANTAFE4 138.00 (514926) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV to SANTAFE4 (514926) 138.0 kV Transmission Circuit #1 b.2. SANTAFE4 (514926) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONRTP4 138.00 (514949) 138 kV Bus a. Apply fault at the SOONRTP4 138.00 (514949) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 (514930) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.2. OAKTRET4 (514930) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.4. CEDARLN4 (514948) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MIDWEST4 138.00 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 138.00 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.3. MIDWEST4 (514946) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on BARNES 4 138.00 (515003) 138 kV Bus a. Apply fault at the BARNES 4 138.00 (515003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. SE15TH 4 (514993) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.3. TINKER54 (514994) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 b.2. CANADN-4 (514947) 138.0 kV to NOBLE 4 (515007) 138.0 kV Transmission Circuit #1 b.3. CANADN-4 (514947) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.4. NOBLE 4 (515007) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 b.5. WLNUTCK4 (515097) 138.0 kV to PAOLI- 4 (515100) 138.0 kV Transmission Circuit #1 b.6. WLNUTCK4 (515097) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780817, 780814, 780820), WCGS U1 (532751) and COM2-1 (511825) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the HSL 8G (514939) and MSTNG (515672, 515673, 515670, 515671 ) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154GEN1 (781594) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-239 (384144) and G24-362 (787837) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-239 (384144) and G24-362 (787837) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837, 787834) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837, 787834) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780817, 780820), G18-115 (763324, 763321) and KNGFRG21 (515665) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780817, 780820), G18-115 (763324, 763321) and KNGFRG21 (515665) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780817, 780820), G18-115 (763324, 763321) and KNGFRG21 (515665) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 (514924) 69.0 kV to PENN 4 (514925) 138.0 kV to PENN 1 (515751) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on BOYD 4 138.00 (514958) 138 kV Bus a. Apply fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOYD 4 (514958) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in ORME3 (521112). The issue is observed in PQ case. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on CLVLDSW4 138.00 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 138.00 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 (520508) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.2. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.3. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.4. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 (521031) 138.0 kV to G22-055-TAP (768080) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on CORNVIL4 138.00 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 138.00 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 (511449) 138.0 kV to CORN TP4 (520867) 138.0 kV Transmission Circuit #1 b.2. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. NAPLSTP4 (520510) 138.0 kV to PAYNESW4 (520888) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on GOLDSBY4 138.00 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 138.00 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to GOLDSBY4 (520924) 138.0 kV Transmission Circuit #1 b.2. GOLDSBY4 (520924) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on LAMAR4 138.00 (520403) 138 kV Bus a. Apply fault at the LAMAR4 138.00 (520403) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 (520403) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 b.2. ACME 4 (520802) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on BAILEY4 138.00 (520401) 138 kV Bus a. Apply fault at the BAILEY4 138.00 (520401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 (520401) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to WMOORE 4 (521123) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on BINGER 4 138.00 (511405) 138 kV Bus a. Apply fault at the BINGER 4 138.00 (511405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGER 4 (511405) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763327, 763325) and RSHSPR-1-B (511976) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763327, 763325) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on CARNEG-4 138.00 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 138.00 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 (511445) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G21-064 (765892, 765895) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G20-020 (764511) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763321, 763324) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763321, 763324) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to NORGE--4 (511483) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G23-229 (776564, 776567) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G23-229 (776564, 776567) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to TONKAWA4 (511586) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G23-229 (776564, 776567) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-115 (763327) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on ACME 4 138.00 (520802) 138 kV Bus a. Apply fault at the ACME 4 138.00 (520802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 (520802) 138.0 kV to WNORMAN4 (521095) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on CANADNS4 138.00 (520842) 138 kV Bus a. Apply fault at the CANADNS4 138.00 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to LIL AXE4 (520976) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to PINK SW4 (521028) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) and G24-128 (780820, 780817, 780814) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to ANADARK2 (520810) 69.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on FRNKLNS4 138.00 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 138.00 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 (520917) 138.0 kV to FRNKLNS2 (520916) 69.0 kV to FRNKTERT (521169) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to WASHITA2 (521088) 69.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on OKLAUN HVDC7345.00 (511565) 345 kV Bus a. Apply fault at the OKLAUN HVDC7345.00 (511565) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN HVDC7 (511565) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on O.K.U.3-7 345.00 (511607) 345 kV Bus a. Apply fault at the O.K.U.3-7 345.00 (511607) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.3-7 (511607) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812) and NTHFGEN1 (521161) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Removing reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Removing reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.2. LES#4-1 (511414) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BOYD 4 138.00 (514958) 138 kV Bus a. Apply Fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.4. ANADARK4 (520814) 138.0 kV to GENCO1 (521101) 13.8 kV Two Winding #1 b.5. ANADARK4 (520814) 138.0 kV to GENCO2 (521102) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADRK6 (520813) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.2. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.4. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.5. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to MCLN 1S (514998) 18.0 kV Two Winding #1 b.3. MCCLAIN4 (514902) 138.0 kV to MCLN 1G (514999) 18.0 kV Two Winding #1 b.4. MCCLAIN4 (514902) 138.0 kV to MCLN 2G (515000) 18.0 kV Two Winding #1 b.5. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.6. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.7. MINCO 7 (514801) 345.0 kV to MINCO_IV__HV (914801) 345.0 kV Transmission Circuit #1 b.8. MINCO 7 (514801) 345.0 kV to MINCO_I_&_HV (914807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL2G (515041) 17.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G22-143 (769844) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL3G (515042) 20.9 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G22-143 (769844) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G22-143 (769844) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-255 (784624) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TREASILD7 345.00 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply Fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TURNER 4 138.00 (514992) 138 kV Bus a. Apply Fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to MINCO 7 (514801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GEN-2017-150345.00 (761229) 345 kV Bus a. Apply Fault at the GEN-2017-150345.00 (761229) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-150 (761229) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-150 (761229) 345.0 kV to G17-150XFMR1 (761230) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G20-087-TAP 345.00 (764550) 345 kV Bus a. Apply Fault at the G20-087-TAP 345.00 (764550) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-087-TAP (764550) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G20-087-TAP (764550) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on G24-128-TAP 345.00 (780810) 345 kV Bus a. Apply Fault at the G24-128-TAP 345.00 (780810) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. G24-128-TAP (780810) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NORMHLL7 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NORMHLL4 (516097) 138 kV Bus a. Apply Fault at the NORMHLL4 (516097) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL4 (516097) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on TREASILD7 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON4 (514898) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to remove bus # | P4 | Yes | Yes | No | Yes | No | Yes | Yes | OKLAUN HVDC7 (511565), O.K.U.-7 (511456), O.K.U2.-7 (511584), and O.K.U3.-7 (511607) exceeded the 1.2 p.u. voltage limit during both transient and post-fault conditions. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to GRACMNT4 (515802) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADRK5 (520812) 13.8 kV to Generator #1 b.5. ANADRK5 (520812) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_003 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_004 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_005 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.5. ANADRK5 (520812) 13.8 kV to Generator #1 b.6. ANADRK5 (520812) 13.8 kV to remove bus # b.7. TUTTLE 4 (520496) 138.0 kV to remove bus # b.8. BRIDGCR4 (520501) 138.0 kV to remove bus # b.9. POCASET4 (521031) 138.0 kV to remove bus # b.10. TUTLETP4 (521072) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_006 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_WFEC_FAULT_007 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_AEPW_FAULT_001 | Single Phase Fault with Stuck Breaker on LES (511467) 138 kV Bus a. Apply Fault at the LES (511467) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. RPPAPER4 (511512) 138.0 kV to LWSTAP 4 (511439) 138.0 kV Transmission Circuit #1 b.3. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.4. OMDUNCN4 (529304) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.5. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 b.6. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 b.7. SHERID4 (511474) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.8. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 b.9. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.10. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 b.11. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.12. S.W.S.-4 (511477) 138.0 kV to FLE TAP4 (511423) 138.0 kV Transmission Circuit #1 b.13. FLETCHR4 (511422) 138.0 kV to remove bus # b.14. FLE TAP4 (511423) 138.0 kV to remove bus # b.15. LWS S4 (511431) 138.0 kV to remove bus # b.16. LWSTAP 4 (511439) 138.0 kV to remove bus # b.17. COMMTAP4 (511494) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.4. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and G23-229 (776567) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and G23-229 (776567, 776567) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to 112GORE4 (511488) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on VERDEN 4 138.00 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 138.00 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 (511421) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 b.2. VERDEN 4 (511421) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 b.3. CORNVIL4 (511449) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMDUNCN4 138.00 (529304) 138 kV Bus a. Apply fault at the OMDUNCN4 138.00 (529304) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and BUFFCK0 (511967) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and G18-115 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-154 (781594) and G18-115 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-239 (784144), G24-362 (787837) and G24-360 (787777) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-026 (762617) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on OMEGA 4 138.00 (515962) 138 kV Bus a. Apply fault at the OMEGA 4 138.00 (515962) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.2. ROMNOSE4 (514823) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on JENSEN 4 138.00 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 138.00 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 (514821) 138.0 kV to EL RENO4 (520893) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory responses are observed in the power output of the G24-252 (784534), G24-255 (784624), G24-254 (784594), and MSTNG (515672, 515673, 515670, 515671) units along with reactive power oscillations in the surrounding area. This issue is also present in the base case. | Removing reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-362 (787837) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-362 (787837) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-362 (787837) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WESTMOR4 138.00 (514887) 138 kV Bus a. Apply fault at the WESTMOR4 138.00 (514887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. WESTMOR4 (514887) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 b.3. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on OU TAP 4 138.00 (514931) 138 kV Bus a. Apply fault at the OU TAP 4 138.00 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 (514903) 138.0 kV to OU TAP 4 (514931) 138.0 kV Transmission Circuit #1 b.2. OU TAP 4 (514931) 138.0 kV to MLENIUM4 (514932) 138.0 kV Transmission Circuit #1 b.3. OU TAP 4 (514931) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.4. MLENIUM4 (514932) 138.0 kV to STUBMAN4 (514952) 138.0 kV Transmission Circuit #1 b.5. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on INDNHIL4 138.00 (514954) 138 kV Bus a. Apply fault at the INDNHIL4 138.00 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 (514904) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.2. HOLLYWD4 (514953) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.3. INDNHIL4 (514954) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 b.4. MOORE 4 (514955) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 b.5. MOORE 4 (514955) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SANTAFE4 138.00 (514926) 138 kV Bus a. Apply fault at the SANTAFE4 138.00 (514926) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV to SANTAFE4 (514926) 138.0 kV Transmission Circuit #1 b.2. SANTAFE4 (514926) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONRTP4 138.00 (514949) 138 kV Bus a. Apply fault at the SOONRTP4 138.00 (514949) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 (514930) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.2. OAKTRET4 (514930) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.4. CEDARLN4 (514948) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MIDWEST4 138.00 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 138.00 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.3. MIDWEST4 (514946) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on BARNES 4 138.00 (515003) 138 kV Bus a. Apply fault at the BARNES 4 138.00 (515003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. SE15TH 4 (514993) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.3. TINKER54 (514994) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 b.2. CANADN-4 (514947) 138.0 kV to NOBLE 4 (515007) 138.0 kV Transmission Circuit #1 b.3. CANADN-4 (514947) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.4. NOBLE 4 (515007) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 b.5. WLNUTCK4 (515097) 138.0 kV to PAOLI- 4 (515100) 138.0 kV Transmission Circuit #1 b.6. WLNUTCK4 (515097) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-239 (784144), G24-362 (787837) and G24-360 (787777) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837) and G24-360 (787777) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-362 (787837) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837, 787834) and G24-360 (787777) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G24-362 (787837, 787834) and G24-360 (787777) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 (514924) 69.0 kV to PENN 4 (514925) 138.0 kV to PENN 1 (515751) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on BOYD 4 138.00 (514958) 138 kV Bus a. Apply fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOYD 4 (514958) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on CLVLDSW4 138.00 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 138.00 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 (520508) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.2. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.3. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.4. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 (521031) 138.0 kV to G22-055-TAP (768080) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on CORNVIL4 138.00 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 138.00 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 (511449) 138.0 kV to CORN TP4 (520867) 138.0 kV Transmission Circuit #1 b.2. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. NAPLSTP4 (520510) 138.0 kV to PAYNESW4 (520888) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on GOLDSBY4 138.00 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 138.00 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to GOLDSBY4 (520924) 138.0 kV Transmission Circuit #1 b.2. GOLDSBY4 (520924) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on LAMAR4 138.00 (520403) 138 kV Bus a. Apply fault at the LAMAR4 138.00 (520403) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 (520403) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 b.2. ACME 4 (520802) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on BAILEY4 138.00 (520401) 138 kV Bus a. Apply fault at the BAILEY4 138.00 (520401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 (520401) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to WMOORE 4 (521123) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on BINGER 4 138.00 (511405) 138 kV Bus a. Apply fault at the BINGER 4 138.00 (511405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGER 4 (511405) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763327, 763325), CDW-GEN1 (511923) and RSHSPR-1-B (511976) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763327, 763325) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on CARNEG-4 138.00 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 138.00 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 (511445) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G21-064 (765892, 765895) and G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-115 (763327) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763327) and RSHSPR-1-B (511976) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763321, 763324, 763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to NORGE--4 (511483) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G23-229 (776567) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G23-229 (776567) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to TONKAWA4 (511586) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G23-229 (776567) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-340 (787180, 787183, 787174, 787177) and WCGS (532751) units along with reactive power oscillations in the surrounding area. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G18-115 (763327) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780817, 780814, 780820) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on ACME 4 138.00 (520802) 138 kV Bus a. Apply fault at the ACME 4 138.00 (520802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 (520802) 138.0 kV to WNORMAN4 (521095) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on CANADNS4 138.00 (520842) 138 kV Bus a. Apply fault at the CANADNS4 138.00 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to LIL AXE4 (520976) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to PINK SW4 (521028) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to ANADARK2 (520810) 69.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on FRNKLNS4 138.00 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 138.00 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 (520917) 138.0 kV to FRNKLNS2 (520916) 69.0 kV to FRNKTERT (521169) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to WASHITA2 (521088) 69.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on OKLAUN HVDC7345.00 (511565) 345 kV Bus a. Apply fault at the OKLAUN HVDC7345.00 (511565) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN HVDC7 (511565) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on O.K.U.3-7 345.00 (511607) 345 kV Bus a. Apply fault at the O.K.U.3-7 345.00 (511607) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.3-7 (511607) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Remove reclosing and reduce clearing time to 2 cycles solve the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Remove reclosing and reduce clearing time to 2 cycles solve the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.2. LES#4-1 (511414) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BOYD 4 138.00 (514958) 138 kV Bus a. Apply Fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.4. ANADARK4 (520814) 138.0 kV to GENCO1 (521101) 13.8 kV Two Winding #1 b.5. ANADARK4 (520814) 138.0 kV to GENCO2 (521102) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADRK6 (520813) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (781594) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.2. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.4. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.5. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to MCLN 1S (514998) 18.0 kV Two Winding #1 b.3. MCCLAIN4 (514902) 138.0 kV to MCLN 1G (514999) 18.0 kV Two Winding #1 b.4. MCCLAIN4 (514902) 138.0 kV to MCLN 2G (515000) 18.0 kV Two Winding #1 b.5. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.6. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.7. MINCO 7 (514801) 345.0 kV to MINCO_IV__HV (914801) 345.0 kV Transmission Circuit #1 b.8. MINCO 7 (514801) 345.0 kV to MINCO_I_&_HV (914807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL2G (515041) 17.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704), G22-143 (769844) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL3G (515042) 20.9 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704), G22-143 (769844) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704), G22-143 (769844) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TREASILD7 345.00 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply Fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TURNER 4 138.00 (514992) 138 kV Bus a. Apply Fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to MINCO 7 (514801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GEN-2017-150345.00 (761229) 345 kV Bus a. Apply Fault at the GEN-2017-150345.00 (761229) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-150 (761229) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-150 (761229) 345.0 kV to G17-150XFMR1 (761230) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G20-087-TAP 345.00 (764550) 345 kV Bus a. Apply Fault at the G20-087-TAP 345.00 (764550) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-087-TAP (764550) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G20-087-TAP (764550) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on G24-128-TAP 345.00 (780810) 345 kV Bus a. Apply Fault at the G24-128-TAP 345.00 (780810) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. G24-128-TAP (780810) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NORMHLL7 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G22-136 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NORMHLL4 (516097) 138 kV Bus a. Apply Fault at the NORMHLL4 (516097) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL4 (516097) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on TREASILD7 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON4 (514898) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to GRACMNT4 (515802) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADRK5 (520812) 13.8 kV to Generator #1 b.5. ANADRK5 (520812) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_003 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_004 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_005 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.5. ANADRK5 (520812) 13.8 kV to Generator #1 b.6. ANADRK5 (520812) 13.8 kV to remove bus # b.7. TUTTLE 4 (520496) 138.0 kV to remove bus # b.8. BRIDGCR4 (520501) 138.0 kV to remove bus # b.9. POCASET4 (521031) 138.0 kV to remove bus # b.10. TUTLETP4 (521072) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_006 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_WFEC_FAULT_007 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_AEPW_FAULT_001 | Single Phase Fault with Stuck Breaker on LES (511467) 138 kV Bus a. Apply Fault at the LES (511467) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. RPPAPER4 (511512) 138.0 kV to LWSTAP 4 (511439) 138.0 kV Transmission Circuit #1 b.3. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.4. OMDUNCN4 (529304) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.5. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 b.6. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 b.7. SHERID4 (511474) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.8. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 b.9. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.10. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 b.11. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.12. S.W.S.-4 (511477) 138.0 kV to FLE TAP4 (511423) 138.0 kV Transmission Circuit #1 b.13. FLETCHR4 (511422) 138.0 kV to remove bus # b.14. FLE TAP4 (511423) 138.0 kV to remove bus # b.15. LWS S4 (511431) 138.0 kV to remove bus # b.16. LWSTAP 4 (511439) 138.0 kV to remove bus # b.17. COMMTAP4 (511494) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip G20-020 (769704) and G24-154 (763327) units. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.4. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G24-154 (763327) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to 112GORE4 (511488) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on VERDEN 4 138.00 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 138.00 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 (511421) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 b.2. VERDEN 4 (511421) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 b.3. CORNVIL4 (511449) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMDUNCN4 138.00 (529304) 138 kV Bus a. Apply fault at the OMDUNCN4 138.00 (529304) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Remove reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Gen-2026-PR13 will be islanded from the network after the fault. | No mitigation required
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on OMEGA 4 138.00 (515962) 138 kV Bus a. Apply fault at the OMEGA 4 138.00 (515962) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.2. ROMNOSE4 (514823) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on JENSEN 4 138.00 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 138.00 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 (514821) 138.0 kV to EL RENO4 (520893) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WESTMOR4 138.00 (514887) 138 kV Bus a. Apply fault at the WESTMOR4 138.00 (514887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. WESTMOR4 (514887) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 b.3. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on OU TAP 4 138.00 (514931) 138 kV Bus a. Apply fault at the OU TAP 4 138.00 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 (514903) 138.0 kV to OU TAP 4 (514931) 138.0 kV Transmission Circuit #1 b.2. OU TAP 4 (514931) 138.0 kV to MLENIUM4 (514932) 138.0 kV Transmission Circuit #1 b.3. OU TAP 4 (514931) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.4. MLENIUM4 (514932) 138.0 kV to STUBMAN4 (514952) 138.0 kV Transmission Circuit #1 b.5. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on INDNHIL4 138.00 (514954) 138 kV Bus a. Apply fault at the INDNHIL4 138.00 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 (514904) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.2. HOLLYWD4 (514953) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.3. INDNHIL4 (514954) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 b.4. MOORE 4 (514955) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 b.5. MOORE 4 (514955) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SANTAFE4 138.00 (514926) 138 kV Bus a. Apply fault at the SANTAFE4 138.00 (514926) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV to SANTAFE4 (514926) 138.0 kV Transmission Circuit #1 b.2. SANTAFE4 (514926) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONRTP4 138.00 (514949) 138 kV Bus a. Apply fault at the SOONRTP4 138.00 (514949) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 (514930) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.2. OAKTRET4 (514930) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.4. CEDARLN4 (514948) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MIDWEST4 138.00 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 138.00 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.3. MIDWEST4 (514946) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on BARNES 4 138.00 (515003) 138 kV Bus a. Apply fault at the BARNES 4 138.00 (515003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. SE15TH 4 (514993) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.3. TINKER54 (514994) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 b.2. CANADN-4 (514947) 138.0 kV to NOBLE 4 (515007) 138.0 kV Transmission Circuit #1 b.3. CANADN-4 (514947) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.4. NOBLE 4 (515007) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 b.5. WLNUTCK4 (515097) 138.0 kV to PAOLI- 4 (515100) 138.0 kV Transmission Circuit #1 b.6. WLNUTCK4 (515097) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 (514924) 69.0 kV to PENN 4 (514925) 138.0 kV to PENN 1 (515751) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on BOYD 4 138.00 (514958) 138 kV Bus a. Apply fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOYD 4 (514958) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on CLVLDSW4 138.00 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 138.00 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 (520508) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.2. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.3. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.4. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 (521031) 138.0 kV to G22-055-TAP (768080) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on CORNVIL4 138.00 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 138.00 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 (511449) 138.0 kV to CORN TP4 (520867) 138.0 kV Transmission Circuit #1 b.2. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. NAPLSTP4 (520510) 138.0 kV to PAYNESW4 (520888) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on GOLDSBY4 138.00 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 138.00 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to GOLDSBY4 (520924) 138.0 kV Transmission Circuit #1 b.2. GOLDSBY4 (520924) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on LAMAR4 138.00 (520403) 138 kV Bus a. Apply fault at the LAMAR4 138.00 (520403) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 (520403) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 b.2. ACME 4 (520802) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on BAILEY4 138.00 (520401) 138 kV Bus a. Apply fault at the BAILEY4 138.00 (520401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 (520401) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to WMOORE 4 (521123) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on BINGER 4 138.00 (511405) 138 kV Bus a. Apply fault at the BINGER 4 138.00 (511405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGER 4 (511405) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on CARNEG-4 138.00 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 138.00 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 (511445) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to NORGE--4 (511483) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to TONKAWA4 (511586) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on ACME 4 138.00 (520802) 138 kV Bus a. Apply fault at the ACME 4 138.00 (520802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 (520802) 138.0 kV to WNORMAN4 (521095) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on CANADNS4 138.00 (520842) 138 kV Bus a. Apply fault at the CANADNS4 138.00 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to LIL AXE4 (520976) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to PINK SW4 (521028) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G21-064 (765895) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to ANADARK2 (520810) 69.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on FRNKLNS4 138.00 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 138.00 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 (520917) 138.0 kV to FRNKLNS2 (520916) 69.0 kV to FRNKTERT (521169) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to WASHITA2 (521088) 69.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on OKLAUN HVDC7345.00 (511565) 345 kV Bus a. Apply fault at the OKLAUN HVDC7345.00 (511565) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN HVDC7 (511565) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on O.K.U.3-7 345.00 (511607) 345 kV Bus a. Apply fault at the O.K.U.3-7 345.00 (511607) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.3-7 (511607) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Remove reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.2. LES#4-1 (511414) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BOYD 4 138.00 (514958) 138 kV Bus a. Apply Fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.4. ANADARK4 (520814) 138.0 kV to GENCO1 (521101) 13.8 kV Two Winding #1 b.5. ANADARK4 (520814) 138.0 kV to GENCO2 (521102) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADRK6 (520813) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-128 (780820, 780817, 780814) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.2. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.4. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.5. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to MCLN 1S (514998) 18.0 kV Two Winding #1 b.3. MCCLAIN4 (514902) 138.0 kV to MCLN 1G (514999) 18.0 kV Two Winding #1 b.4. MCCLAIN4 (514902) 138.0 kV to MCLN 2G (515000) 18.0 kV Two Winding #1 b.5. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.6. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.7. MINCO 7 (514801) 345.0 kV to MINCO_IV__HV (914801) 345.0 kV Transmission Circuit #1 b.8. MINCO 7 (514801) 345.0 kV to MINCO_I_&_HV (914807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL2G (515041) 17.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL3G (515042) 20.9 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TREASILD7 345.00 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply Fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TURNER 4 138.00 (514992) 138 kV Bus a. Apply Fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to MINCO 7 (514801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GEN-2017-150345.00 (761229) 345 kV Bus a. Apply Fault at the GEN-2017-150345.00 (761229) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-150 (761229) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-150 (761229) 345.0 kV to G17-150XFMR1 (761230) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G20-087-TAP 345.00 (764550) 345 kV Bus a. Apply Fault at the G20-087-TAP 345.00 (764550) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-087-TAP (764550) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G20-087-TAP (764550) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on G24-128-TAP 345.00 (780810) 345 kV Bus a. Apply Fault at the G24-128-TAP 345.00 (780810) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. G24-128-TAP (780810) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NORMHLL7 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NORMHLL4 (516097) 138 kV Bus a. Apply Fault at the NORMHLL4 (516097) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL4 (516097) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on TREASILD7 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to remove bus # | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON4 (514898) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to remove bus # | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to GRACMNT4 (515802) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADRK5 (520812) 13.8 kV to Generator #1 b.5. ANADRK5 (520812) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_003 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_004 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_005 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.5. ANADRK5 (520812) 13.8 kV to Generator #1 b.6. ANADRK5 (520812) 13.8 kV to remove bus # b.7. TUTTLE 4 (520496) 138.0 kV to remove bus # b.8. BRIDGCR4 (520501) 138.0 kV to remove bus # b.9. POCASET4 (521031) 138.0 kV to remove bus # b.10. TUTLETP4 (521072) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_006 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_WFEC_FAULT_007 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_AEPW_FAULT_001 | Single Phase Fault with Stuck Breaker on LES (511467) 138 kV Bus a. Apply Fault at the LES (511467) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. RPPAPER4 (511512) 138.0 kV to LWSTAP 4 (511439) 138.0 kV Transmission Circuit #1 b.3. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.4. OMDUNCN4 (529304) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.5. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 b.6. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 b.7. SHERID4 (511474) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.8. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 b.9. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.10. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 b.11. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.12. S.W.S.-4 (511477) 138.0 kV to FLE TAP4 (511423) 138.0 kV Transmission Circuit #1 b.13. FLETCHR4 (511422) 138.0 kV to remove bus # b.14. FLE TAP4 (511423) 138.0 kV to remove bus # b.15. LWS S4 (511431) 138.0 kV to remove bus # b.16. LWSTAP 4 (511439) 138.0 kV to remove bus # b.17. COMMTAP4 (511494) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.4. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G19-045 (763772) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to 112GORE4 (511488) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on VERDEN 4 138.00 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 138.00 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 (511421) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 b.2. VERDEN 4 (511421) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 b.3. CORNVIL4 (511449) 138.0 kV to N29CHIK4 (511502) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on OMDUNCN4 138.00 (529304) 138 kV Bus a. Apply fault at the OMDUNCN4 138.00 (529304) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on DEMPSEYR POI230.00 (511541) 230 kV Bus a. Apply fault at the DEMPSEYR POI230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEMPSEYR POI (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on O.K.U.2-7 345.00 (511584) 345 kV Bus a. Apply fault at the O.K.U.2-7 345.00 (511584) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.2-7 (511584) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on CEMRD_TP4 138.00 (511576) 138 kV Bus a. Apply fault at the CEMRD_TP4 138.00 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T-CONCO4 (511424) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.3. TUTCONT4 (511425) 138.0 kV to CEMRD_TP4 (511576) 138.0 kV Transmission Circuit #1 b.4. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. TUTTLE4 (511501) 138.0 kV to LEONARD4 (511575) 138.0 kV Transmission Circuit #1 b.6. CEMRD_TP4 (511576) 138.0 kV to CMTRYRD4 (515864) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on CAN_GAS4 138.00 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 138.00 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 (511540) 138.0 kV to REDROCKRD4 (511548) 138.0 kV Transmission Circuit #1 b.2. CAN_GAS4 (511540) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. CAN_GAS4 (511540) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 b.4. TALBEAR4 (515460) 138.0 kV to TLBEART4 (515472) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Gen-2026-PR13 will be islanded from the network after the fault. | No mitigation required
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on OMEGA 4 138.00 (515962) 138 kV Bus a. Apply fault at the OMEGA 4 138.00 (515962) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.2. ROMNOSE4 (514823) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on JENSENT4 138.00 (514820) 138 kV Bus a. Apply fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.3. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on JENSEN 4 138.00 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 138.00 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 (514821) 138.0 kV to EL RENO4 (520893) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on KETCHTP4 138.00 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 138.00 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 (514828) 138.0 kV to KETCH 4 (514834) 138.0 kV Transmission Circuit #1 b.2. KETCHTP4 (514828) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.3. KETCHTP4 (514828) 138.0 kV to MITCHSB4 (515466) 138.0 kV Transmission Circuit #1 b.4. WATRLOO4 (514831) 138.0 kV to LBRTYLK4 (515373) 138.0 kV Transmission Circuit #1 b.5. WATRLOO4 (514831) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 b.6. MITCHSB4 (515466) 138.0 kV to WHITESB4 (515467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on LAKESID4 138.00 (514849) 138 kV Bus a. Apply fault at the LAKESID4 138.00 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 (514848) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on QUAILCK4 138.00 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 138.00 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 (514851) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on SLVRLAK4 138.00 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 138.00 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on BRADEN 4 138.00 (514854) 138 kV Bus a. Apply fault at the BRADEN 4 138.00 (514854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 (514852) 138.0 kV to BRADEN 4 (514854) 138.0 kV Transmission Circuit #1 b.2. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on RICHRDS4 138.00 (514862) 138 kV Bus a. Apply fault at the RICHRDS4 138.00 (514862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. RICHRDS4 (514862) 138.0 kV to PIEDMNT4 (514864) 138.0 kV Transmission Circuit #1 b.3. PIEDMNT4 (514864) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to COUNCIL4 (514865) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to DAYTON 4 (514892) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on MORGAN 4 138.00 (514896) 138 kV Bus a. Apply fault at the MORGAN 4 138.00 (514896) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.2. XEROX 4 (514893) 138.0 kV to CZECHAL4 (514894) 138.0 kV Transmission Circuit #1 b.3. XEROX 4 (514893) 138.0 kV to MORGAN 4 (514896) 138.0 kV Transmission Circuit #1 b.4. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on LNEOAK 4 138.00 (514873) 138 kV Bus a. Apply fault at the LNEOAK 4 138.00 (514873) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WESTMOR4 138.00 (514887) 138 kV Bus a. Apply fault at the WESTMOR4 138.00 (514887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. WESTMOR4 (514887) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 b.3. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on 36&MER 4 138.00 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 138.00 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 (514888) 138.0 kV to WRAIRPT4 (514889) 138.0 kV Transmission Circuit #1 b.2. 36&MER 4 (514888) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 b.3. 36&MER 4 (514888) 138.0 kV to HOBBYLO4 (515338) 138.0 kV Transmission Circuit #1 b.4. WRAIRPT4 (514889) 138.0 kV to PENN 4 (514925) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on SARA 4 138.00 (514895) 138 kV Bus a. Apply fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on OU TAP 4 138.00 (514931) 138 kV Bus a. Apply fault at the OU TAP 4 138.00 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUBROOK4 (514903) 138.0 kV to OU TAP 4 (514931) 138.0 kV Transmission Circuit #1 b.2. OU TAP 4 (514931) 138.0 kV to MLENIUM4 (514932) 138.0 kV Transmission Circuit #1 b.3. OU TAP 4 (514931) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.4. MLENIUM4 (514932) 138.0 kV to STUBMAN4 (514952) 138.0 kV Transmission Circuit #1 b.5. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on INDNHIL4 138.00 (514954) 138 kV Bus a. Apply fault at the INDNHIL4 138.00 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 (514904) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.2. HOLLYWD4 (514953) 138.0 kV to INDNHIL4 (514954) 138.0 kV Transmission Circuit #1 b.3. INDNHIL4 (514954) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 b.4. MOORE 4 (514955) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 b.5. MOORE 4 (514955) 138.0 kV to INDIANH4 (515380) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SANTAFE4 138.00 (514926) 138 kV Bus a. Apply fault at the SANTAFE4 138.00 (514926) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV to SANTAFE4 (514926) 138.0 kV Transmission Circuit #1 b.2. SANTAFE4 (514926) 138.0 kV to OAKCRK 4 (514960) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on TURNER 4 138.00 (514992) 138 kV Bus a. Apply fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on SOONRTP4 138.00 (514949) 138 kV Bus a. Apply fault at the SOONRTP4 138.00 (514949) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 (514930) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.2. OAKTRET4 (514930) 138.0 kV to WILKINS4 (514950) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.4. CEDARLN4 (514948) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on MIDWEST4 138.00 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 138.00 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.3. MIDWEST4 (514946) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on BARNES 4 138.00 (515003) 138 kV Bus a. Apply fault at the BARNES 4 138.00 (515003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. SE15TH 4 (514993) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.3. TINKER54 (514994) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 b.2. CANADN-4 (514947) 138.0 kV to NOBLE 4 (515007) 138.0 kV Transmission Circuit #1 b.3. CANADN-4 (514947) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.4. NOBLE 4 (515007) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 b.5. WLNUTCK4 (515097) 138.0 kV to PAOLI- 4 (515100) 138.0 kV Transmission Circuit #1 b.6. WLNUTCK4 (515097) 138.0 kV to PURCELL4 (515475) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 1.5 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on MATO 7 345.00 (511587) 345 kV Bus a. Apply fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to SW 5TH 4 (514920) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 (514860) 69.0 kV to MUSTANG4 (514861) 138.0 kV to MUSTANG1 (515740) 13.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on CIMARON7 345.00 (514901) 345 kV Bus a. Apply fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI41 (515700) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI21 (515703) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA4 (514907) 138.0 kV to ARCADIA7 (514908) 345.0 kV to ARCADI31 (515704) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 (514924) 69.0 kV to PENN 4 (514925) 138.0 kV to PENN 1 (515751) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on PENN 4 138.00 (514925) 138 kV Bus a. Apply fault at the PENN 4 138.00 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 (514925) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 (514933) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on NORTWST4 138.00 (514879) 138 kV Bus a. Apply fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on BOYD 4 138.00 (514958) 138 kV Bus a. Apply fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOYD 4 (514958) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on TRAV3WD7 345.00 (516036) 345 kV Bus a. Apply fault at the TRAV3WD7 345.00 (516036) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAV3WD7 (516036) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to CHERRYRD 4 (521129) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on CLVLDSW4 138.00 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 138.00 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 (520508) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on FLETCH-4 138.00 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 138.00 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.2. COMANCH4 (520864) 138.0 kV to EMPIRE 4 (520900) 138.0 kV Transmission Circuit #1 b.3. EMPIRE 4 (520900) 138.0 kV to FLETCH-4 (520912) 138.0 kV Transmission Circuit #1 b.4. FLETCH-4 (520912) 138.0 kV to GEORGIA4 (520923) 138.0 kV Transmission Circuit #1 b.5. FLETCH-4 (520912) 138.0 kV to FLETCHR2 (520911) 69.0 kV to FLCHTERT (521168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 (521031) 138.0 kV to G22-055-TAP (768080) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on CORNVIL4 138.00 (511449) 138 kV Bus a. Apply fault at the CORNVIL4 138.00 (511449) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL4 (511449) 138.0 kV to CORN TP4 (520867) 138.0 kV Transmission Circuit #1 b.2. SEQUOYAHJ4 (520422) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. NAPLSTP4 (520510) 138.0 kV to PAYNESW4 (520888) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to CANADNS4 (520842) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on GOLDSBY4 138.00 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 138.00 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to GOLDSBY4 (520924) 138.0 kV Transmission Circuit #1 b.2. GOLDSBY4 (520924) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on LAMAR4 138.00 (520403) 138 kV Bus a. Apply fault at the LAMAR4 138.00 (520403) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR4 (520403) 138.0 kV to OU SW 4 (521104) 138.0 kV Transmission Circuit #1 b.2. ACME 4 (520802) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on BAILEY4 138.00 (520401) 138 kV Bus a. Apply fault at the BAILEY4 138.00 (520401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 (520401) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. FRNKLNS4 (520917) 138.0 kV to WMOORE 4 (521123) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on CLINTJC4 138.00 (511485) 138 kV Bus a. Apply fault at the CLINTJC4 138.00 (511485) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on BINGER 4 138.00 (511405) 138 kV Bus a. Apply fault at the BINGER 4 138.00 (511405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGER 4 (511405) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on TREASILD7 345.00 (511409) 345 kV Bus a. Apply fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on CARNEG-4 138.00 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 138.00 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 (511445) 138.0 kV to S.W.S.-4 (511477) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle deviation and undamped oscillations were observed at the G24-128 generating units (780814, 780817, and 780820). Following the fault, all power was transferred through the Chisholm 345/230 kV transformer. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to NORGE--4 (511483) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on S.W.S.-4 138.00 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 138.00 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 (511477) 138.0 kV to TONKAWA4 (511586) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on DVISION4 138.00 (514853) 138 kV Bus a. Apply fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on MUSTANG4 138.00 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 138.00 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 (514861) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDBUD 7 (514909) 345.0 kV to G24-344-TAP (787290) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on CANADN-4 138.00 (514947) 138 kV Bus a. Apply fault at the CANADN-4 138.00 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 (514947) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on CEDARLN4 138.00 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 138.00 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 (514948) 138.0 kV to G21-088-TAP (766111) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_146 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_147 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_148 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_149 | 3 Phase fault on NOBLE4 138.00 (520400) 138 kV Bus a. Apply fault at the NOBLE4 138.00 (520400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 (520400) 138.0 kV to LIDDELL4 (520975) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_150 | 3 Phase fault on ACME 4 138.00 (520802) 138 kV Bus a. Apply fault at the ACME 4 138.00 (520802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 (520802) 138.0 kV to WNORMAN4 (521095) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_151 | 3 Phase fault on CANADNS4 138.00 (520842) 138 kV Bus a. Apply fault at the CANADNS4 138.00 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 (520842) 138.0 kV to LIL AXE4 (520976) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_152 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to FRNKLNS4 (520917) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_153 | 3 Phase fault on FRANKLN4 138.00 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 138.00 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 (520913) 138.0 kV to PINK SW4 (521028) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_154 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_155 | 3 Phase fault on ANADARK4 138.00 (520814) 138 kV Bus a. Apply fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 (520814) 138.0 kV to ANADARK2 (520810) 69.0 kV to ADRKTERT (521181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_156 | 3 Phase fault on FRNKLNS4 138.00 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 138.00 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 (520917) 138.0 kV to FRNKLNS2 (520916) 69.0 kV to FRNKTERT (521169) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHITA4 138.00 (521089) 138 kV Bus a. Apply fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 (521089) 138.0 kV to WASHITA2 (521088) 69.0 kV to WASHTERT (521179) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_158 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_159 | 3 Phase fault on OKLAUN HVDC7345.00 (511565) 345 kV Bus a. Apply fault at the OKLAUN HVDC7345.00 (511565) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN HVDC7 (511565) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_160 | 3 Phase fault on O.K.U.3-7 345.00 (511607) 345 kV Bus a. Apply fault at the O.K.U.3-7 345.00 (511607) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.3-7 (511607) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Remove reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WELSH3 (509406), WELSH1 (509404), G23-204 (776067, 776064) and WILKE2 (509408) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 1 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | The transient voltage exceeds 1.2 p.u. at the DVRSION (511999), OKLAUN (511565), O.K.U. (511456), and O.K.U.3 (511607) substations. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.2. LES#4-1 (511414) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BOYD 4 138.00 (514958) 138 kV Bus a. Apply Fault at the BOYD 4 138.00 (514958) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDARLN4 (514948) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.4. ANADARK4 (520814) 138.0 kV to GENCO1 (521101) 13.8 kV Two Winding #1 b.5. ANADARK4 (520814) 138.0 kV to GENCO2 (521102) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.3. ANADRK6 (520813) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ANADARK4 138.00 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 138.00 (520814) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WASHITA4 138.00 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 138.00 (521089) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to MATO 7 (511587) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on MATO 7 345.00 (511587) 345 kV Bus a. Apply Fault at the MATO 7 345.00 (511587) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to SEVEN7A_HV (511592) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ARCADIA7 345.00 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 345.00 (514908) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CIMARON4 138.00 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 138.00 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO11 (515714) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON4 (514898) 138.0 kV to CIMARON7 (514901) 345.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to FSHRTAP7 (515610) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKESID4 (514849) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.2. SLVRLAK4 (514852) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 b.3. DVISION4 (514853) 138.0 kV to RICHRDS4 (514862) 138.0 kV Transmission Circuit #1 b.4. DVISION4 (514853) 138.0 kV to HAYMAKR4 (514863) 138.0 kV Transmission Circuit #1 b.5. DVISION4 (514853) 138.0 kV to G21-041-TAP (765691) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on DRAPER 4 138.00 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 138.00 (514933) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.5. DRAPER 4 (514933) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 4 (514933) 138.0 kV to MIDWEST4 (514946) 138.0 kV Transmission Circuit #1 b.2. DRAPER 4 (514933) 138.0 kV to SOONRTP4 (514949) 138.0 kV Transmission Circuit #1 b.3. DRAPER 4 (514933) 138.0 kV to GM 4 (514961) 138.0 kV Transmission Circuit #1 b.4. DRAPER 4 (514933) 138.0 kV to BARNES 4 (515003) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.7. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.8. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.9. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.10. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER31 (515720) 13.8 kV Three Winding #3 b.11. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER41 (515721) 13.8 kV Three Winding #4 b.12. DRAPER 4 (514933) 138.0 kV to DRAPER 7 (514934) 345.0 kV to DRAPER21 (515792) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVCELRN2 (514817) 69.0 kV to ELRENO 2 (514818) 69.0 kV Transmission Circuit #1 b.2. ELRENO 2 (514818) 69.0 kV to OKRCHET2 (515506) 69.0 kV Transmission Circuit #1 b.3. EL-RENO4 (514819) 138.0 kV to JENSENT4 (514820) 138.0 kV Transmission Circuit #1 b.4. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.5. EL-RENO4 (514819) 138.0 kV to OMEGA 4 (515962) 138.0 kV Transmission Circuit #1 b.6. ELRENO 2 (514818) 69.0 kV to EL-RENO4 (514819) 138.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRACMNT4 138.00 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 138.00 (515802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to GRACMNT4 (515802) 138.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.3. GRCMNT11 (515801) 13.8 kV to GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATO 7 (511587) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. STUBMAN4 (514952) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on HOLLYWD4 138.00 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 138.00 (514953) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. MIDWEST4 (514946) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. MATHWSN7 (515497) 345.0 kV to TRAV3WD7 (516036) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTMOR4 (514887) 138.0 kV to MCCLAIN4 (514902) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to MCLN 1S (514998) 18.0 kV Two Winding #1 b.3. MCCLAIN4 (514902) 138.0 kV to MCLN 1G (514999) 18.0 kV Two Winding #1 b.4. MCCLAIN4 (514902) 138.0 kV to MCLN 2G (515000) 18.0 kV Two Winding #1 b.5. MCCLAIN4 (514902) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.6. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to MCNOWND7 (515444) 345.0 kV Transmission Circuit #1 b.3. MINCO 7 (514801) 345.0 kV to MNCWND37 (515549) 345.0 kV Transmission Circuit #1 b.4. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.5. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. MINCO 7 (514801) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.7. MINCO 7 (514801) 345.0 kV to MINCO_IV__HV (914801) 345.0 kV Transmission Circuit #1 b.8. MINCO 7 (514801) 345.0 kV to MINCO_I_&_HV (914807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. CIMARON7 (514901) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.3. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.4. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.5. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.6. DRAPER 7 (514934) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #2 b.7. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.8. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.9. NORMHLL7 (516096) 345.0 kV to MCCLAIN7 (516359) 345.0 kV Two Winding #1 b.10. NORMHLL7 (516096) 345.0 kV to GEN-2024-013 (777361) 345.0 kV Transmission Circuit #1 b.11. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL11 (516098) 13.8 kV Three Winding #1 b.12. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNEOAK 4 (514873) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NORTWST4 138.00 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 138.00 (514879) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRADEN 4 (514854) 138.0 kV to NORTWST4 (514879) 138.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 b.5. NORTWST4 (514879) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #3 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL2G (515041) 17.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 b.2. SEMINOL7 (515045) 345.0 kV to SEMINL3G (515042) 20.9 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TREASILD7 345.00 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 345.00 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. TREASILD7 (511409) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on TUTCONT4 138.00 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 138.00 (511425) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUTCONT4 (511425) 138.0 kV to TUTTLE4 (511501) 138.0 kV Transmission Circuit #1 b.2. TUTCONT4 (511425) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-7 (511468) 345.0 kV to G20-087-TAP (764550) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on MINCO 7 345.00 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINCO 7 (514801) 345.0 kV to NORMHLL7 (516096) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EL-RENO4 138.00 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 138.00 (514819) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EL-RENO4 (514819) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. EL-RENO4 (514819) 138.0 kV to ELRENO 2 (514818) 69.0 kV to EL RENO1 (515722) 13.2 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JENSENT4 138.00 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 138.00 (514820) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JENSENT4 (514820) 138.0 kV to JENSEN 4 (514821) 138.0 kV Transmission Circuit #1 b.2. JENSENT4 (514820) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on DVISION4 138.00 (514853) 138 kV Bus a. Apply Fault at the DVISION4 138.00 (514853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DVISION4 (514853) 138.0 kV to LAKESID4 (514849) 138.0 kV Transmission Circuit #1 b.2. DVISION4 (514853) 138.0 kV to SLVRLAK4 (514852) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HAYMAKR4 138.00 (514863) 138 kV Bus a. Apply Fault at the HAYMAKR4 138.00 (514863) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYMAKR4 (514863) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. HAYMAKR4 (514863) 138.0 kV to DVISION4 (514853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on CZECHAL4 138.00 (514894) 138 kV Bus a. Apply Fault at the CZECHAL4 138.00 (514894) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CZECHAL4 (514894) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 b.2. CZECHAL4 (514894) 138.0 kV to XEROX 4 (514893) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on SARA 4 138.00 (514895) 138 kV Bus a. Apply Fault at the SARA 4 138.00 (514895) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SARA 4 (514895) 138.0 kV to STHLAKE4 (515481) 138.0 kV Transmission Circuit #1 b.2. SARA 4 (514895) 138.0 kV to CIMARON4 (514898) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on CIMARON7 345.00 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 345.00 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to CIMARON4 (514898) 138.0 kV to CIMARO21 (515715) 13.8 kV Three Winding #2 b.2. CIMARON7 (514901) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MCCLAIN4 138.00 (514902) 138 kV Bus a. Apply Fault at the MCCLAIN4 138.00 (514902) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCLAIN4 (514902) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 b.2. MCCLAIN4 (514902) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #3 b.2. REDBUD 7 (514909) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SOGATE 4 138.00 (514928) 138 kV Bus a. Apply Fault at the SOGATE 4 138.00 (514928) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOGATE 4 (514928) 138.0 kV to TURNER 4 (514992) 138.0 kV Transmission Circuit #1 b.2. SOGATE 4 (514928) 138.0 kV to WESTMOR4 (514887) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on PLVALLY4 138.00 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 138.00 (514929) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLVALLY4 (514929) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. PLVALLY4 (514929) 138.0 kV to HOLLYWD4 (514953) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on DRAPER 7 345.00 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 345.00 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. DRAPER 7 (514934) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on CHERYCK4 138.00 (514957) 138 kV Bus a. Apply Fault at the CHERYCK4 138.00 (514957) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERYCK4 (514957) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. CHERYCK4 (514957) 138.0 kV to BOYD 4 (514958) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TURNER 4 138.00 (514992) 138 kV Bus a. Apply Fault at the TURNER 4 138.00 (514992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURNER 4 (514992) 138.0 kV to NORMHLL4 (516097) 138.0 kV Transmission Circuit #1 b.2. TURNER 4 (514992) 138.0 kV to SOGATE 4 (514928) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to G24-128-TAP (780810) 345.0 kV Transmission Circuit #1 b.2. GRACMNT7 (515800) 345.0 kV to MINCO 7 (514801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #3 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on NORMHLL7 345.00 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 345.00 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 b.2. NORMHLL7 (516096) 345.0 kV to NORMHLL4 (516097) 138.0 kV to NORMHL21 (516099) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on GEN-2017-150345.00 (761229) 345 kV Bus a. Apply Fault at the GEN-2017-150345.00 (761229) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-150 (761229) 345.0 kV to GEN-2017-233 (761250) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-150 (761229) 345.0 kV to G17-150XFMR1 (761230) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G20-087-TAP 345.00 (764550) 345 kV Bus a. Apply Fault at the G20-087-TAP 345.00 (764550) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-087-TAP (764550) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G20-087-TAP (764550) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on G24-128-TAP 345.00 (780810) 345 kV Bus a. Apply Fault at the G24-128-TAP 345.00 (780810) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-128-TAP (780810) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. G24-128-TAP (780810) 345.0 kV to TREASILD7 (511409) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on NORMHLL7 (516096) 345 kV Bus a. Apply Fault at the NORMHLL7 (516096) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL7 (516096) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAPER 7 (514934) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NORMHLL4 (516097) 138 kV Bus a. Apply Fault at the NORMHLL4 (516097) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMHLL4 (516097) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRACMNT7 (515800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on TREASILD7 (511409) 345 kV Bus a. Apply Fault at the TREASILD7 (511409) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON7 (514901) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MATHWSN7 (515497) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIMARON4 (514898) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. This issue was also present in the base case, and the Gen-2026-PR13 units were not found to have any impact on the observed oscillations. | Multi - Border - Woodward 345 kV Tap
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TREASILD7 (511409) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 b.2. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.2. ANADARK4 (520814) 138.0 kV to GRACMNT4 (515802) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADRK5 (520812) 13.8 kV to Generator #1 b.5. ANADRK5 (520812) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_003 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. S.W.S.-4 (511477) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_004 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_005 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BRIDGCR4 (520501) 138.0 kV to SUNSHIN4 (521059) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to ANADARK4 (520814) 138.0 kV Transmission Circuit #1 b.3. ANADRK5 (520812) 13.8 kV to ANADARK4 (520814) 138.0 kV Two Winding #1 b.4. ANADARK4 (520814) 138.0 kV to POCASET4 (521031) 138.0 kV Transmission Circuit #1 b.5. ANADRK5 (520812) 13.8 kV to Generator #1 b.6. ANADRK5 (520812) 13.8 kV to remove bus # b.7. TUTTLE 4 (520496) 138.0 kV to remove bus # b.8. BRIDGCR4 (520501) 138.0 kV to remove bus # b.9. POCASET4 (521031) 138.0 kV to remove bus # b.10. TUTLETP4 (521072) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_006 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLINTJC4 (511485) 138.0 kV to CLINTON4 (520856) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.3. ONEY 4 (521017) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.4. HINTON 4 (520468) 138.0 kV to remove bus # b.5. DEERCR 4 (520503) 138.0 kV to remove bus # b.6. BINGERJ4 (520827) 138.0 kV to remove bus # b.7. CLINTON4 (520856) 138.0 kV to remove bus # b.8. HYDRO 4 (520950) 138.0 kV to remove bus # b.9. NIJECT 4 (521010) 138.0 kV to remove bus # b.10. ONEY 4 (521017) 138.0 kV to remove bus # b.11. SICKLES4 (521050) 138.0 kV to remove bus # b.12. WEATHFD4 (521092) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_WFEC_FAULT_007 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #1 b.2. GRACMNT4 (515802) 138.0 kV to WASHITA4 (521089) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_AEPW_FAULT_001 | Single Phase Fault with Stuck Breaker on LES (511467) 138 kV Bus a. Apply Fault at the LES (511467) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COMANC-4 (511437) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. RPPAPER4 (511512) 138.0 kV to LWSTAP 4 (511439) 138.0 kV Transmission Circuit #1 b.3. S.W.S.-4 (511477) 138.0 kV to ELSWORTH 4 (511563) 138.0 kV Transmission Circuit #1 b.4. OMDUNCN4 (529304) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.5. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 b.6. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 b.7. SHERID4 (511474) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.8. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 b.9. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.10. L.E.S.-7 (511468) 345.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 b.11. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 b.12. S.W.S.-4 (511477) 138.0 kV to FLE TAP4 (511423) 138.0 kV Transmission Circuit #1 b.13. FLETCHR4 (511422) 138.0 kV to remove bus # b.14. FLE TAP4 (511423) 138.0 kV to remove bus # b.15. LWS S4 (511431) 138.0 kV to remove bus # b.16. LWSTAP 4 (511439) 138.0 kV to remove bus # b.17. COMMTAP4 (511494) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power of FRWF3 (534094) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power of FRWF3 (534094) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power of FRWF3 (534094) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.4. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the reactive power of FRWF3 (534094) unit. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR13 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR13 | 04 SOUTHEAST | 914801 | MINCO_IV__HV345.00 | 345 | 15.0113 | 15.0733 | 0.062
GEN-2026-PR13 | 04 SOUTHEAST | 914802 | MINCO IV HV2345.00 | 345 | 10.0919 | 10.1539 | 0.062
GEN-2026-PR13 | 04 SOUTHEAST | 514801 | MINCO 7 345.00 | 345 | 26.6783 | 26.7403 | 0.062
GEN-2026-PR13 | 04 SOUTHEAST | 914807 | MINCO_I_&_HV345.00 | 345 | 26.5565 | 26.6179 | 0.0614
GEN-2026-PR13 | 04 SOUTHEAST | 515444 | MCNOWND7 345.00 | 345 | 26.5599 | 26.6213 | 0.0614
GEN-2026-PR13 | 04 SOUTHEAST | 761250 | GEN-2017-233345.00 | 345 | 25.7181 | 25.7755 | 0.0574
GEN-2026-PR13 | 04 SOUTHEAST | 761229 | GEN-2017-150345.00 | 345 | 25.6632 | 25.7204 | 0.0572
GEN-2026-PR13 | 04 SOUTHEAST | 514901 | CIMARON7 345.00 | 345 | 43.5441 | 43.5674 | 0.0233
GEN-2026-PR13 | 04 SOUTHEAST | 784141 | GEN-2024-239345.00 | 345 | 42.8358 | 42.8583 | 0.0225
GEN-2026-PR13 | 04 SOUTHEAST | 515549 | MNCWND37 345.00 | 345 | 15.5955 | 15.6157 | 0.0202
GEN-2026-PR13 | 04 SOUTHEAST | 784531 | GEN-2024-252345.00 | 345 | 38.8041 | 38.8223 | 0.0182
GEN-2026-PR13 | 04 SOUTHEAST | 784530 | GEN-2024-252345.00 | 345 | 38.2758 | 38.2938 | 0.018
GEN-2026-PR13 | 04 SOUTHEAST | 516096 | NORMHLL7 345.00 | 345 | 33.2936 | 33.3081 | 0.0145
GEN-2026-PR13 | 04 SOUTHEAST | 515800 | GRACMNT7 345.00 | 345 | 23.185 | 23.199 | 0.014
GEN-2026-PR13 | 04 SOUTHEAST | 515497 | MATHWSN7 345.00 | 345 | 43.7203 | 43.7328 | 0.0125
GEN-2026-PR13 | 04 SOUTHEAST | 784591 | GEN-2024-254345.00 | 345 | 38.9448 | 38.9545 | 0.0097
GEN-2026-PR13 | 04 SOUTHEAST | 784590 | GEN-2024-254345.00 | 345 | 38.4147 | 38.4243 | 0.0096
GEN-2026-PR13 | 04 SOUTHEAST | 515939 | MNCWND47 345.00 | 345 | 10.7201 | 10.7292 | 0.0091
GEN-2026-PR13 | 04 SOUTHEAST | 780810 | G24-128-TAP 345.00 | 345 | 21.4107 | 21.4197 | 0.009
GEN-2026-PR13 | 04 SOUTHEAST | 514880 | NORTWST7 345.00 | 345 | 39.8527 | 39.8615 | 0.0088
GEN-2026-PR13 | 04 SOUTHEAST | 514934 | DRAPER 7 345.00 | 345 | 31.0053 | 31.014 | 0.0087
GEN-2026-PR13 | 04 SOUTHEAST | 780811 | GEN-2024-128345.00 | 345 | 19.8866 | 19.8939 | 0.0073
GEN-2026-PR13 | 04 SOUTHEAST | 516097 | NORMHLL4 138.00 | 138 | 47.5948 | 47.6016 | 0.0068
GEN-2026-PR13 | 04 SOUTHEAST | 514933 | DRAPER 4 138.00 | 138 | 48.9812 | 48.9879 | 0.0067
GEN-2026-PR13 | 04 SOUTHEAST | 514898 | CIMARON4 138.00 | 138 | 49.2318 | 49.2383 | 0.0065
GEN-2026-PR13 | 04 SOUTHEAST | 777361 | GEN-2024-013345.00 | 345 | 22.6295 | 22.6355 | 0.006
GEN-2026-PR13 | 04 SOUTHEAST | 514929 | PLVALLY4 138.00 | 138 | 44.3007 | 44.3065 | 0.0058
GEN-2026-PR13 | 04 SOUTHEAST | 514879 | NORTWST4 138.00 | 138 | 51.0486 | 51.0534 | 0.0048
GEN-2026-PR13 | 04 SOUTHEAST | 777368 | GEN-2024-C1 345.00 | 345 | 20.4106 | 20.4154 | 0.0048
GEN-2026-PR13 | 04 SOUTHEAST | 777369 | GEN-2024-C2 345.00 | 345 | 20.4106 | 20.4154 | 0.0048
GEN-2026-PR13 | 04 SOUTHEAST | 511409 | TREASILD7 345.00 | 345 | 17.9981 | 18.0028 | 0.0047
GEN-2026-PR13 | 04 SOUTHEAST | 515980 | MNCWND57 345.00 | 345 | 7.694 | 7.6986 | 0.0046
GEN-2026-PR13 | 04 SOUTHEAST | 514953 | HOLLYWD4 138.00 | 138 | 38.7021 | 38.706 | 0.0039
GEN-2026-PR13 | 04 SOUTHEAST | 515610 | FSHRTAP7 345.00 | 345 | 18.294 | 18.2978 | 0.0038
GEN-2026-PR13 | 04 SOUTHEAST | 514946 | MIDWEST4 138.00 | 138 | 37.5393 | 37.5428 | 0.0035
GEN-2026-PR13 | 04 SOUTHEAST | 515802 | GRACMNT4 138.00 | 138 | 35.8181 | 35.8213 | 0.0032
GEN-2026-PR13 | 04 SOUTHEAST | 515045 | SEMINOL7 345.00 | 345 | 35.7582 | 35.7613 | 0.0031
GEN-2026-PR13 | 04 SOUTHEAST | 514881 | SPRNGCK7 345.00 | 345 | 28.1221 | 28.1252 | 0.0031
GEN-2026-PR13 | 04 SOUTHEAST | 514853 | DVISION4 138.00 | 138 | 40.2706 | 40.2735 | 0.0029
GEN-2026-PR13 | 04 SOUTHEAST | 514908 | ARCADIA7 345.00 | 345 | 34.9617 | 34.9645 | 0.0028
GEN-2026-PR13 | 04 SOUTHEAST | 786601 | GEN-2024-321345.00 | 345 | 34.3055 | 34.3083 | 0.0028
GEN-2026-PR13 | 04 SOUTHEAST | 514992 | TURNER 4 138.00 | 138 | 32.0314 | 32.0342 | 0.0028
GEN-2026-PR13 | 04 SOUTHEAST | 511992 | HVBUS 345.00 | 345 | 13.8858 | 13.8885 | 0.0027
GEN-2026-PR13 | 04 SOUTHEAST | 514909 | REDBUD 7 345.00 | 345 | 35.509 | 35.5117 | 0.0027
GEN-2026-PR13 | 04 SOUTHEAST | 784620 | GEN-2024-255345.00 | 345 | 25.8253 | 25.8279 | 0.0026
GEN-2026-PR13 | 04 SOUTHEAST | 784621 | GEN-2024-255345.00 | 345 | 26.1889 | 26.1915 | 0.0026
GEN-2026-PR13 | 04 SOUTHEAST | 520814 | ANADARK4 138.00 | 138 | 38.426 | 38.4284 | 0.0024
GEN-2026-PR13 | 04 SOUTHEAST | 762614 | GEN-2018-026138.00 | 138 | 40.1897 | 40.1921 | 0.0024
GEN-2026-PR13 | 04 SOUTHEAST | 514954 | INDNHIL4 138.00 | 138 | 30.5019 | 30.5043 | 0.0024
GEN-2026-PR13 | 04 SOUTHEAST | 520917 | FRNKLNS4 138.00 | 138 | 32.2394 | 32.2418 | 0.0024
GEN-2026-PR13 | 04 SOUTHEAST | 765691 | G21-041-TAP 138.00 | 138 | 40.6718 | 40.6742 | 0.0024
GEN-2026-PR13 | 04 SOUTHEAST | 514852 | SLVRLAK4 138.00 | 138 | 36.5402 | 36.5425 | 0.0023
GEN-2026-PR13 | 04 SOUTHEAST | 764550 | G20-087-TAP 345.00 | 345 | 16.3256 | 16.3279 | 0.0023
GEN-2026-PR13 | 04 SOUTHEAST | 764555 | GEN-2020-087345.00 | 345 | 16.3135 | 16.3158 | 0.0023
GEN-2026-PR13 | 04 SOUTHEAST | 514902 | MCCLAIN4 138.00 | 138 | 33.4337 | 33.4359 | 0.0022
GEN-2026-PR13 | 04 SOUTHEAST | 514854 | BRADEN 4 138.00 | 138 | 35.1474 | 35.1496 | 0.0022
GEN-2026-PR13 | 04 SOUTHEAST | 511920 | CDW-SUB 345.00 | 345 | 12.0549 | 12.057 | 0.0021
GEN-2026-PR13 | 04 SOUTHEAST | 514873 | LNEOAK 4 138.00 | 138 | 35.0568 | 35.0589 | 0.0021
GEN-2026-PR13 | 04 SOUTHEAST | 514896 | MORGAN 4 138.00 | 138 | 36.523 | 36.5251 | 0.0021
GEN-2026-PR13 | 04 SOUTHEAST | 765690 | GEN-2021-041138.00 | 138 | 38.1063 | 38.1084 | 0.0021
GEN-2026-PR13 | 04 SOUTHEAST | 514925 | PENN 4 138.00 | 138 | 32.5015 | 32.5035 | 0.002
GEN-2026-PR13 | 04 SOUTHEAST | 514887 | WESTMOR4 138.00 | 138 | 31.1726 | 31.1746 | 0.002
GEN-2026-PR13 | 04 SOUTHEAST | 514893 | XEROX 4 138.00 | 138 | 32.6518 | 32.6537 | 0.0019
GEN-2026-PR13 | 04 SOUTHEAST | 514907 | ARCADIA4 138.00 | 138 | 44.3551 | 44.3569 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 762647 | GEN-2018-029138.00 | 138 | 47.515 | 47.5168 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 515605 | CANADN7 345.00 | 345 | 12.8903 | 12.8921 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 511468 | L.E.S.-7 345.00 | 345 | 16.4193 | 16.4211 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 514863 | HAYMAKR4 138.00 | 138 | 28.9277 | 28.9295 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 514928 | SOGATE 4 138.00 | 138 | 27.3658 | 27.3676 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 514952 | STUBMAN4 138.00 | 138 | 26.5208 | 26.5226 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 514851 | QUAILCK4 138.00 | 138 | 32.7552 | 32.757 | 0.0018
GEN-2026-PR13 | 04 SOUTHEAST | 515461 | RNDBARN4 138.00 | 138 | 42.1636 | 42.1653 | 0.0017
GEN-2026-PR13 | 04 SOUTHEAST | 511477 | S.W.S.-4 138.00 | 138 | 35.7646 | 35.7663 | 0.0017
GEN-2026-PR13 | 04 SOUTHEAST | 514894 | CZECHAL4 138.00 | 138 | 31.097 | 31.0987 | 0.0017
GEN-2026-PR13 | 04 SOUTHEAST | 763318 | GEN-2018-115345.00 | 345 | 16.0707 | 16.0724 | 0.0017
GEN-2026-PR13 | 04 SOUTHEAST | 515044 | SEMINOL4 138.00 | 138 | 50.1784 | 50.1801 | 0.0017
GEN-2026-PR13 | 04 SOUTHEAST | 514957 | CHERYCK4 138.00 | 138 | 24.0619 | 24.0635 | 0.0016
GEN-2026-PR13 | 04 SOUTHEAST | 521089 | WASHITA4 138.00 | 138 | 31.7699 | 31.7715 | 0.0016
GEN-2026-PR13 | 04 SOUTHEAST | 514948 | CEDARLN4 138.00 | 138 | 26.079 | 26.0806 | 0.0016
GEN-2026-PR13 | 04 SOUTHEAST | 515374 | CHISHOM4 138.00 | 138 | 32.0105 | 32.0121 | 0.0016
GEN-2026-PR13 | 04 SOUTHEAST | 514949 | SOONRTP4 138.00 | 138 | 24.8615 | 24.863 | 0.0015
GEN-2026-PR13 | 04 SOUTHEAST | 515600 | KNGFSHR7 345.00 | 345 | 11.5503 | 11.5518 | 0.0015
GEN-2026-PR13 | 04 SOUTHEAST | 515977 | LKKONWA4 138.00 | 138 | 47.6567 | 47.6582 | 0.0015
GEN-2026-PR13 | 04 SOUTHEAST | 770081 | GEN-2022-155138.00 | 138 | 42.0826 | 42.0841 | 0.0015
GEN-2026-PR13 | 04 SOUTHEAST | 514834 | KETCH 4 138.00 | 138 | 31.2781 | 31.2795 | 0.0014
GEN-2026-PR13 | 04 SOUTHEAST | 514828 | KETCHTP4 138.00 | 138 | 30.3426 | 30.3439 | 0.0013
GEN-2026-PR13 | 04 SOUTHEAST | 514930 | OAKTRET4 138.00 | 138 | 23.2245 | 23.2258 | 0.0013
GEN-2026-PR13 | 04 SOUTHEAST | 514958 | BOYD 4 138.00 | 138 | 22.3345 | 22.3358 | 0.0013
GEN-2026-PR13 | 04 SOUTHEAST | 515707 | HSL13 4 138.00 | 138 | 40.5462 | 40.5475 | 0.0013
GEN-2026-PR13 | 04 SOUTHEAST | 514849 | LAKESID4 138.00 | 138 | 26.9342 | 26.9354 | 0.0012
GEN-2026-PR13 | 04 SOUTHEAST | 515875 | REDNGTN7 345.00 | 345 | 19.0011 | 19.0023 | 0.0012
GEN-2026-PR13 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 138.00 | 138 | 27.269 | 27.2702 | 0.0012
GEN-2026-PR13 | 04 SOUTHEAST | 514961 | GM 4 138.00 | 138 | 21.4078 | 21.4089 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 511587 | MATO 7 345.00 | 345 | 10.4266 | 10.4277 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 514864 | PIEDMNT4 138.00 | 138 | 24.5675 | 24.5686 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 514904 | WESTHSE4 138.00 | 138 | 20.3123 | 20.3134 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 515457 | AIRDEPT4 138.00 | 138 | 21.8236 | 21.8247 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 766110 | GEN-2021-088138.00 | 138 | 23.2096 | 23.2107 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 515481 | STHLAKE4 138.00 | 138 | 23.1344 | 23.1355 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 515877 | REDDIRT7 345.00 | 345 | 18.9962 | 18.9973 | 0.0011
GEN-2026-PR13 | 04 SOUTHEAST | 514895 | SARA 4 138.00 | 138 | 20.3983 | 20.3993 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 515003 | BARNES 4 138.00 | 138 | 24.1187 | 24.1197 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 515407 | TATONGA7 345.00 | 345 | 19.0284 | 19.0294 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 511592 | SEVEN7A_HV 345.00 | 345 | 9.9229 | 9.9239 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 511599 | SEVEN7AB2 345.00 | 345 | 9.9229 | 9.9239 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 511608 | SEVEN7AB3 345.00 | 345 | 9.9229 | 9.9239 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 514862 | RICHRDS4 138.00 | 138 | 23.7301 | 23.7311 | 0.001
GEN-2026-PR13 | 04 SOUTHEAST | 514993 | SE15TH 4 138.00 | 138 | 24.2623 | 24.2632 | 0.0009
GEN-2026-PR13 | 04 SOUTHEAST | 514820 | JENSENT4 138.00 | 138 | 19.6021 | 19.6029 | 0.0008
GEN-2026-PR13 | 04 SOUTHEAST | 760939 | GEN-2017-171345.00 | 345 | 12.7909 | 12.7917 | 0.0008
GEN-2026-PR13 | 04 SOUTHEAST | 514994 | TINKER54 138.00 | 138 | 20.9003 | 20.901 | 0.0007
GEN-2026-PR13 | 04 SOUTHEAST | 514819 | EL-RENO4 138.00 | 138 | 17.9597 | 17.9604 | 0.0007
GEN-2026-PR13 | 04 SOUTHEAST | 515466 | MITCHSB4 138.00 | 138 | 23.9679 | 23.9686 | 0.0007
GEN-2026-PR13 | 04 SOUTHEAST | 520547 | SEQOYAH4 138.00 | 138 | 21.3904 | 21.3911 | 0.0007
GEN-2026-PR13 | 04 SOUTHEAST | 520923 | GEORGIA4 138.00 | 138 | 19.5308 | 19.5314 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 511553 | CHISHOLM7 345.00 | 345 | 13.038 | 13.0386 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 515585 | MAMTHPW7 345.00 | 345 | 14.6105 | 14.6111 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 516059 | BECKHAM7 345.00 | 345 | 13.0769 | 13.0775 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 781591 | GEN-2024-154345.00 | 345 | 12.9935 | 12.9941 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 515375 | WWRDEHV7 345.00 | 345 | 23.1777 | 23.1783 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 767221 | GEN-2022-012345.00 | 345 | 22.8159 | 22.8165 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 767301 | GEN-2022-016345.00 | 345 | 22.8377 | 22.8383 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 767321 | GEN-2022-017345.00 | 345 | 22.4897 | 22.4903 | 0.0006
GEN-2026-PR13 | 04 SOUTHEAST | 514715 | WOODRNG7 345.00 | 345 | 20.2176 | 20.2181 | 0.0005
GEN-2026-PR13 | 04 SOUTHEAST | 514821 | JENSEN 4 138.00 | 138 | 16.7525 | 16.753 | 0.0005
GEN-2026-PR13 | 04 SOUTHEAST | 515465 | LGARBER4 138.00 | 138 | 22.3475 | 22.348 | 0.0005
GEN-2026-PR13 | 04 SOUTHEAST | 914720 | SKELETON__HV345.00 | 345 | 19.1149 | 19.1154 | 0.0005
GEN-2026-PR13 | 04 SOUTHEAST | 301541 | 4MEMORAL 138.00 | 138 | 21.6536 | 21.654 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 763527 | GEN-2019-012345.00 | 345 | 20.1016 | 20.102 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 787771 | GEN-2024-360138.00 | 138 | 21.8541 | 21.8545 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 514803 | SOONER 7 345.00 | 345 | 29.8372 | 29.8376 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 514906 | JNSKAMO4 138.00 | 138 | 22.0423 | 22.0427 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 515448 | CRSRDSW7 345.00 | 345 | 12.9715 | 12.9719 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 516192 | WAGNWTIE7 345.00 | 345 | 16.2751 | 16.2755 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 516198 | WAGNWL7 345.00 | 345 | 16.2751 | 16.2755 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 516207 | GADWALL7 345.00 | 345 | 16.2751 | 16.2755 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 520893 | EL RENO4 138.00 | 138 | 15.6839 | 15.6843 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 588720 | GEN-2017-117138.00 | 138 | 15.6839 | 15.6843 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 771681 | GEN-2022-235138.00 | 138 | 15.6839 | 15.6843 | 0.0004
GEN-2026-PR13 | 04 SOUTHEAST | 510925 | KIOWA 7 345.00 | 345 | 21.1931 | 21.1934 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 516106 | BOBCAT 7 345.00 | 345 | 16.2523 | 16.2526 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 776561 | GEN-2023-229138.00 | 138 | 18.4581 | 18.4584 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 787770 | G24-360-TAP 138.00 | 138 | 22.2871 | 22.2874 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 515458 | BORDER 7345.00 | 345 | 10.3324 | 10.3327 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 511557 | CHISHOLM6 230.00 | 230 | 12.7986 | 12.7989 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 514827 | CTNWOOD4 138.00 | 138 | 18.792 | 18.7923 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 515055 | MAUD 4 138.00 | 138 | 22.3653 | 22.3656 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 515961 | GUTHRIE7 345.00 | 345 | 14.5396 | 14.5399 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 516019 | KINGWD 7 345.00 | 345 | 17.1299 | 17.1302 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 520508 | CLVLDSW4 138.00 | 138 | 13.3185 | 13.3188 | 0.0003
GEN-2026-PR13 | 04 SOUTHEAST | 511425 | TUTCONT4 138.00 | 138 | 10.6773 | 10.6775 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 511563 | ELSWORTH 4138.00 | 138 | 10.6269 | 10.6271 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515460 | TALBEAR4 138.00 | 138 | 8.695 | 8.6952 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515582 | SLNGWND7 345.00 | 345 | 9.0175 | 9.0177 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515825 | GRTWSRN7 345.00 | 345 | 10.6005 | 10.6007 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515933 | MLCLMRD4 138.00 | 138 | 9.3099 | 9.3101 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 521017 | ONEY 4 138.00 | 138 | 11.632 | 11.6322 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 765450 | GEN-2021-016345.00 | 345 | 11.8579 | 11.8581 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 768080 | G22-055-TAP 138.00 | 138 | 8.6254 | 8.6256 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 784050 | G24-236-TAP 345.00 | 345 | 12.3249 | 12.3251 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 510907 | PITTSB-7 345.00 | 345 | 21.7712 | 21.7714 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 511483 | NORGE--4 138.00 | 138 | 12.5112 | 12.5114 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 511575 | LEONARD4 138.00 | 138 | 10.2949 | 10.2951 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 511586 | TONKAWA4 138.00 | 138 | 11.0663 | 11.0665 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 514714 | WOODRNG4 138.00 | 138 | 20.8034 | 20.8036 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515376 | WWRDEHV4 138.00 | 138 | 26.256 | 26.2562 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515476 | HUNTERS7 345.00 | 345 | 13.6187 | 13.6189 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 516010 | PINTAIL7 345.00 | 345 | 17.1934 | 17.1936 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 516036 | TRAV3WD7 345.00 | 345 | 7.4905 | 7.4907 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 516086 | TRAV3WZ7 345.00 | 345 | 6.9588 | 6.959 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 516146 | 25MILE 7 345.00 | 345 | 16.2226 | 16.2228 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 516159 | 25MILZ 7 345.00 | 345 | 16.1936 | 16.1938 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 520473 | CKSHATP4 138.00 | 138 | 11.6706 | 11.6708 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 520591 | CNADSLR4 138.00 | 138 | 12.3481 | 12.3483 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 520810 | ANADARK2 69.000 | 69 | 16.9403 | 16.9405 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 562020 | PRSCRKII 7 345.00 | 345 | 11.5516 | 11.5518 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 784471 | GEN-2024-250345.00 | 345 | 20.765 | 20.7652 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 787170 | G24-340-TAP 345.00 | 345 | 19.8332 | 19.8334 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 511501 | TUTTLE4 138.00 | 138 | 10.4927 | 10.4929 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 511540 | CAN_GAS4 138.00 | 138 | 9.9407 | 9.9409 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515477 | CHSHLMV7 345.00 | 345 | 13.5956 | 13.5958 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 515951 | PERSIMN7 345.00 | 345 | 12.7046 | 12.7048 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 588560 | GEN-2017-011345.00 | 345 | 13.0386 | 13.0388 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 787200 | GEN-2024-341345.00 | 345 | 20.0709 | 20.0711 | 0.0002
GEN-2026-PR13 | 04 SOUTHEAST | 509834 | COGENT 7 345.00 | 345 | 32.0787 | 32.0788 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 762592 | GEN-2018-024345.00 | 345 | 20.5151 | 20.5152 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511422 | FLETCHR4 138.00 | 138 | 8.424 | 8.4241 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511541 | DEMPSEYR POI230.00 | 230 | 9.1936 | 9.1937 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511600 | HVBUS 138.00 | 138 | 8.0354 | 8.0355 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515314 | REDCORN4 138.00 | 138 | 8.9213 | 8.9214 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515422 | C-RIVER7 345.00 | 345 | 13.5865 | 13.5866 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515531 | VANOSTP4 138.00 | 138 | 14.4421 | 14.4422 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516110 | GLSSAND4 138.00 | 138 | 11.1668 | 11.1669 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520838 | CADDO 2 69.000 | 69 | 12.6924 | 12.6925 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520859 | COGAR 4 138.00 | 138 | 9.5955 | 9.5956 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 763069 | G18-071-TAP 345.00 | 345 | 14.9376 | 14.9377 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 765890 | GEN-2021-064138.00 | 138 | 9.1701 | 9.1702 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 772680 | G23-035-TAP 138.00 | 138 | 8.6755 | 8.6756 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 784051 | GEN-2024-236345.00 | 345 | 10.3111 | 10.3112 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 787831 | GEN-2024-362138.00 | 138 | 8.078 | 8.0781 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511554 | RKY_RDG4 138.00 | 138 | 5.9882 | 5.9883 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511929 | ZONE-6 SUB 345.00 | 345 | 7.0702 | 7.0703 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516054 | TRAV1WD7 345.00 | 345 | 5.5295 | 5.5296 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520912 | FLETCH-4 138.00 | 138 | 7.5902 | 7.5903 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 521010 | NIJECT 4 138.00 | 138 | 5.5557 | 5.5558 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 521027 | PINERTP2 69.000 | 69 | 4.914 | 4.9141 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 914715 | SKELETON__HV345.00 | 345 | 6.0077 | 6.0078 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520489 | MOORE 2 69.000 | 69 | 3.0786 | 3.0787 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 510861 | V-WEYCO1 4 138.00 | 138 | 12.3765 | 12.3766 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511421 | VERDEN 4 138.00 | 138 | 10.7674 | 10.7675 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511424 | T-CONCO4 138.00 | 138 | 7.0396 | 7.0397 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511490 | ELKCITY6 230.00 | 230 | 7.8964 | 7.8965 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511576 | CEMRD_TP4 138.00 | 138 | 7.0804 | 7.0805 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 514823 | ROMNOSE4 138.00 | 138 | 6.3826 | 6.3827 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515472 | TLBEART4 138.00 | 138 | 9.8785 | 9.8786 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515646 | GRNTWD 7 345.00 | 345 | 11.0779 | 11.078 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515852 | DGRASSE7 345.00 | 345 | 15.3551 | 15.3552 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515864 | CMTRYRD4 138.00 | 138 | 6.8784 | 6.8785 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515962 | OMEGA 4 138.00 | 138 | 6.1471 | 6.1472 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516006 | DMNDSPG7 345.00 | 345 | 7.926 | 7.9261 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516074 | PONDRSA7 345.00 | 345 | 9.8731 | 9.8732 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516087 | TRAV22Z7 345.00 | 345 | 5.6449 | 5.645 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516100 | HORIZON4 138.00 | 138 | 6.8274 | 6.8275 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516107 | TRAV21Z7 345.00 | 345 | 5.6452 | 5.6453 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516108 | TRAV11Z7 345.00 | 345 | 5.2463 | 5.2464 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516109 | TRAV12Z7 345.00 | 345 | 5.2462 | 5.2463 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516210 | RAVEN 7 345.00 | 345 | 21.2129 | 21.213 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520440 | HARPER2 69.000 | 69 | 15.926 | 15.9261 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520468 | HINTON 4 138.00 | 138 | 4.0278 | 4.0279 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520472 | CHCKSHA4 138.00 | 138 | 8.9324 | 8.9325 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520496 | TUTTLE 4 138.00 | 138 | 7.0793 | 7.0794 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520514 | BCVI SW4 138.00 | 138 | 7.3704 | 7.3705 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520827 | BINGERJ4 138.00 | 138 | 8.2666 | 8.2667 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 521031 | POCASET4 138.00 | 138 | 9.1067 | 9.1068 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 521103 | SLKHILLS 4 138.00 | 138 | 7.3952 | 7.3953 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 521129 | CHERRYRD 4 138.00 | 138 | 5.9207 | 5.9208 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 523019 | OSLO-SYLVIE7345.00 | 345 | 9.1303 | 9.1304 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 523020 | SYLVIE 7 345.00 | 345 | 9.1303 | 9.1304 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 523030 | OLSO 7 345.00 | 345 | 9.1303 | 9.1304 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 523041 | FRWLN7 345.00 | 345 | 10.4045 | 10.4046 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 525850 | ELK_CT1 345.00 | 345 | 15.1158 | 15.1159 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 585420 | SUBST HS 345.00 | 345 | 8.1403 | 8.1404 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 588838 | G17-092-SWYD345.00 | 345 | 21.2129 | 21.213 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 762321 | GEN-2017-164345.00 | 345 | 11.9209 | 11.921 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 762342 | GEN-2017-178345.00 | 345 | 8.3148 | 8.3149 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 763065 | GEN-2018-071345.00 | 345 | 14.8798 | 14.8799 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 772681 | GEN-2023-035138.00 | 138 | 8.1721 | 8.1722 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 774681 | GEN-2023-135345.00 | 345 | 14.0854 | 14.0855 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 775520 | G23-177-TAP 138.00 | 138 | 8.7622 | 8.7623 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 787171 | GEN-2024-340345.00 | 345 | 19.8231 | 19.8232 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 787290 | G24-344-TAP 345.00 | 345 | 17.3658 | 17.3659 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 787291 | GEN-2024-344345.00 | 345 | 17.3658 | 17.3659 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 915975 | WILLOW_CR_HV345.00 | 345 | 17.4283 | 17.4284 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511544 | DEMPSEYR_HV 230.00 | 230 | 5.3721 | 5.3722 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 516045 | TRAV2WD7 345.00 | 345 | 5.9788 | 5.9789 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520513 | BCV SW 4 138.00 | 138 | 5.3763 | 5.3764 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 520531 | AMBER 4 138.00 | 138 | 7.4103 | 7.4104 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 768081 | GEN-2022-055138.00 | 138 | 5.9038 | 5.9039 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511445 | CARNEG-4 138.00 | 138 | 9.2427 | 9.2428 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 514809 | JOHNCO 7 345.00 | 345 | 11.6087 | 11.6088 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515694 | ARMFTWD4 138.00 | 138 | 10.4997 | 10.4998 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515894 | THUNDER7 345.00 | 345 | 13.3762 | 13.3763 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 775521 | GEN-2023-177138.00 | 138 | 8.7082 | 8.7083 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 511877 | G16133G16146345.00 | 345 | 34.8143 | 34.8144 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 515974 | GEN-2015-066345.00 | 345 | 17.5497 | 17.5498 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 588810 | GEN-2017-040345.00 | 345 | 20.6852 | 20.6853 | 0.0001
GEN-2026-PR13 | 04 SOUTHEAST | 510866 | V-WEYCO T4 138.00 | 138 | 12.9277 | 12.9277 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 510911 | VALIANT7 345.00 | 345 | 15.6126 | 15.6126 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 510958 | V-WEYCO2 4 138.00 | 138 | 12.2914 | 12.2914 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511405 | BINGER 4 138.00 | 138 | 6.1017 | 6.1017 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511542 | BUFFCK6 230.00 | 230 | 6.6932 | 6.6932 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511547 | ROARK6 230.00 | 230 | 5.0007 | 5.0007 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511573 | REDBDPLN4 138.00 | 138 | 4.2683 | 4.2683 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511726 | ZONE-5 SUB 345.00 | 345 | 7.0296 | 7.0296 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511878 | G16133_765TN765.00 | 765 | 9.4614 | 9.4614 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511879 | G16133_765R1765.00 | 765 | 9.4614 | 9.4614 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511880 | G16133_765R2765.00 | 765 | 4.5921 | 4.5921 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511881 | G16133_765R3765.00 | 765 | 3.6597 | 3.6597 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511882 | G16133_765CS765.00 | 765 | 3.6597 | 3.6597 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511883 | G16133_345CS345.00 | 345 | 7.9574 | 7.9574 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511884 | ZONE-1 SUB 345.00 | 345 | 7.0625 | 7.0625 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511893 | ZONE-2 SUB 345.00 | 345 | 7.0443 | 7.0443 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511902 | ZONE-3 SUB 345.00 | 345 | 6.984 | 6.984 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 511911 | ZONE-4 SUB 345.00 | 345 | 6.5208 | 6.5208 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 514811 | OKARCHE2 69.000 | 69 | 4.0399 | 4.0399 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 514817 | SVCELRN2 69.000 | 69 | 6.8165 | 6.8165 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 514818 | ELRENO 2 69.000 | 69 | 7.8787 | 7.8787 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515052 | TRIBBEY2 69.000 | 69 | 2.689 | 2.689 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515053 | PEARSNT2 69.000 | 69 | 4.5484 | 4.5484 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515067 | PEARSON2 69.000 | 69 | 3.0408 | 3.0408 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515095 | SRVCEPL2 69.000 | 69 | 2.4545 | 2.4545 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515363 | CENT 4 138.00 | 138 | 3.2827 | 3.2827 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515394 | KEENAN 4 138.00 | 138 | 9.2901 | 9.2901 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515398 | OUSPRT 4 138.00 | 138 | 9.969 | 9.969 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515506 | OKRCHET2 69.000 | 69 | 4.0467 | 4.0467 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515636 | TRIBYTP2 69.000 | 69 | 2.692 | 2.692 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515637 | SRVCPLT2 69.000 | 69 | 2.6965 | 2.6965 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515686 | BLUWND 7 345.00 | 345 | 11.3124 | 11.3124 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515688 | FRNTWND7 345.00 | 345 | 12.861 | 12.861 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 515990 | SKELTON7 345.00 | 345 | 5.1998 | 5.1998 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 516066 | FRNT2WD7 345.00 | 345 | 11.8954 | 11.8954 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 516363 | ARMADILLO_HV138.00 | 138 | 10.3465 | 10.3465 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 520460 | GEARY 4 138.00 | 138 | 5.7807 | 5.7807 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 520490 | MTNVIEW2 69.000 | 69 | 2.3834 | 2.3834 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 520512 | BC SW 4 138.00 | 138 | 6.5924 | 6.5924 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 520543 | PINERDG2 69.000 | 69 | 2.8601 | 2.8601 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 520916 | FRNKLNS2 69.000 | 69 | 5.5753 | 5.5753 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 521006 | MARSHAL4 138.00 | 138 | 8.3795 | 8.3795 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 521024 | PARADSE4 138.00 | 138 | 5.654 | 5.654 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 521088 | WASHITA2 69.000 | 69 | 9.5657 | 9.5657 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 523040 | OLYMPIA7 345.00 | 345 | 12.5764 | 12.5764 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 523103 | NOBLE_WND 3115.00 | 115 | 9.8617 | 9.8617 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 523130 | GRPLNS-HV4-3115.00 | 115 | 6.8531 | 6.8531 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 523131 | GRPLNS-HV2-3115.00 | 115 | 9.0681 | 9.0681 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 523961 | POTTER_CO 7345.00 | 345 | 18.5163 | 18.5163 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 524296 | SPNSPUR_WND7345.00 | 345 | 6.4287 | 6.4287 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 524299 | SPNSPUR_COL7345.00 | 345 | 6.4287 | 6.4287 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 525851 | ELK_CT3 7345.00 | 345 | 15.0871 | 15.0871 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 529200 | OMCDLEC7 345.00 | 345 | 15.3346 | 15.3346 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 529281 | OMKFIND2 69.000 | 69 | 3.8907 | 3.8907 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 539871 | PIXLEY-SOLAR345.00 | 345 | 15.5707 | 15.5707 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 588190 | GEN-2016-128345.00 | 345 | 4.9453 | 4.9453 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 589300 | GEN-2017-092345.00 | 345 | 16.9086 | 16.9086 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 760032 | GEN-2017-133345.00 | 345 | 5.4018 | 5.4018 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 760830 | GEN-2017-149345.00 | 345 | 3.9923 | 3.9923 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 762834 | GEN-2018-049345.00 | 345 | 6.897 | 6.897 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 763131 | GEN-2018-082345.00 | 345 | 12.1657 | 12.1657 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 763769 | GEN-2019-045138.00 | 138 | 15.8988 | 15.8988 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 764075 | GEN-2020-054345.00 | 345 | 14.1588 | 14.1588 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 764510 | GEN-2020-020345.00 | 345 | 15.451 | 15.451 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 765470 | GEN-2021-018345.00 | 345 | 7.6337 | 7.6337 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 765480 | GEN-2021-019345.00 | 345 | 13.232 | 13.232 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 775201 | GEN-2023-161138.00 | 138 | 5.9916 | 5.9916 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 776821 | GEN-2023-102345.00 | 345 | 11.081 | 11.081 | 0
GEN-2026-PR13 | 04 SOUTHEAST | 785701 | GEN-2024-291345.00 | 345 | 13.3639 | 13.3639 | 0

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR13 | 54.559 | PASS | 0.49823 | PASS | N/A | N/A | No

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | BASE CASE | 57.4863 | PASS | 0.50155 | PASS | 401.5454 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511501 [TUTTLE4 138.00] CKT 1 | 57.4687 | PASS | 0.50156 | PASS | 401.5551 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511576 [CEMRD_TP4 138.00] CKT 1 | 57.4863 | PASS | 0.50155 | PASS | 401.5456 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 57.4686 | PASS | 0.50156 | PASS | 401.5562 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 57.4851 | PASS | 0.50155 | PASS | 401.5461 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 57.3437 | PASS | 0.50156 | PASS | 401.5596 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514820 [JENSENT4 138.00] CKT 1 | 57.4849 | PASS | 0.50155 | PASS | 401.547 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 57.473 | PASS | 0.50154 | PASS | 401.5424 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 515962 [OMEGA 4 138.00] CKT 1 | 57.4776 | PASS | 0.50155 | PASS | 401.5455 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514821 [JENSEN 4 138.00] CKT 1 | 57.4644 | PASS | 0.50154 | PASS | 401.5433 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 57.4741 | PASS | 0.50154 | PASS | 401.5432 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 57.4658 | PASS | 0.50154 | PASS | 401.5426 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514863 [HAYMAKR4 138.00] CKT 1 | 57.4212 | PASS | 0.50155 | PASS | 401.5547 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514854 [BRADEN 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 57.4841 | PASS | 0.50154 | PASS | 401.5448 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514863 [HAYMAKR4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 57.4169 | PASS | 0.50155 | PASS | 401.5545 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514864 [PIEDMNT4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 57.4873 | PASS | 0.50155 | PASS | 401.5462 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 57.4674 | PASS | 0.50154 | PASS | 401.5423 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514887 [WESTMOR4 138.00] TO BUS 514902 [MCCLAIN4 138.00] CKT 1 | 57.4796 | PASS | 0.50156 | PASS | 401.5558 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514887 [WESTMOR4 138.00] TO BUS 514928 [SOGATE 4 138.00] CKT 1 | 57.4273 | PASS | 0.50155 | PASS | 401.5482 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514893 [XEROX 4 138.00] TO BUS 514894 [CZECHAL4 138.00] CKT 1 | 57.3256 | PASS | 0.50155 | PASS | 401.5464 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514894 [CZECHAL4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 57.3225 | PASS | 0.50155 | PASS | 401.5451 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 57.4504 | PASS | 0.50155 | PASS | 401.55 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 515481 [STHLAKE4 138.00] CKT 1 | 57.4567 | PASS | 0.50156 | PASS | 401.557 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 515481 [STHLAKE4 138.00] CKT 1 | 57.4575 | PASS | 0.50156 | PASS | 401.5579 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 57.3315 | PASS | 0.50156 | PASS | 401.5583 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514928 [SOGATE 4 138.00] TO BUS 514992 [TURNER 4 138.00] CKT 1 | 57.4248 | PASS | 0.50155 | PASS | 401.5483 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514929 [PLVALLY4 138.00] TO BUS 514953 [HOLLYWD4 138.00] CKT 1 | 57.4576 | PASS | 0.50154 | PASS | 401.537 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514929 [PLVALLY4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 57.4577 | PASS | 0.50154 | PASS | 401.5364 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514946 [MIDWEST4 138.00] CKT 1 | 57.4774 | PASS | 0.50154 | PASS | 401.5358 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514949 [SOONRTP4 138.00] CKT 1 | 57.4868 | PASS | 0.50154 | PASS | 401.5436 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514961 [GM 4 138.00] CKT 1 | 57.4612 | PASS | 0.50155 | PASS | 401.5471 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 57.3464 | PASS | 0.50153 | PASS | 401.5342 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514946 [MIDWEST4 138.00] TO BUS 514953 [HOLLYWD4 138.00] CKT 1 | 57.4829 | PASS | 0.50155 | PASS | 401.5476 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514957 [CHERYCK4 138.00] TO BUS 514958 [BOYD 4 138.00] CKT 1 | 57.4796 | PASS | 0.50154 | PASS | 401.5407 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514957 [CHERYCK4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 57.4813 | PASS | 0.50154 | PASS | 401.5391 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514992 [TURNER 4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 57.4239 | PASS | 0.50155 | PASS | 401.5482 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 57.3726 | PASS | 0.50155 | PASS | 401.5518 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 57.4319 | PASS | 0.50155 | PASS | 401.5488 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 57.4319 | PASS | 0.50155 | PASS | 401.5488 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 57.4384 | PASS | 0.50155 | PASS | 401.5462 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 2 | 57.4507 | PASS | 0.50155 | PASS | 401.5461 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520422 [SEQUOYAHJ4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 57.4866 | PASS | 0.50155 | PASS | 401.548 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520508 [CLVLDSW4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 57.4811 | PASS | 0.50156 | PASS | 401.5564 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 57.4865 | PASS | 0.50155 | PASS | 401.5486 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 57.4841 | PASS | 0.50155 | PASS | 401.5509 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 57.4902 | PASS | 0.50155 | PASS | 401.5465 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 57.471 | PASS | 0.50157 | PASS | 401.5653 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 57.5166 | PASS | 0.50151 | PASS | 401.5055 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511405 [BINGER 4 138.00] CKT 1 | 57.4866 | PASS | 0.50155 | PASS | 401.5458 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511421 [VERDEN 4 138.00] CKT 1 | 57.4863 | PASS | 0.50155 | PASS | 401.549 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511445 [CARNEG-4 138.00] CKT 1 | 57.4854 | PASS | 0.50155 | PASS | 401.5517 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 57.4867 | PASS | 0.50155 | PASS | 401.5487 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4 138.00] CKT 1 | 57.4834 | PASS | 0.50155 | PASS | 401.5455 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 57.4795 | PASS | 0.50155 | PASS | 401.5456 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.4.00] CKT 1 | 57.4848 | PASS | 0.50155 | PASS | 401.5463 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.4.00] CKT 1 | 57.4848 | PASS | 0.50155 | PASS | 401.5463 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.00] CKT 1 | 57.1511 | PASS | 0.50153 | PASS | 401.5286 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 776561 [GEN-2023-229 138.00] CKT 1 | 57.5044 | PASS | 0.50153 | PASS | 401.5273 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.8.00] CKT 1 | 57.4092 | PASS | 0.50153 | PASS | 401.5293 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511501 [TUTTLE4 138.00] TO BUS 511575 [LEONARD4 138.00] CKT 1 | 57.4678 | PASS | 0.50156 | PASS | 401.5565 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511490 [ELKCITY6 230.00] CKT 1 | 57.4243 | PASS | 0.50164 | PASS | 401.6395 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511541 [DEMPSEYR POI 230.00] CKT 1 | 57.2758 | PASS | 0.50154 | PASS | 401.5352 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511553 [CHISHOLM7 345.00] CKT 1 | 57.4152 | PASS | 0.50153 | PASS | 401.5286 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511576 [CEMRD_TP4 138.00] TO BUS 511424 [T-CONCO4 138.00] CKT 1 | 57.4863 | PASS | 0.50155 | PASS | 401.5454 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511576 [CEMRD_TP4 138.00] TO BUS 515864 [CMTRYRD4 138.00] CKT 1 | 57.4863 | PASS | 0.50155 | PASS | 401.5454 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514818 [ELRENO 2 69.00] TO BUS 514817 [SVCELRN2 69.00] CKT 1 | 57.4804 | PASS | 0.50155 | PASS | 401.5457 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514818 [ELRENO 2 69.00] TO BUS 515506 [OKRCHET2 69.00] CKT 1 | 57.4798 | PASS | 0.50155 | PASS | 401.5458 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514818 [ELRENO 2 69.00] TO BUS 514819 [EL-RENO4 138.00] CKT 5 | 57.4693 | PASS | 0.50155 | PASS | 401.5468 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514821 [JENSEN 4 138.00] TO BUS 511540 [CAN_GAS4 138.00] CKT 1 | 57.4822 | PASS | 0.50154 | PASS | 401.5435 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514821 [JENSEN 4 138.00] TO BUS 520893 [EL RENO4 138.00] CKT 1 | 57.469 | PASS | 0.50156 | PASS | 401.5568 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514834 [KETCH 4 138.00] CKT 1 | 57.4849 | PASS | 0.50155 | PASS | 401.5452 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 515466 [MITCHSB4 138.00] CKT 1 | 57.4637 | PASS | 0.50154 | PASS | 401.5399 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514849 [LAKESID4 138.00] CKT 1 | 57.471 | PASS | 0.50155 | PASS | 401.5451 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514852 [SLVRLAK4 138.00] CKT 1 | 57.4878 | PASS | 0.50154 | PASS | 401.5447 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514862 [RICHRDS4 138.00] CKT 1 | 57.486 | PASS | 0.50154 | PASS | 401.5449 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 765691 [G21-041-TAP 138.00] CKT 1 | 57.4674 | PASS | 0.50154 | PASS | 401.5385 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514854 [BRADEN 4 138.00] TO BUS 514852 [SLVRLAK4 138.00] CKT 1 | 57.484 | PASS | 0.50154 | PASS | 401.5443 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514864 [PIEDMNT4 138.00] TO BUS 514862 [RICHRDS4 138.00] CKT 1 | 57.4866 | PASS | 0.50155 | PASS | 401.5452 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 514851 [QUAILCK4 138.00] CKT 1 | 57.485 | PASS | 0.50155 | PASS | 401.5455 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 515374 [CHISHOM4 138.00] CKT 1 | 57.4746 | PASS | 0.50154 | PASS | 401.5437 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 2 | 57.4726 | PASS | 0.50155 | PASS | 401.5472 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 3 | 57.4732 | PASS | 0.50155 | PASS | 401.5476 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 4 | 57.4733 | PASS | 0.50155 | PASS | 401.5475 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514887 [WESTMOR4 138.00] TO BUS 514925 [PENN 4 138.00] CKT 1 | 57.462 | PASS | 0.50155 | PASS | 401.5508 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514893 [XEROX 4 138.00] TO BUS 514896 [MORGAN 4 138.00] CKT 1 | 57.3261 | PASS | 0.50155 | PASS | 401.5471 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 57.2811 | PASS | 0.50155 | PASS | 401.5507 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 2 | 57.2595 | PASS | 0.50155 | PASS | 401.551 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 514998 [MCLN 1S 18.00] CKT 1 | 57.3185 | PASS | 0.50155 | PASS | 401.5504 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 514999 [MCLN 1G 18.00] CKT 1 | 57.3106 | PASS | 0.50156 | PASS | 401.5628 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 515000 [MCLN 2G 18.00] CKT 1 | 57.3105 | PASS | 0.50156 | PASS | 401.5629 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 57.4815 | PASS | 0.50155 | PASS | 401.5536 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 57.4761 | PASS | 0.50154 | PASS | 401.5434 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 57.4723 | PASS | 0.50156 | PASS | 401.5634 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 57.4873 | PASS | 0.50155 | PASS | 401.5469 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 2 | 57.4854 | PASS | 0.50155 | PASS | 401.5482 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 3 | 57.4852 | PASS | 0.50155 | PASS | 401.553 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 4 | 57.4851 | PASS | 0.50155 | PASS | 401.5548 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 57.4569 | PASS | 0.50155 | PASS | 401.5477 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514934 [DRAPER 7 345.00] CKT 3 | 57.4529 | PASS | 0.50155 | PASS | 401.5467 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514934 [DRAPER 7 345.00] CKT 4 | 57.4529 | PASS | 0.50155 | PASS | 401.5467 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514946 [MIDWEST4 138.00] TO BUS 520917 [FRNKLNS4 138.00] CKT 1 | 57.4595 | PASS | 0.50152 | PASS | 401.5191 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514949 [SOONRTP4 138.00] TO BUS 514930 [OAKTRET4 138.00] CKT 1 | 57.4829 | PASS | 0.50155 | PASS | 401.5507 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514949 [SOONRTP4 138.00] TO BUS 514948 [CEDARLN4 138.00] CKT 1 | 57.4828 | PASS | 0.50155 | PASS | 401.5458 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514953 [HOLLYWD4 138.00] TO BUS 514952 [STUBMAN4 138.00] CKT 1 | 57.4892 | PASS | 0.50154 | PASS | 401.5434 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514953 [HOLLYWD4 138.00] TO BUS 514954 [INDNHIL4 138.00] CKT 1 | 57.4561 | PASS | 0.50155 | PASS | 401.5494 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514958 [BOYD 4 138.00] TO BUS 514948 [CEDARLN4 138.00] CKT 1 | 57.4781 | PASS | 0.50154 | PASS | 401.5427 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514961 [GM 4 138.00] TO BUS 515457 [AIRDEPT4 138.00] CKT 1 | 57.4615 | PASS | 0.50155 | PASS | 401.5464 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 57.4548 | PASS | 0.50154 | PASS | 401.5442 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514994 [TINKER54 138.00] CKT 1 | 57.4787 | PASS | 0.50154 | PASS | 401.5441 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515040 [SEMINL1G 20.9.00] CKT 1 | 57.2345 | PASS | 0.5015 | PASS | 401.4988 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 2 | 57.4863 | PASS | 0.50155 | PASS | 401.5471 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515531 [VANOSTP4 138.00] CKT 1 | 57.4887 | PASS | 0.50155 | PASS | 401.5452 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515977 [LKKONWA4 138.00] CKT 1 | 57.492 | PASS | 0.50154 | PASS | 401.5435 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 775520 [G23-177-TAP 138.00] CKT 1 | 57.4828 | PASS | 0.50155 | PASS | 401.5453 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 787770 [G24-360-TAP 138.00] CKT 1 | 57.4889 | PASS | 0.50154 | PASS | 401.5441 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 57.4748 | PASS | 0.50154 | PASS | 401.539 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 2 | 57.4744 | PASS | 0.50154 | PASS | 401.5394 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 3 | 57.4748 | PASS | 0.50154 | PASS | 401.539 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 515800 [GRACMNT7 345.00] CKT 3 | 55.3694 | PASS | 0.50163 | PASS | 401.6261 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515962 [OMEGA 4 138.00] TO BUS 514823 [ROMNOSE4 138.00] CKT 1 | 57.4776 | PASS | 0.50154 | PASS | 401.5443 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 516096 [NORMHLL7 345.00] CKT 2 | 57.2793 | PASS | 0.50155 | PASS | 401.545 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 57.2805 | PASS | 0.50154 | PASS | 401.545 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520422 [SEQUOYAHJ4 138.00] TO BUS 520473 [CKSHATP4 138.00] CKT 1 | 57.4867 | PASS | 0.50155 | PASS | 401.5478 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520422 [SEQUOYAHJ4 138.00] TO BUS 520547 [SEQOYAH4 138.00] CKT 1 | 57.4859 | PASS | 0.50155 | PASS | 401.5467 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520508 [CLVLDSW4 138.00] TO BUS 520859 [COGAR 4 138.00] CKT 1 | 57.4775 | PASS | 0.50156 | PASS | 401.5571 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520508 [CLVLDSW4 138.00] TO BUS 772680 [G23-035-TAP 138.00] CKT 1 | 57.4877 | PASS | 0.50155 | PASS | 401.5453 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520440 [HARPER2 69.00] CKT 1 | 57.4872 | PASS | 0.50155 | PASS | 401.5459 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520807 [ANADRK1 13.8.00] CKT 1 | 57.4863 | PASS | 0.50155 | PASS | 401.5455 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520808 [ANADRK2 13.8.00] CKT 1 | 57.4863 | PASS | 0.50155 | PASS | 401.5455 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520809 [ANADRK3 13.8.00] CKT 1 | 57.4251 | PASS | 0.50154 | PASS | 401.543 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520838 [CADDO 2 69.00] CKT 1 | 57.4846 | PASS | 0.50155 | PASS | 401.5456 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 57.4728 | PASS | 0.50155 | PASS | 401.5456 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.8.00] CKT 1 | 57.3868 | PASS | 0.50154 | PASS | 401.5369 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.8.00] CKT 1 | 57.387 | PASS | 0.50154 | PASS | 401.5367 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.8.00] CKT 1 | 57.3868 | PASS | 0.50154 | PASS | 401.5369 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.8.00] CKT 1 | 57.4374 | PASS | 0.50154 | PASS | 401.5414 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.8.00] CKT 1 | 57.435 | PASS | 0.50154 | PASS | 401.5421 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.8.00] CKT 1 | 57.4116 | PASS | 0.50154 | PASS | 401.5412 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.8.00] CKT 1 | 57.4115 | PASS | 0.50154 | PASS | 401.5415 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.8.00] CKT 1 | 57.415 | PASS | 0.50154 | PASS | 401.5364 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520923 [GEORGIA4 138.00] TO BUS 520912 [FLETCH-4 138.00] CKT 1 | 57.4864 | PASS | 0.50155 | PASS | 401.548 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 520827 [BINGERJ4 138.00] CKT 1 | 57.4716 | PASS | 0.50156 | PASS | 401.563 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521031 [POCASET4 138.00] TO BUS 768080 [G22-055-TAP 138.00] CKT 1 | 57.4859 | PASS | 0.50155 | PASS | 401.5498 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521088 [WASHITA2 69.00] TO BUS 520838 [CADDO 2 69.00] CKT 1 | 57.4851 | PASS | 0.50155 | PASS | 401.5454 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521088 [WASHITA2 69.00] TO BUS 521027 [PINERTP2 69.00] CKT 1 | 57.4806 | PASS | 0.50155 | PASS | 401.5497 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521088 [WASHITA2 69.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 57.4814 | PASS | 0.50155 | PASS | 401.5461 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 520512 [BC SW 4 138.00] CKT 1 | 57.5036 | PASS | 0.50152 | PASS | 401.5221 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 520514 [BCVI SW4 138.00] CKT 1 | 57.4991 | PASS | 0.50153 | PASS | 401.5255 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521129 [CHERRYRD 4 138.00] TO BUS 520513 [BCV SW 4 138.00] CKT 1 | 57.4887 | PASS | 0.50154 | PASS | 401.5415 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521129 [CHERRYRD 4 138.00] TO BUS 521024 [PARADSE4 138.00] CKT 1 | 57.489 | PASS | 0.50155 | PASS | 401.5468 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 56.4286 | PASS | 0.50161 | PASS | 401.6096 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 784534 [G24-252GEN1 13.8.00] CKT 1 | 56.4285 | PASS | 0.50161 | PASS | 401.6088 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 3 | 57.4876 | PASS | 0.50154 | PASS | 401.5416 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 784595 [G24-254XFMR2 34.5.00] CKT 2 | 57.4876 | PASS | 0.50154 | PASS | 401.5411 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 56.8489 | PASS | 0.50157 | PASS | 401.5675 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 784594 [G24-254GEN1 13.8.00] CKT 1 | 56.8489 | PASS | 0.50157 | PASS | 401.567 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784620 [GEN-2024-255 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 3 | 57.4892 | PASS | 0.50154 | PASS | 401.5392 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784620 [GEN-2024-255 345.00] TO BUS 784625 [G24-255XFMR2 34.5.00] CKT 2 | 57.4892 | PASS | 0.50154 | PASS | 401.5389 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784621 [GEN-2024-255 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 57.1017 | PASS | 0.50154 | PASS | 401.5369 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784621 [GEN-2024-255 345.00] TO BUS 784624 [G24-255GEN1 13.8.00] CKT 1 | 57.1017 | PASS | 0.50154 | PASS | 401.5366 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 57.2101 | PASS | 0.5014973133734412 | PASS | 401.4973 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786604 [G24-321GEN1 18.00] CKT 1 | 57.3574 | PASS | 0.50152 | PASS | 401.5186 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786607 [G24-321GEN2 18.00] CKT 1 | 57.3574 | PASS | 0.49827178317170673 | PASS | 401.5186 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 787290 [G24-344-TAP 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 57.0711 | PASS | 0.50148 | PASS | 401.4804 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 787290 [G24-344-TAP 345.00] TO BUS 787170 [G24-340-TAP 345.00] CKT 1 | 57.0612 | PASS | 0.50149 | PASS | 401.4898 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 787290 [G24-344-TAP 345.00] TO BUS 787291 [GEN-2024-344 345.00] CKT 1 | 57.4918 | PASS | 0.50153 | PASS | 401.5348 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 914807 [MINCO_I_&_HV 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 57.4864 | PASS | 0.50155 | PASS | 401.5457 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 914807 [MINCO_I_&_HV 345.00] TO BUS 914809 [MINCO_I_&_T1 34.5.00] CKT 1 | 57.4864 | PASS | 0.50155 | PASS | 401.5455 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | BASE CASE | 55.9921 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511501 [TUTTLE4 138.00] CKT 1 | 55.989 | PASS | 0.49828 | PASS | 398.2781 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511576 [CEMRD_TP4 138.00] CKT 1 | 55.9922 | PASS | 0.49828 | PASS | 398.2755 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 55.9888 | PASS | 0.49828 | PASS | 398.2789 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 55.9896 | PASS | 0.49828 | PASS | 398.2778 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 55.9486 | PASS | 0.49828 | PASS | 398.2756 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514820 [JENSENT4 138.00] CKT 1 | 55.9913 | PASS | 0.49828 | PASS | 398.2765 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 55.9811 | PASS | 0.49827 | PASS | 398.2739 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 515962 [OMEGA 4 138.00] CKT 1 | 55.9821 | PASS | 0.49828 | PASS | 398.2751 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514821 [JENSEN 4 138.00] CKT 1 | 55.977 | PASS | 0.49828 | PASS | 398.2759 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 55.9831 | PASS | 0.49827 | PASS | 398.2747 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 55.9764 | PASS | 0.49828 | PASS | 398.2759 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514863 [HAYMAKR4 138.00] CKT 1 | 55.9396 | PASS | 0.49828 | PASS | 398.2786 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514854 [BRADEN 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 55.9944 | PASS | 0.49828 | PASS | 398.2803 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514863 [HAYMAKR4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 55.9369 | PASS | 0.49828 | PASS | 398.2776 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514864 [PIEDMNT4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 55.9946 | PASS | 0.49828 | PASS | 398.279 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 55.983 | PASS | 0.49828 | PASS | 398.2803 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514887 [WESTMOR4 138.00] TO BUS 514902 [MCCLAIN4 138.00] CKT 1 | 55.9847 | PASS | 0.49828 | PASS | 398.2811 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514887 [WESTMOR4 138.00] TO BUS 514928 [SOGATE 4 138.00] CKT 1 | 55.9449 | PASS | 0.49828 | PASS | 398.2766 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514893 [XEROX 4 138.00] TO BUS 514894 [CZECHAL4 138.00] CKT 1 | 55.8841 | PASS | 0.49827 | PASS | 398.2732 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514894 [CZECHAL4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 55.8816 | PASS | 0.49827 | PASS | 398.2736 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 55.9523 | PASS | 0.49828 | PASS | 398.2765 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 515481 [STHLAKE4 138.00] CKT 1 | 55.9622 | PASS | 0.49828 | PASS | 398.2785 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 515481 [STHLAKE4 138.00] CKT 1 | 55.9634 | PASS | 0.49828 | PASS | 398.2787 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 55.8434 | PASS | 0.49828 | PASS | 398.2792 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514928 [SOGATE 4 138.00] TO BUS 514992 [TURNER 4 138.00] CKT 1 | 55.9443 | PASS | 0.49828 | PASS | 398.2766 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514929 [PLVALLY4 138.00] TO BUS 514953 [HOLLYWD4 138.00] CKT 1 | 55.974 | PASS | 0.49827 | PASS | 398.2696 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514929 [PLVALLY4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 55.9741 | PASS | 0.49827 | PASS | 398.2692 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514946 [MIDWEST4 138.00] CKT 1 | 55.9872 | PASS | 0.49828 | PASS | 398.2769 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514949 [SOONRTP4 138.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2757 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514961 [GM 4 138.00] CKT 1 | 55.9782 | PASS | 0.49828 | PASS | 398.2777 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 515003 [BARNES 4 138.00] CKT 1 | 55.917 | PASS | 0.49827 | PASS | 398.2705 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514946 [MIDWEST4 138.00] TO BUS 514953 [HOLLYWD4 138.00] CKT 1 | 55.9906 | PASS | 0.49828 | PASS | 398.2758 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514957 [CHERYCK4 138.00] TO BUS 514958 [BOYD 4 138.00] CKT 1 | 55.9873 | PASS | 0.49827 | PASS | 398.2726 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514957 [CHERYCK4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 55.9886 | PASS | 0.49827 | PASS | 398.2719 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514992 [TURNER 4 138.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 55.9438 | PASS | 0.49828 | PASS | 398.2765 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 55.9068 | PASS | 0.49828 | PASS | 398.2786 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 2 | 55.9513 | PASS | 0.49828 | PASS | 398.2771 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 3 | 55.9513 | PASS | 0.49828 | PASS | 398.2771 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 55.9731 | PASS | 0.49828 | PASS | 398.2752 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 2 | 55.9781 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520422 [SEQUOYAHJ4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 55.9892 | PASS | 0.49828 | PASS | 398.2767 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520508 [CLVLDSW4 138.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 55.9716 | PASS | 0.49828 | PASS | 398.279 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520923 [GEORGIA4 138.00] CKT 1 | 55.9844 | PASS | 0.49828 | PASS | 398.2772 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521031 [POCASET4 138.00] CKT 1 | 55.9854 | PASS | 0.49828 | PASS | 398.2786 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521129 [CHERRYRD 4 138.00] CKT 1 | 55.9935 | PASS | 0.49828 | PASS | 398.2758 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 55.9715 | PASS | 0.49828 | PASS | 398.2798 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521089 [WASHITA4 138.00] TO BUS 521103 [SLKHILLS 4 138.00] CKT 1 | 56.0008 | PASS | 0.49827 | PASS | 398.2694 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511405 [BINGER 4 138.00] CKT 1 | 55.9917 | PASS | 0.49828 | PASS | 398.2757 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511421 [VERDEN 4 138.00] CKT 1 | 55.9869 | PASS | 0.49828 | PASS | 398.2757 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511445 [CARNEG-4 138.00] CKT 1 | 55.9789 | PASS | 0.49828 | PASS | 398.2755 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511483 [NORGE--4 138.00] CKT 1 | 55.9871 | PASS | 0.49828 | PASS | 398.2758 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511563 [ELSWORTH 4 138.00] CKT 1 | 55.991 | PASS | 0.49827 | PASS | 398.2748 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511586 [TONKAWA4 138.00] CKT 1 | 55.9922 | PASS | 0.49828 | PASS | 398.2763 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511846 [SWS1-1 14.4.00] CKT 1 | 55.9908 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511847 [SWS2-1 14.4.00] CKT 1 | 55.9908 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511848 [SWS3-1 24.00] CKT 1 | 55.9829 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 776561 [GEN-2023-229 138.00] CKT 1 | 56.0045 | PASS | 0.49827 | PASS | 398.2738 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511477 [S.W.S.-4 138.00] TO BUS 511849 [SWS NG4 13.8.00] CKT 1 | 55.9919 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511501 [TUTTLE4 138.00] TO BUS 511575 [LEONARD4 138.00] CKT 1 | 55.9882 | PASS | 0.49828 | PASS | 398.2786 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511490 [ELKCITY6 230.00] CKT 1 | 55.9798 | PASS | 0.4983 | PASS | 398.3021 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511541 [DEMPSEYR POI 230.00] CKT 1 | 55.8727 | PASS | 0.49828 | PASS | 398.2846 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511557 [CHISHOLM6 230.00] TO BUS 511553 [CHISHOLM7 345.00] CKT 1 | 55.9662 | PASS | 0.49827 | PASS | 398.271 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511576 [CEMRD_TP4 138.00] TO BUS 511424 [T-CONCO4 138.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 511576 [CEMRD_TP4 138.00] TO BUS 515864 [CMTRYRD4 138.00] CKT 1 | 55.9921 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514818 [ELRENO 2 69.00] TO BUS 514817 [SVCELRN2 69.00] CKT 1 | 55.9854 | PASS | 0.49828 | PASS | 398.2757 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514818 [ELRENO 2 69.00] TO BUS 515506 [OKRCHET2 69.00] CKT 1 | 55.9885 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514818 [ELRENO 2 69.00] TO BUS 514819 [EL-RENO4 138.00] CKT 5 | 55.9788 | PASS | 0.49828 | PASS | 398.276 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514821 [JENSEN 4 138.00] TO BUS 511540 [CAN_GAS4 138.00] CKT 1 | 55.9856 | PASS | 0.49827 | PASS | 398.2735 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514821 [JENSEN 4 138.00] TO BUS 520893 [EL RENO4 138.00] CKT 1 | 55.9862 | PASS | 0.49828 | PASS | 398.282 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514834 [KETCH 4 138.00] CKT 1 | 55.9926 | PASS | 0.49828 | PASS | 398.2758 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 515466 [MITCHSB4 138.00] CKT 1 | 55.963 | PASS | 0.49827 | PASS | 398.273 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514849 [LAKESID4 138.00] CKT 1 | 55.9826 | PASS | 0.49828 | PASS | 398.2768 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514852 [SLVRLAK4 138.00] CKT 1 | 55.9936 | PASS | 0.49828 | PASS | 398.2771 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 514862 [RICHRDS4 138.00] CKT 1 | 55.9933 | PASS | 0.49828 | PASS | 398.2762 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514853 [DVISION4 138.00] TO BUS 765691 [G21-041-TAP 138.00] CKT 1 | 55.9839 | PASS | 0.49827 | PASS | 398.2748 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514854 [BRADEN 4 138.00] TO BUS 514852 [SLVRLAK4 138.00] CKT 1 | 55.994 | PASS | 0.49828 | PASS | 398.2797 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514864 [PIEDMNT4 138.00] TO BUS 514862 [RICHRDS4 138.00] CKT 1 | 55.9941 | PASS | 0.49828 | PASS | 398.2771 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 514851 [QUAILCK4 138.00] CKT 1 | 55.9922 | PASS | 0.49828 | PASS | 398.2759 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 515374 [CHISHOM4 138.00] CKT 1 | 55.9854 | PASS | 0.49828 | PASS | 398.2756 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 2 | 55.9811 | PASS | 0.49827 | PASS | 398.2742 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 3 | 55.9819 | PASS | 0.49827 | PASS | 398.2743 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 4 | 55.9874 | PASS | 0.49828 | PASS | 398.2806 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514887 [WESTMOR4 138.00] TO BUS 514925 [PENN 4 138.00] CKT 1 | 55.9875 | PASS | 0.49828 | PASS | 398.2792 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514893 [XEROX 4 138.00] TO BUS 514896 [MORGAN 4 138.00] CKT 1 | 55.8846 | PASS | 0.49827 | PASS | 398.2736 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 55.8609 | PASS | 0.49831 | PASS | 398.3132 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 2 | 55.7995 | PASS | 0.49823 | PASS | 398.2255 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 514998 [MCLN 1S 18.00] CKT 1 | 55.7948 | PASS | 0.49829 | PASS | 398.2865 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 514999 [MCLN 1G 18.00] CKT 1 | 55.7967 | PASS | 0.49828 | PASS | 398.2818 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514902 [MCCLAIN4 138.00] TO BUS 515000 [MCLN 2G 18.00] CKT 1 | 55.7966 | PASS | 0.49828 | PASS | 398.2818 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 55.9891 | PASS | 0.49828 | PASS | 398.2755 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514906 [JNSKAMO4 138.00] CKT 1 | 55.9926 | PASS | 0.49828 | PASS | 398.2769 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 55.9765 | PASS | 0.49828 | PASS | 398.2798 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 55.9889 | PASS | 0.49828 | PASS | 398.2763 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 2 | 55.9913 | PASS | 0.49827 | PASS | 398.2745 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 3 | 55.9875 | PASS | 0.49827 | PASS | 398.2742 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 4 | 55.9876 | PASS | 0.49827 | PASS | 398.2747 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514934 [DRAPER 7 345.00] CKT 2 | 55.9763 | PASS | 0.49827 | PASS | 398.2741 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514934 [DRAPER 7 345.00] CKT 3 | 55.9618 | PASS | 0.49825 | PASS | 398.2508 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514933 [DRAPER 4 138.00] TO BUS 514934 [DRAPER 7 345.00] CKT 4 | 55.9618 | PASS | 0.49825 | PASS | 398.2508 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514946 [MIDWEST4 138.00] TO BUS 520917 [FRNKLNS4 138.00] CKT 1 | 55.9759 | PASS | 0.49827 | PASS | 398.2675 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514949 [SOONRTP4 138.00] TO BUS 514930 [OAKTRET4 138.00] CKT 1 | 55.9905 | PASS | 0.49828 | PASS | 398.2784 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514949 [SOONRTP4 138.00] TO BUS 514948 [CEDARLN4 138.00] CKT 1 | 55.9897 | PASS | 0.49828 | PASS | 398.2765 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514953 [HOLLYWD4 138.00] TO BUS 514952 [STUBMAN4 138.00] CKT 1 | 55.9941 | PASS | 0.49827 | PASS | 398.2743 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514953 [HOLLYWD4 138.00] TO BUS 514954 [INDNHIL4 138.00] CKT 1 | 55.9742 | PASS | 0.49828 | PASS | 398.2772 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514958 [BOYD 4 138.00] TO BUS 514948 [CEDARLN4 138.00] CKT 1 | 55.9862 | PASS | 0.49827 | PASS | 398.2735 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 514961 [GM 4 138.00] TO BUS 515457 [AIRDEPT4 138.00] CKT 1 | 55.9745 | PASS | 0.49828 | PASS | 398.2771 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514993 [SE15TH 4 138.00] CKT 1 | 55.9748 | PASS | 0.49828 | PASS | 398.275 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515003 [BARNES 4 138.00] TO BUS 514994 [TINKER54 138.00] CKT 1 | 55.9868 | PASS | 0.49827 | PASS | 398.2747 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515040 [SEMINL1G 20.9.00] CKT 1 | 55.6697 | PASS | 0.49826 | PASS | 398.2634 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 2 | 55.9922 | PASS | 0.49828 | PASS | 398.2762 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515531 [VANOSTP4 138.00] CKT 1 | 55.9943 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515977 [LKKONWA4 138.00] CKT 1 | 55.9971 | PASS | 0.49827 | PASS | 398.2736 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 775520 [G23-177-TAP 138.00] CKT 1 | 55.9867 | PASS | 0.49828 | PASS | 398.2765 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 787770 [G24-360-TAP 138.00] CKT 1 | 55.9946 | PASS | 0.49827 | PASS | 398.2747 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 55.9808 | PASS | 0.49827 | PASS | 398.272 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 2 | 55.9806 | PASS | 0.49827 | PASS | 398.2723 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 3 | 55.9808 | PASS | 0.49827 | PASS | 398.272 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515802 [GRACMNT4 138.00] TO BUS 515800 [GRACMNT7 345.00] CKT 3 | 54.559 | PASS | 0.49832 | PASS | 398.3184 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 515962 [OMEGA 4 138.00] TO BUS 514823 [ROMNOSE4 138.00] CKT 1 | 55.9819 | PASS | 0.49827 | PASS | 398.2741 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 516096 [NORMHLL7 345.00] CKT 2 | 55.8214 | PASS | 0.49827 | PASS | 398.2733 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 55.8204 | PASS | 0.49827 | PASS | 398.2733 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520422 [SEQUOYAHJ4 138.00] TO BUS 520473 [CKSHATP4 138.00] CKT 1 | 55.9895 | PASS | 0.49828 | PASS | 398.2765 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520422 [SEQUOYAHJ4 138.00] TO BUS 520547 [SEQOYAH4 138.00] CKT 1 | 55.9912 | PASS | 0.49828 | PASS | 398.2758 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520508 [CLVLDSW4 138.00] TO BUS 520859 [COGAR 4 138.00] CKT 1 | 55.9793 | PASS | 0.49828 | PASS | 398.2777 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520508 [CLVLDSW4 138.00] TO BUS 772680 [G23-035-TAP 138.00] CKT 1 | 55.9889 | PASS | 0.49828 | PASS | 398.2763 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520440 [HARPER2 69.00] CKT 1 | 55.9937 | PASS | 0.49828 | PASS | 398.2757 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520807 [ANADRK1 13.8.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520808 [ANADRK2 13.8.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520809 [ANADRK3 13.8.00] CKT 1 | 55.8996 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520838 [CADDO 2 69.00] CKT 1 | 55.9894 | PASS | 0.49828 | PASS | 398.2756 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520810 [ANADARK2 69.00] TO BUS 520814 [ANADARK4 138.00] CKT 1 | 55.9708 | PASS | 0.49828 | PASS | 398.2755 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520811 [ANADRK4 13.8.00] CKT 1 | 55.821 | PASS | 0.49827 | PASS | 398.2745 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520812 [ANADRK5 13.8.00] CKT 1 | 55.821 | PASS | 0.49827 | PASS | 398.2745 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 520813 [ANADRK6 13.8.00] CKT 1 | 55.821 | PASS | 0.49827 | PASS | 398.2745 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521101 [GENCO1 13.8.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2753 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521102 [GENCO2 13.8.00] CKT 1 | 55.9095 | PASS | 0.49828 | PASS | 398.2751 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521110 [ORME1 13.8.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521111 [ORME2 13.8.00] CKT 1 | 55.992 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520814 [ANADARK4 138.00] TO BUS 521112 [ORME3 13.8.00] CKT 1 | 55.9919 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 520923 [GEORGIA4 138.00] TO BUS 520912 [FLETCH-4 138.00] CKT 1 | 55.9845 | PASS | 0.49828 | PASS | 398.277 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521017 [ONEY 4 138.00] TO BUS 520827 [BINGERJ4 138.00] CKT 1 | 55.9719 | PASS | 0.49828 | PASS | 398.2793 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521031 [POCASET4 138.00] TO BUS 768080 [G22-055-TAP 138.00] CKT 1 | 55.9871 | PASS | 0.49828 | PASS | 398.2779 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521088 [WASHITA2 69.00] TO BUS 520838 [CADDO 2 69.00] CKT 1 | 55.9895 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521088 [WASHITA2 69.00] TO BUS 521027 [PINERTP2 69.00] CKT 1 | 55.9876 | PASS | 0.49828 | PASS | 398.276 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521088 [WASHITA2 69.00] TO BUS 521089 [WASHITA4 138.00] CKT 1 | 55.9829 | PASS | 0.49828 | PASS | 398.2756 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 520512 [BC SW 4 138.00] CKT 1 | 55.9979 | PASS | 0.49827 | PASS | 398.2711 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521103 [SLKHILLS 4 138.00] TO BUS 520514 [BCVI SW4 138.00] CKT 1 | 55.9944 | PASS | 0.49827 | PASS | 398.2727 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521129 [CHERRYRD 4 138.00] TO BUS 520513 [BCV SW 4 138.00] CKT 1 | 55.9941 | PASS | 0.49827 | PASS | 398.2737 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 521129 [CHERRYRD 4 138.00] TO BUS 521024 [PARADSE4 138.00] CKT 1 | 55.9917 | PASS | 0.49828 | PASS | 398.2754 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 54.8797 | PASS | 0.49832 | PASS | 398.3233 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 784534 [G24-252GEN1 13.8.00] CKT 1 | 54.8793 | PASS | 0.49832 | PASS | 398.3227 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 3 | 55.9933 | PASS | 0.49827 | PASS | 398.2717 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 784595 [G24-254XFMR2 34.5.00] CKT 2 | 55.9931 | PASS | 0.49827 | PASS | 398.2714 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 55.3416 | PASS | 0.49827 | PASS | 398.2675 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 784594 [G24-254GEN1 13.8.00] CKT 1 | 55.3414 | PASS | 0.49827 | PASS | 398.2672 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784620 [GEN-2024-255 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 3 | 55.9924 | PASS | 0.49827 | PASS | 398.2739 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784620 [GEN-2024-255 345.00] TO BUS 784625 [G24-255XFMR2 34.5.00] CKT 2 | 55.9921 | PASS | 0.49827 | PASS | 398.2739 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784621 [GEN-2024-255 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 55.5663 | PASS | 0.49828 | PASS | 398.2751 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 784621 [GEN-2024-255 345.00] TO BUS 784624 [G24-255GEN1 13.8.00] CKT 1 | 55.566 | PASS | 0.49828 | PASS | 398.2751 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 55.6503 | PASS | 0.49827 | PASS | 398.2726 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786604 [G24-321GEN1 18.00] CKT 1 | 55.8305 | PASS | 0.49827 | PASS | 398.2718 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786607 [G24-321GEN2 18.00] CKT 1 | 55.8305 | PASS | 0.49827 | PASS | 398.2718 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 787290 [G24-344-TAP 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 55.5004 | PASS | 0.49824 | PASS | 398.2425 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 787290 [G24-344-TAP 345.00] TO BUS 787170 [G24-340-TAP 345.00] CKT 1 | 55.4938 | PASS | 0.49825 | PASS | 398.2475 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 787290 [G24-344-TAP 345.00] TO BUS 787291 [GEN-2024-344 345.00] CKT 1 | 55.9938 | PASS | 0.49827 | PASS | 398.2719 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 914807 [MINCO_I_&_HV 345.00] TO BUS 514801 [MINCO 7 345.00] CKT 1 | 55.9923 | PASS | 0.49828 | PASS | 398.2755 | 25.96 | 31.3
GEN-2026-PR13 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR13 | 345kV Bus at OGE Minco Substation, Hinton County, OK | OPEN LINE FROM BUS 914807 [MINCO_I_&_HV 345.00] TO BUS 914809 [MINCO_I_&_T1 34.5.00] CKT 1 | 55.9922 | PASS | 0.49828 | PASS | 398.2755 | 25.96 | 31.3

## WSCR
* WSCR is not applicable for this study.