## Executive Summary
Executive Summary: Group 04 GEN-2026-PR14 Priority Process Study
Interconnection Customer GEN-2026-PR14 (Group 04) has requested an Interconnection Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT). The DISIS Manual Version 4.4 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gimodifications@spp.org for more information about the study process.
DISIS Manual Version 4.4
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20260331.pdf
This Priority Process analyzes the impact of interconnecting new PR14 generation for total of:
43.99 MW
The minimum cost of interconnecting GEN-2026-PR14 included in this Priority Process is estimated at:
Total Network Upgrade $ 0 Steady State Network Upgrade $ 0 Stability Network Upgrade $ 0 Steady State/Stability Network Upgrade $ 0 Interconnection Costs TBD
Models Used in Steady State Study
2025 ITP Series
Winter: 2029
Summer: 2026, 2029
Models Used in Stability Study
2024 MDWG
Winter: 2029, Summer: 2029
* 2024 MDAG Transition models developed for DISIS-2023-001 were utilized for this study. These models were updated to incorporate and dispatch DISIS-2024-001 requests located within five bus levels of the GEN-2026-PR14 point of interconnection (POI), in order to assess the stability impacts of nearby projects in accordance with queue order.
By: SPP Generator Interconnection Department
Published: 07/30/2026
Costs for Battery Requests were allocated using the 29SP (summer peak) model.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Refer to the 'JTIQ Screening Summary' tab for JTIQ impact of the request based on DISIS Manual Section 4.6 and in accordance to Section 9.4.2(d) of the MISO-SPP JOA.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4622500% | SPP | Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2026-PR14 | 04 SOUTHEAST | 38 | Priority Process | Battery/Storage | 43.99 | 0 | 0 | 0 | 0 | 0 | 0 | 43.99 | 43,99 | -2.8993 | ER | OG&E | Sooner - Cleveland 345kV | None
GEN-2026-PR13 | 04 SOUTHEAST | 37 | Priority Process | Wind | 25.96 | [9 empty] | ER | OG&E | Minco 345kV Substation | None
GEN-2026-PR12 | 04 SOUTHEAST | 36 | Priority Process | Wind | 11.96 | [9 empty] | ER | OG&E | NARDINS2 69kV | None
GEN-2026-PR11 | 05 SOUTHWEST | 35 | Priority Process | Wind | 30 | [9 empty] | ER | SPS | Lost Draw 3 115kV substation | None
GEN-2026-PR9 | 05 SOUTHWEST | 34 | Priority Process | Wind | 15.99 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | None
GEN-2026-PR7 | 03 CENTRAL | 33 | Priority Process | Wind | 39.76 | [9 empty] | ER | MIDW | South Hays 230kV | None
GEN-2026-PR6 | 04 SOUTHEAST | 32 | Priority Process | Wind | 49.72 | [9 empty] | ER | OG&E | Woodring 345kV Substation | None
GEN-2026-PR5 | 04 SOUTHEAST | 31 | Priority Process | Battery/Storage | 60.4 | [9 empty] | ER | OG&E | Woodring 345 kV Substation | None
GEN-2026-PR4 | 05 SOUTHWEST | 30 | Priority Process | Battery/Storage | 131.56 | [9 empty] | ER | SPS | Hitchland 345kV | None
GEN-2026-PR3 | 04 SOUTHEAST | 29 | Priority Process | Wind | 49.68 | [9 empty] | ER | OG&E | Otter 138kV | None
GEN-2026-PR2 | 04 SOUTHEAST | 28 | Priority Process | Wind | 41.89 | [9 empty] | ER | OG&E | Tatonga 345 kV Substation | None
GEN-2026-PR1 | 05 SOUTHWEST | 27 | Priority Process | Wind | 52.63 | [9 empty] | ER | OG&E | Beaver County 345 kV Substation | None
ASGI-2024-001 | 01 NORTH | 26 | DIS-24-1 | Thermal | 17.1 | [9 empty] | ER | WAPA | Pine Lake 12.47 kV | DISIS STAGE
ASGI-2024-002 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 30 | [9 empty] | ER | SPS | GridLiance's Cougar 69 kV Substation | DISIS STAGE
ASGI-2024-003 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 79.8 | [9 empty] | ER/NR | SUNC | Rolla 115 kV Substation | DISIS STAGE
ASGI-2024-006 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | KCPL | Y-road 115 kV switching station | DISIS STAGE
ASGI-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 47.99 | [9 empty] | ER/NR | KCPL | Marshall Miami 13.2 kV Substation | DISIS STAGE
ASGI-2024-008 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 86 | [9 empty] | ER/NR | KCPL | Marshall Miami 161 kV Substation | DISIS STAGE
ASGI-2024-020 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 131.58 | [9 empty] | ER/NR | WERE | Johns-Manville 115 kV Substation | DISIS STAGE
ASGI-2024-023 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | AEPW | Hope NW - Fulton 115 kV Line | DISIS STAGE
ASGI-2024-024 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 79 | [9 empty] | ER/NR | KCPL | Alabama St 161 kV Substation | DISIS STAGE
GEN-2024-003 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 102.2 | [9 empty] | ER | AEPW | Fitzhugh 161kV | DISIS STAGE
GEN-2024-007 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | MIDW | Seward 115 kV Substation | DISIS STAGE
GEN-2024-013 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 496 | [9 empty] | ER/NR | OKGE | Norman Hills 345 kV | DISIS STAGE
GEN-2024-015 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 280 | [9 empty] | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation | DISIS STAGE
GEN-2024-016 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | MIDW | Post Rock - Macon 345 kV Line | DISIS STAGE
GEN-2024-017 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-018 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 31 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-019 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 62 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation | DISIS STAGE
GEN-2024-020 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-021 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 540 | [9 empty] | ER/NR | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2024-022 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 390 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-023 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 270 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2024-025 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-029 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Crescent 138 kV Substation | DISIS STAGE
GEN-2024-030 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Santa Fe 115 kV Substation | DISIS STAGE
GEN-2024-032 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SUNC | Hugoton 115 kV Substation | DISIS STAGE
GEN-2024-034 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 175 | [9 empty] | ER/NR | WAPA | Forman 115 kV Substation | DISIS STAGE
GEN-2024-035 | 01 NORTH | 26 | DIS-24-1 | Hybrid | 270 | [9 empty] | ER/NR | WAPA | Groton 345 kV Substation | DISIS STAGE
GEN-2024-038 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | OPPD | Cooper - S12080 161 kV line | DISIS STAGE
GEN-2024-039 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Humboldt - S1280 161 kV line | DISIS STAGE
GEN-2024-040 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 174 | [9 empty] | ER/NR | OPPD | S3458 to Cooper 345 kV line | DISIS STAGE
GEN-2024-041 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV Line | DISIS STAGE
GEN-2024-042 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Tuco - Whirlwind 345 kV line | DISIS STAGE
GEN-2024-043 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | Crossroads - Tolk 345 kV Line | DISIS STAGE
GEN-2024-044 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 36 | [9 empty] | ER/NR | AEPW | Hosston - Plain Dealing 69 kV Line | DISIS STAGE
GEN-2024-045 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland - Moore 230kV line | DISIS STAGE
GEN-2024-046 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 345 | [9 empty] | ER/NR | SPS | Hitchland-Moore 230 kV line | DISIS STAGE
GEN-2024-050 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Olson 230 kV Substation | DISIS STAGE
GEN-2024-051 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 170 | [9 empty] | ER/NR | LES | Waverly 115 kV Substation | DISIS STAGE
GEN-2024-052 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 42 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-054 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV line | DISIS STAGE
GEN-2024-055 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | KCPL | Butler - Nevada 161 kV line | DISIS STAGE
GEN-2024-056 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | OKGE | Cow Creek - Morrison 138 kV line | DISIS STAGE
GEN-2024-058 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | GRDA | Farmland - Delaware 138 kV line | DISIS STAGE
GEN-2024-061 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Creswell 138 kV Substation | DISIS STAGE
GEN-2024-062 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 230 | [9 empty] | ER/NR | WFEC | Dover SW 138 kV Substation | DISIS STAGE
GEN-2024-063 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 256 | [9 empty] | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2024-065 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | NPPD | FREMONT7 115 kV Substation | DISIS STAGE
GEN-2024-067 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 380 | [9 empty] | ER/NR | SUNC | Cirrus 345 kV Substation | DISIS STAGE
GEN-2024-068 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Lydia - Welsh 345 kV Line | DISIS STAGE
GEN-2024-069 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 228 | [9 empty] | ER/NR | WERE | Franklin 69 kV Substation | DISIS STAGE
GEN-2024-071 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 75 | [9 empty] | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line | DISIS STAGE
GEN-2024-072 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Beloit 115 kV Substation | DISIS STAGE
GEN-2024-073 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads - Hobbs 345 kV Substation | DISIS STAGE
GEN-2024-074 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | KCPL | Duncan Road 161 kV Substation | DISIS STAGE
GEN-2024-076 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2024-077 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-078 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Pringle 230 kV Substation | DISIS STAGE
GEN-2024-079 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-080 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | San Juan 230 kV Substation | DISIS STAGE
GEN-2024-081 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-082 | 01 NORTH | 26 | DIS-24-1 | Thermal | 745 | [9 empty] | ER | WAPA | Springbrook - Tande 345 kV Line | DISIS STAGE
GEN-2024-083 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | WFEC | Hugo 345 kV Substation | DISIS STAGE
GEN-2024-084 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 167 | [9 empty] | ER/NR | EMDE | Reeds Spring - Aurora 161 kV Line | DISIS STAGE
GEN-2024-085 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 160 | [9 empty] | ER/NR | SUNC | Otis 115 kV Substation | DISIS STAGE
GEN-2024-088 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 144.999 | [9 empty] | ER/NR | SPRM | McCartney 161 kV Substation | DISIS STAGE
GEN-2024-089 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 195 | [9 empty] | ER | SPS | Pleasant Hills 230 kV Substation | DISIS STAGE
GEN-2024-090 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-091 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | EMDE | 145 JOPLIN WEST 7TH 161 kV Substation | DISIS STAGE
GEN-2024-092 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199.5 | [9 empty] | ER/NR | SPS | Portales 115 kV Substation | DISIS STAGE
GEN-2024-099 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Newhart 230 kV Substation | DISIS STAGE
GEN-2024-102 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV Substation | DISIS STAGE
GEN-2024-109 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400.5 | [9 empty] | ER/NR | SPS | Tolk - Crossroads 345 kV line | DISIS STAGE
GEN-2024-113 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line | DISIS STAGE
GEN-2024-114 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence County 161 kV Line | DISIS STAGE
GEN-2024-117 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line | DISIS STAGE
GEN-2024-118 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | East 11th Street 138kV Substation | DISIS STAGE
GEN-2024-119 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Lexington 138 kV Substation | DISIS STAGE
GEN-2024-120 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | JNS KAMO 138 kV Substation | DISIS STAGE
GEN-2024-121 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jarbalo 115 kV Substation | DISIS STAGE
GEN-2024-122 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line | DISIS STAGE
GEN-2024-123 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 120 | [9 empty] | ER/NR | AEPW | Center - Tenaha 138 kV Line | DISIS STAGE
GEN-2024-124 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 420 | [9 empty] | ER/NR | SPS | Crossroads-Hobbs-Roadrunner 345 kV Line | DISIS STAGE
GEN-2024-125 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line | DISIS STAGE
GEN-2024-128 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 690 | [9 empty] | ER/NR | OKGE | Gracemont - Lawton 345 kV Line | DISIS STAGE
GEN-2024-129 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 910 | [9 empty] | ER/NR | WERE | Caney River - Neosho 345 kV Line | DISIS STAGE
GEN-2024-132 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1300 | [9 empty] | ER/NR | OKGE | Hugo (71 miles) - Sunnyside (42 miles) 345 kV Line | DISIS STAGE
GEN-2024-134 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-135 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2024-136 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 400 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-137 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-138 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.5 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-139 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 246.08 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-140 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 245.7 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV line | DISIS STAGE
GEN-2024-141 | 01 NORTH | 26 | DIS-24-1 | Wind | 424 | [9 empty] | ER/NR | WAPA | BASIN__-BE4 230 kV Substation | DISIS STAGE
GEN-2024-142 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.03 | [9 empty] | ER/NR | WERE | Reno - Summit 345 kV Line | DISIS STAGE
GEN-2024-143 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-144 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 296.9 | [9 empty] | ER/NR | SUNC | Setab 345 kV Substation | DISIS STAGE
GEN-2024-145 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 243.7 | [9 empty] | ER/NR | SPS | XIT Interchange 230 kV Substation | DISIS STAGE
GEN-2024-153 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-154 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Chisholm 345 kV Substation | DISIS STAGE
GEN-2024-157 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 140 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-158 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 190 | [9 empty] | ER/NR | AEPW | Altus Jct - Snyder 138 kV Line | DISIS STAGE
GEN-2024-159 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Oasis - San Juan Mesa Wind 230 kV Line | DISIS STAGE
GEN-2024-161 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 170 | [9 empty] | ER/NR | AEPW | Hobart - Martha 138 kV Line | DISIS STAGE
GEN-2024-162 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 110 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2024-164 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Arbuckle 138 kV Substation | DISIS STAGE
GEN-2024-165 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-166 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 275 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2024-167 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Orrick 161 kV Substation | DISIS STAGE
GEN-2024-168 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 196.38 | [9 empty] | ER/NR | NPPD | Geneva 115 kV Substation | DISIS STAGE
GEN-2024-170 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 280 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345 kV Substation | DISIS STAGE
GEN-2024-171 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line | DISIS STAGE
GEN-2024-173 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | NPPD | Pawnee Lake 115 kV Substation | DISIS STAGE
GEN-2024-175 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | SPRM | Summit 161 kV Substation | DISIS STAGE
GEN-2024-176 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WERE | Reno County 115 kV Substation | DISIS STAGE
GEN-2024-177 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Red Point 138 kV Substation | DISIS STAGE
GEN-2024-178 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pirkey 138 kV Substation | DISIS STAGE
GEN-2024-180 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Dam 161 kV Substation | DISIS STAGE
GEN-2024-181 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPRM | Brookline 161 kV Substation | DISIS STAGE
GEN-2024-184 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Atoka to Lehigh 138 kV Line | DISIS STAGE
GEN-2024-186 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Roswell Interchange 115 kV Substation | DISIS STAGE
GEN-2024-187 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WFEC | Civit-Stratford 138 kV Line | DISIS STAGE
GEN-2024-189 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SUNC | ITC Great Plains Saddle 345 kV Substation | DISIS STAGE
GEN-2024-193 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Buckner 345 kV Line | DISIS STAGE
GEN-2024-194 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 249.6 | [9 empty] | ER/NR | SUNC | Spearville - Holcomb 345 kV Line | DISIS STAGE
GEN-2024-204 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Brown 138 kV Substation | DISIS STAGE
GEN-2024-205 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SUNC | St. John 115 kV Substation | DISIS STAGE
GEN-2024-206 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 226.3 | [9 empty] | ER/NR | INDN | Blue Valley 161 kV Substation | DISIS STAGE
GEN-2024-207 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 778.6 | [9 empty] | ER/NR | INDN | Blue Valley - Blumil 161 kV Line | DISIS STAGE
GEN-2024-209 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | SUNC | Elm Creek - North Manhattan 230 kV Line | DISIS STAGE
GEN-2024-210 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | St. Francis Tap 115 kV Substation | DISIS STAGE
GEN-2024-211 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-212 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 303 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-213 | 02 NEBRASKA | 26 | DIS-24-1 | Thermal | 360 | [9 empty] | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2024-215 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SUNC | Elm Creek 345 kV Substation | DISIS STAGE
GEN-2024-216 | 01 NORTH | 26 | DIS-24-1 | Wind | 225 | [9 empty] | ER/NR | WAPA | Miles City 230 kV Substation | DISIS STAGE
GEN-2024-217 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Sibley - Hawthorne 345 kV line | DISIS STAGE
GEN-2024-218 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Cimarron River 115 kV Substation | DISIS STAGE
GEN-2024-219 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line | DISIS STAGE
GEN-2024-220 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 55 | [9 empty] | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line | DISIS STAGE
GEN-2024-221 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 400 | [9 empty] | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line | DISIS STAGE
GEN-2024-226 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-227 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | John W Turk Jr Power Plant 345 kV Substation | DISIS STAGE
GEN-2024-228 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Rice to Circle 230 kV Line | DISIS STAGE
GEN-2024-229 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-230 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side - Oklaunion North 345 kV | DISIS STAGE
GEN-2024-231 | 02 NEBRASKA | 26 | DIS-24-1 | Hybrid | 65 | [9 empty] | ER/NR | OPPD | S1399 5 161 kV Substation | DISIS STAGE
GEN-2024-232 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line | DISIS STAGE
GEN-2024-234 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 200 | [9 empty] | ER/NR | OPPD | Raun - Tekamah 161 kV line | DISIS STAGE
GEN-2024-235 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | AEPW | Sooner - Wekiwa 345 kV line | DISIS STAGE
GEN-2024-236 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 241.4 | [9 empty] | ER/NR | OKGE | Seminole - Muskogee 345 kV line | DISIS STAGE
GEN-2024-239 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Cimarron 345 kV Substation | DISIS STAGE
GEN-2024-240 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | AEPW | Neosho - Delaware 345 kV line | DISIS STAGE
GEN-2024-241 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Substation | DISIS STAGE
GEN-2024-242 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OKGE | 515171 138 kV Substation | DISIS STAGE
GEN-2024-243 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50.1 | [9 empty] | ER/NR | SWPA | Van Buren 161 kV Substation | DISIS STAGE
GEN-2024-244 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sooner 115 kV Substation | DISIS STAGE
GEN-2024-245 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | OKGE | Lincoln 138 kV Substation | DISIS STAGE
GEN-2024-246 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | North Loving 115 kV Substation | DISIS STAGE
GEN-2024-247 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 456.6 | [9 empty] | ER | GRDA | Stillwater Northtap 138 kV Substation | DISIS STAGE
GEN-2024-249 | 03 CENTRAL | 26 | DIS-24-1 | Thermal | 721.2 | [9 empty] | ER/NR | WERE | Jeffrey EC 345 kV Substation | DISIS STAGE
GEN-2024-250 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-251 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 125 | [9 empty] | ER/NR | SPS | Atoka 115 kV Substation | DISIS STAGE
GEN-2024-252 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Cimmaron 345 kV Substation | DISIS STAGE
GEN-2024-253 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line | DISIS STAGE
GEN-2024-254 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Mathewson 345 kV Substation | DISIS STAGE
GEN-2024-255 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | OKGE | Spring Creek 345 kV Substation | DISIS STAGE
GEN-2024-257 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 220 | [9 empty] | ER/NR | SUNC | Skellyville 115 kV Tap Substation | DISIS STAGE
GEN-2024-258 | 03 CENTRAL | 26 | DIS-24-1 | Wind | 300 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-259 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199.8 | [9 empty] | ER/NR | WERE | Asbury 161 kV Substation | DISIS STAGE
GEN-2024-260 | 03 CENTRAL | 26 | DIS-24-1 | Storage | 199.8 | [9 empty] | ER/NR | KCPL | East Town 161 kV Substation | DISIS STAGE
GEN-2024-261 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 150 | [9 empty] | ER/NR | SPS | Hobbs - LCEC West 115 kV Line | DISIS STAGE
GEN-2024-265 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 155 | [9 empty] | ER/NR | SPS | Bensing 115 kV Substation | DISIS STAGE
GEN-2024-266 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Potter Co - Hitchland 345 kV Line | DISIS STAGE
GEN-2024-267 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 195 | [9 empty] | ER/NR | WFEC | Durantp4 - Sclmnjc4 138 kV Line | DISIS STAGE
GEN-2024-268 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 390 | [9 empty] | ER/NR | OKGE | Keefton 345 kV Substation | DISIS STAGE
GEN-2024-271 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Chaves County - San Juan Wind 230 kV Line | DISIS STAGE
GEN-2024-272 | 03 CENTRAL | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SUNC | Sawyer 115 kV Substation | DISIS STAGE
GEN-2024-273 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 16.214 | [9 empty] | ER/NR | SPS | Pearl 115 kV Substation | DISIS STAGE
GEN-2024-274 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 175 | [9 empty] | ER/NR | SUNC | Harper - Anthony 138 kV Line | DISIS STAGE
GEN-2024-276 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-277 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line | DISIS STAGE
GEN-2024-278 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 264.3 | [9 empty] | ER/NR | SPS | Eddy County - Crossroads 345 kV Line | DISIS STAGE
GEN-2024-280 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 350 | [9 empty] | ER/NR | SPS | Andrews County 345 kV Substation | DISIS STAGE
GEN-2024-281 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | SPS | Jal - Teague 115 kV Line | DISIS STAGE
GEN-2024-282 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-283 | 01 NORTH | 26 | DIS-24-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Maurine - New Underwood 230 kV Line | DISIS STAGE
GEN-2024-284 | 01 NORTH | 26 | DIS-24-1 | Solar | 199 | [9 empty] | ER/NR | WAPA | Antelope Valley - Broadland 345 kV Line | DISIS STAGE
GEN-2024-285 | 01 NORTH | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | WAPA | Crocker 345 kV Substation | DISIS STAGE
GEN-2024-286 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 136 | [9 empty] | ER | OKGE | AES 5 161 kV Substation | DISIS STAGE
GEN-2024-287 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 199.8 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line | DISIS STAGE
GEN-2024-288 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 130 | [9 empty] | ER/NR | SUNC | Elm Creek - Tobias 345 kV Line | DISIS STAGE
GEN-2024-289 | 03 CENTRAL | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | KCPL | Archie - Clinton 161 kV Line | DISIS STAGE
GEN-2024-291 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 250 | [9 empty] | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2024-293 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 248 | [9 empty] | ER | OKGE | Muskoge7 345 kV Substation | DISIS STAGE
GEN-2024-294 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line | DISIS STAGE
GEN-2024-295 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 115 | [9 empty] | ER/NR | SPS | S Loving 115 kV Substation | DISIS STAGE
GEN-2024-296 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-297 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-298 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 167 | [9 empty] | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line | DISIS STAGE
GEN-2024-299 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 744 | [9 empty] | ER | OKGE | AES 5 345 kV Substation | DISIS STAGE
GEN-2024-303 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-304 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 500 | [9 empty] | ER/NR | SPS | Crossroads 345 kV Substation | DISIS STAGE
GEN-2024-305 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 50 | [9 empty] | ER/NR | AEPW | Superior - Jefferson 69 kV Line | DISIS STAGE
GEN-2024-306 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Taylor Switching Station 115 kV Substation | DISIS STAGE
GEN-2024-308 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | WFEC | Okeene - Mooreland 138 kV line | DISIS STAGE
GEN-2024-310 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-311 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | SPS | Eddy - Chaves 230 kV line | DISIS STAGE
GEN-2024-312 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 50 | [9 empty] | ER/NR | SWPA | Clarksville Ozark 161 kV line | DISIS STAGE
GEN-2024-316 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | AEPW | Pittsburg - Valliant 345 kV Line | DISIS STAGE
GEN-2024-317 | 05 SOUTHWEST | 26 | DIS-24-1 | Solar | 300 | [9 empty] | ER/NR | SPS | Dragon 345 kV Substation | DISIS STAGE
GEN-2024-318 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line | DISIS STAGE
GEN-2024-319 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KACY | Metro 5 161 kV Substation | DISIS STAGE
GEN-2024-320 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | WERE | Jaggard 115 kV Substation | DISIS STAGE
GEN-2024-321 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 493 | [9 empty] | ER/NR | OKGE | Seminole 345 kV Substation | DISIS STAGE
GEN-2024-322 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 75 | [9 empty] | ER/NR | MIDW | Redlin - Beach3 115 kV line | DISIS STAGE
GEN-2024-323 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 356.8 | [9 empty] | ER | WFEC | ITC Hugo 7 345 kV Substation | DISIS STAGE
GEN-2024-324 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 160 | [9 empty] | ER/NR | SPS | Samson 115 kV Substation | DISIS STAGE
GEN-2024-325 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | SPS | Sierra 115 kV Substation | DISIS STAGE
GEN-2024-326 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WAPA | Belfield 230 kV Substation | DISIS STAGE
GEN-2024-327 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Berthold 115 kV Substation | DISIS STAGE
GEN-2024-328 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | WAPA | Little Missouri 230 kV Substation | DISIS STAGE
GEN-2024-329 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WAPA | Pleasant Valley 115 kV Substation | DISIS STAGE
GEN-2024-330 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 225 | [9 empty] | ER/NR | WERE | Midian 138 kV Substation | DISIS STAGE
GEN-2024-331 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WAPA | Round Up 345 kV Substation | DISIS STAGE
GEN-2024-332 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Discovery 138 kV Substation | DISIS STAGE
GEN-2024-333 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Kelley Avenue 138 kV | DISIS STAGE
GEN-2024-334 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 124 | [9 empty] | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2024-336 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Ink Basin 230 kV Substation | DISIS STAGE
GEN-2024-337 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 250 | [9 empty] | ER/NR | OKGE | Sunnyside - Pooleville 138 kV line | DISIS STAGE
GEN-2024-338 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 350 | [9 empty] | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line | DISIS STAGE
GEN-2024-339 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Stranger Creek 115 kV Substation | DISIS STAGE
GEN-2024-340 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1400 | [9 empty] | ER/NR | OKGE | Riverside – Redbud 345 kV line | DISIS STAGE
GEN-2024-341 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1045 | [9 empty] | ER/NR | AEPW | Pittsburgh 345 kV Substation | DISIS STAGE
GEN-2024-343 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 470.5 | [9 empty] | ER/NR | AEPW | LeBrock 345 kV Substation | DISIS STAGE
GEN-2024-344 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Riverside - Redbud Switch 345 kV Line | DISIS STAGE
GEN-2024-345 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 600.001 | [9 empty] | ER/NR | AEPW | Delaware 345 kV Substation | DISIS STAGE
GEN-2024-346 | 04 SOUTHEAST | 26 | DIS-24-1 | Wind | 220 | [9 empty] | ER/NR | AEPW | Coffeyville Tap - North Barlettsville 138 kV Line | DISIS STAGE
GEN-2024-351 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 199 | [9 empty] | ER/NR | SPS | Cooper Ranch 115 kV Substation | DISIS STAGE
GEN-2024-352 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | KCPL | Sibley 345 kV Substation | DISIS STAGE
GEN-2024-355 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 199 | [9 empty] | ER/NR | SPS | Lubbock South 230 kV Substation | DISIS STAGE
GEN-2024-359 | 01 NORTH | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | WAPA | Belfield 345 kV Substation | DISIS STAGE
GEN-2024-360 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 160 | [9 empty] | ER/NR | OKGE | Seminole - Maud 138 kV Line | DISIS STAGE
GEN-2024-361 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 80 | [9 empty] | ER/NR | OKGE | Spring Valley - Warwick 138 kV line | DISIS STAGE
GEN-2024-362 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 140 | [9 empty] | ER/NR | AEPW | Leonard 138 kV Substation | DISIS STAGE
GEN-2024-364 | 05 SOUTHWEST | 26 | DIS-24-1 | Hybrid | 300 | [9 empty] | ER/NR | SPS | Bushland 230 kV Substation | DISIS STAGE
GEN-2024-365 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-366 | 05 SOUTHWEST | 26 | DIS-24-1 | Wind | 200 | [9 empty] | ER/NR | SPS | Hobbs - Yoakum 345 kV Line | DISIS STAGE
GEN-2024-367 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345 kV Substation | DISIS STAGE
GEN-2024-368 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Bowers 115 kV Substation | DISIS STAGE
GEN-2024-369 | 04 SOUTHEAST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | AEPW | Cornville 138 kV Substation | DISIS STAGE
GEN-2024-370 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | KCPL | Smithville 161 kV Substation | DISIS STAGE
GEN-2024-371 | 05 SOUTHWEST | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | SPS | Maddox 115 kV Substation | DISIS STAGE
GEN-2024-372 | 02 NEBRASKA | 26 | DIS-24-1 | Battery/Storage | 250 | [9 empty] | ER/NR | OPPD | S1247 161 kV Substation | DISIS STAGE
GEN-2024-373 | 04 SOUTHEAST | 26 | DIS-24-1 | Hybrid | 120 | [9 empty] | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line | DISIS STAGE
GEN-2024-374 | 02 NEBRASKA | 26 | DIS-24-1 | Solar | 225 | [9 empty] | ER/NR | WAPA | Stegall 345 kV Substation | DISIS STAGE
GEN-2024-375 | 03 CENTRAL | 26 | DIS-24-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Malta Bend - Norton 161 kV Line | DISIS STAGE
GEN-2024-376 | 04 SOUTHEAST | 26 | DIS-24-1 | Solar | 142.183 | [9 empty] | ER/NR | AEPW | Hemphill 138 kV Substation | DISIS STAGE
GEN-2024-377 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Pirkey 345 kV Substation | DISIS STAGE
GEN-2024-379 | 04 SOUTHEAST | 26 | DIS-24-1 | Thermal | 1350.001 | [9 empty] | ER/NR | AEPW | Longwood - El Dorado 345 kV Line | DISIS STAGE
GEN-2013-008 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 1.65 | [9 empty] | ER | SPS | 0
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 02 NEBRASKA | 16 | DIS-16-1 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Gas | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC | 0
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | CT | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.407 | [9 empty] | ER | SWPA | 0
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS | 0
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Buro 115kV substation
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 10.53 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS | 0
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 12 | [9 empty] | ER | KCPL | Paola 161kV
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS | 0
GEN-2019-019 | 01 NORTH | 21 | DIS-18-2_19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-018 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.15 | [9 empty] | ER | SPS | FEC 69kV line
ASGI-2013-002 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
ASGI-2013-003 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 18.4 | [9 empty] | ER | SPS | 0
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS | 0
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS | 0
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | [9 empty] | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 16 | DIS-16-1 | Steam | 22.5 | [9 empty] | ER | SUNC | 0
GEN-2011-046 | 05 SOUTHWEST | 16 | DIS-16-1 | Diesel CT | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS | 0
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS | 0
GEN-2014-035 | 05 SOUTHWEST | 16 | DIS-16-1 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | FACILITY STUDY STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | [9 empty] | ER | KCPL | 0
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 36.6 | [9 empty] | ER | SUNC | Garden City 115kV substation, bus 531445
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | FACILITY STUDY STAGE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wosley Substation 69kV
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 40 | [9 empty] | ER/NR | SPS | 0
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 42.195 | [9 empty] | ER | SPS | 0
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | WAPA | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 50 | [9 empty] | ER/NR | SPS | 0
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 50 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161 kV Substation | FACILITY STUDY STAGE
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | [9 empty] | ER/NR | AEPW | Lydia 345kV substation | FACILITY STUDY STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek – Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland - Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.725 | [9 empty] | ER | SWPA | 0
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EMDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-129 | 03 CENTRAL | 8 | PQ | CT | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR4 | 05 SOUTHWEST | 25 | Replacement | Solar | 72 | [9 empty] | ER | SPS | Cunningham 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-013 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Solar | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 74.9 | [9 empty] | ER/NR | OKGE | Roman Nose 138 kV Substation | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Coal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | FACILITY STUDY STAGE
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR3 | 05 SOUTHWEST | 25 | Replacement | Wind | 80 | [9 empty] | ER/NR | SPS | Norton 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | Powell Corner 115kV Substation
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap | FACILITY STUDY STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | [9 empty] | ER | AEPW | Winnsboro 138 kV Substation | FACILITY STUDY STAGE
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR2 | 04 SOUTHEAST | 25 | Replacement | Thermal | 94.242 | [9 empty] | ER | OKGE | Tinker Air Force Base 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | FACILITY STUDY STAGE
GEN-2023-GR1 | 04 SOUTHEAST | 25 | Replacement | Thermal | 97.488 | [9 empty] | ER | WFEC | Anadarko Power Plant 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-024 | 04 SOUTHEAST | 18 | DIS-17-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | WAPA | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-044 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | FACILITY STUDY STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | FACILITY STUDY STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Woodward 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | GRDA | Kerr Grove 161 kV | FACILITY STUDY STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 100 | [9 empty] | ER/NR | SWPA | Carthage 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | FACILITY STUDY STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 100 | [9 empty] | ER/NR | WFEC | Mooreland - Noel 138 kV Line | FACILITY STUDY STAGE
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 8 | PQ | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs - Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 110 | [9 empty] | ER/NR | BEPC | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-040 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 113 | [9 empty] | ER/NR | AEPW | Snyder – Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | FACILITY STUDY STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | FACILITY STUDY STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | [9 empty] | ER/NR | WFEC | Pharaoh 138 kV Substation | FACILITY STUDY STAGE
GEN-2011-027 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 16 | DIS-16-1 | Gas | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 120 | [9 empty] | ER/NR | NPPD | Grant 115 kV Substation | FACILITY STUDY STAGE
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 125 | [9 empty] | ER/NR | WFEC | Unger - Frogville 138 kV line | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER | SPS | Kress 115 kV Substation | FACILITY STUDY STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | [9 empty] | ER/NR | WERE | Clear Water - Waco 138 kV line | FACILITY STUDY STAGE
GEN-2007-040 | 03 CENTRAL | 8 | PQ | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | FACILITY STUDY STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 135 | [9 empty] | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | FACILITY STUDY STAGE
GEN-2013-012 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER | BEPC | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-037 | 01 NORTH | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EMDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | FACILITY STUDY STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Maud 138 kV substation | FACILITY STUDY STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | SWPA | Jonesboro - Independence 161 kV | FACILITY STUDY STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER | KCPL | Salisbury 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | INDN | Sub M 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | [9 empty] | ER/NR | WAPA | Red Pointe 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Storage | 150 | [9 empty] | ER/NR | GRDA | Pawnee Switch 138 kV | FACILITY STUDY STAGE
GEN-2007-052 | 04 SOUTHEAST | 8 | PQ | Gas | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-GR5 | 05 SOUTHWEST | 25 | Replacement | Solar | 150 | [9 empty] | ER | SPS | Plant X 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | FACILITY STUDY STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 8 | PQ | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | CT | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-019 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | FACILITY STUDY STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 175 | [9 empty] | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | FACILITY STUDY STAGE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2012-024 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Weatherford Jct. to Hinton 138 kV line | FACILITY STUDY STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEPW | Longwood to Scottville 138 kV line | FACILITY STUDY STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | [9 empty] | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | FACILITY STUDY STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | [9 empty] | ER/NR | WFEC | Prague - Chernicky 138 kV Line | FACILITY STUDY STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | FACILITY STUDY STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Caney Creek 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | FACILITY STUDY STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Bison 345kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Battlefield BESS 161kV | FACILITY STUDY STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OKGE | Horseshoe Lake 138 kV Substation | FACILITY STUDY STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | FACILITY STUDY STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | FACILITY STUDY STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | FACILITY STUDY STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | [9 empty] | ER/NR | SUNC | Holcomb 345 kV | FACILITY STUDY STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | FACILITY STUDY STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KCPL | Liberty South 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | FACILITY STUDY STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Storage | 200 | [9 empty] | ER/NR | KACY | Nearman 161 kV Substation | FACILITY STUDY STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | OKGE | Lula 138 kV Substation | FACILITY STUDY STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | FACILITY STUDY STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | [9 empty] | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | FACILITY STUDY STAGE
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 8 | PQ | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | BEPC | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 CENTRAL | 8 | PQ | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 200.22 | [9 empty] | ER/NR | OKGE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-092 | 03 CENTRAL | 8 | PQ | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 8 | PQ | Wind | 201 | [9 empty] | ER | OPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | BEPC | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | FACILITY STUDY STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-045 | 05 SOUTHWEST | 16 | DIS-16-1 | NG CT | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line | FACILITY STUDY STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2015-066 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 225 | [9 empty] | ER/NR | EMDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | [9 empty] | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | FACILITY STUDY STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2_19-1 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | FACILITY STUDY STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-064 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2_19-1 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | FACILITY STUDY STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | NPPD | Twin Church 230 kV Substation | FACILITY STUDY STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | [9 empty] | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | FACILITY STUDY STAGE
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell – Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-18-2_19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2_19-1 | Wind | 255 | [9 empty] | ER | BEPC | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-047 | 05 SOUTHWEST | 8 | PQ | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740 345 kV | FACILITY STUDY STAGE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OKGE | Woodward 345kV Substation | FACILITY STUDY STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | BEPC | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2_19-1 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | FACILITY STUDY STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEPW | Pirkey 345kV Substation | FACILITY STUDY STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | FACILITY STUDY STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | [9 empty] | ER | WERE | Jeffery Energy Center 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | [9 empty] | ER | SUNC | Setab 345 kV | FACILITY STUDY STAGE
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 8 | PQ | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | WERE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2014-040 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 320 | [9 empty] | ER/NR | NPPD | Axtell 345 kV Substation | FACILITY STUDY STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | [9 empty] | ER/NR | SPS | Finney-Carpenter 345 KV line | FACILITY STUDY STAGE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | FACILITY STUDY STAGE
GEN-2007-062 | 04 SOUTHEAST | 8 | PQ | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 475 | [9 empty] | ER/NR | OKGE | Degrasse 345 kV Substation | FACILITY STUDY STAGE
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER/NR | NPPD | New Beatrice Power Station 345 kV | FACILITY STUDY STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | [9 empty] | ER | NPPD | Olive Creek 345 kV Substation | FACILITY STUDY STAGE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | FACILITY STUDY STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | FACILITY STUDY STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | FACILITY STUDY STAGE
GEN-2022-GR1 | 04 SOUTHEAST | 24 | Replacement | Thermal | 513 | [9 empty] | ER | AEPW | Pirkey 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Gas | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEPW | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 914.6 | [9 empty] | ER | AEPW | Welsh-Lydia 345kV Line | FACILITY STUDY STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 102 | [9 empty] | ER/NR | BEPC
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
ASGI-2016-007NWE208 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2005-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2006-015IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2009-018IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | BEPC
GEN-2009-020AIS | 01 NORTH | 16 | DIS-16-1 | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 16 | DIS-16-1 | Wind | 110 | [9 empty] | ER/NR | BEPC
GEN-2014-006IS | 01 NORTH | 16 | DIS-16-1 | Gas | 125 | [9 empty] | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2014-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 150 | [9 empty] | ER/NR | BEPC
GEN-2013-009IS | 01 NORTH | 16 | DIS-16-1 | Wind | 19.5 | [9 empty] | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | 16 | DIS-16-1 | Wind | 20 | [9 empty] | ER | WAPA
GEN-2008-008IS | 01 NORTH | 16 | DIS-16-1 | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2005-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | 16 | DIS-16-1 | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | 16 | DIS-16-1 | Wind | 34 | [9 empty] | ER/NR | BEPC
GEN-2007-020IS | 01 NORTH | 16 | DIS-16-1 | Wind | 16 | [9 empty] | ER/NR | BEPC
GEN-2009-001IS | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER/NR | BEPC
BEPCNDPW1 | 01 NORTH | 18 | DIS-17-1 | Wind | 5 | [9 empty] | ER | BEPC
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 167.2 | [9 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 127.9 | [9 empty] | ER | OTP
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 230 | [9 empty] | ER/NR | OTP
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 140 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 284 | [9 empty] | ER/NR | OTP
J569 | 01 NORTH | 2 | ICS1 | Wind | 100 | [9 empty] | ER/NR | XEL
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 22 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 45 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.7 | [9 empty] | ER | WERE
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
J476 | 03 CENTRAL | 2 | ICS1 | Wind | 246 | [9 empty] | ER/NR | MEC
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 287 | [9 empty] | ER | OKGE
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 17.5 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | 6 | DIS-11-1 | Coal | 900 | [9 empty] | ER | KCPL
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | CT/ST | 300 | [9 empty] | ER/NR | EMDE
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS
MPC00100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER | OTP
MPC00200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 60 | [9 empty] | ER | OTP
MPC00300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER | OTP
MPC00500 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 327.9 | [9 empty] | ER/NR | OTP
MPC00500GRE | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 51 | [9 empty] | ER/NR | GRE
MPC01200 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 49.5 | [9 empty] | ER | OTP
MPC01300 | 01 NORTH | 14.5 | DIS-15-2-PQ | Coal | 493 | [9 empty] | ER/NR | OTP
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99.25 | [9 empty] | ER | OTP
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 103.32 | [9 empty] | ER | OKGE
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 134 | [9 empty] | ER | OKGE
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 156.8 | [9 empty] | ER | AEPW
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | 16 | DIS-16-1 | Coal | 650 | [9 empty] | ER | AEPW
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 124.2 | [9 empty] | ER/NR | NPPD
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 350 | [9 empty] | ER | OKGE
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 522 | [9 empty] | ER | SPS
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 202.5 | [9 empty] | ER | OKGE
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 750 | [9 empty] | ER | AEPW
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 176.9 | [9 empty] | ER | OKGE
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW
J1846 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW
J1889 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW
J1898 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL
J2027 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE
J2031 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW
J2053 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL
J2068 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 75 | [9 empty] | ER/NR | XEL
J2078 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW
J2080 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | MP
J2087 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL
J2097 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2104 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL
J2120 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW
J2157 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 100 | [9 empty] | ER/NR | MP
J2219 | 01 NORTH | 23.5 | DIS-22-1-PQ | Battery/Storage | 180 | [9 empty] | ER/NR | DPC
J2227 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 80.1 | [9 empty] | ER/NR | DPC
J2250 | 01 NORTH | 23.5 | DIS-22-1-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
J2268 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW
J2276 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP
J2309 | 01 NORTH | 23.5 | DIS-22-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL
J1998 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 66 | [9 empty] | ER/NR | ALTW
J2122 | 02 NEBRASKA | 23.5 | DIS-22-1-PQ | Wind | 33 | [9 empty] | ER/NR | ALTW
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | 2 | ICS1 | Wind | 315 | [9 empty] | ER | OKGE
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | 8 | PQ | Wind | 165.3 | [9 empty] | ER | SPS
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | 8 | PQ | CT | 157 | [9 empty] | ER | SPS
WAPASEAMSFtRandallHydro | 02 NEBRASKA | 8 | PQ | Hydro | 360 | [9 empty] | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | 8 | PQ | Hydro | 102 | [9 empty] | ER | WAPA
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | 8 | PQ | Wind | 105.6 | [9 empty] | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 151.2 | [9 empty] | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 252.5 | [9 empty] | ER | SUNC
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | 8 | PQ | Wind | 50.72 | [9 empty] | ER | MIDW
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | 8 | PQ | Wind | 227.5 | [9 empty] | ER | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | 8 | PQ | Wind | 657.8 | [9 empty] | ER | SPS
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER/NR | NPPD
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | 25 | Surplus | Solar | 175 | [9 empty] | ER | SUNC
HAWCT_GEN-2021-SR9 | 03 CENTRAL | 23 | Surplus | Solar | 96.75 | [9 empty] | ER/NR | KCPL

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 26SP | ERIS 29SP | ERIS 29L | ERIS 29WP | NRIS 26SP | NRIS 29SP | NRIS 29L | NRIS 29WP | Stability 29SP | Stability 29WP
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 43.99 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | 43.99 | N/A | N/A | N/A | N/A | 43.99 | 43.99
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 43.99 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | 43.99 | N/A | N/A | N/A | N/A | 43.99 | 43.99
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 43.99 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 43.99 | N/A
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 43.99 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 43.99 | N/A
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 43.99 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | 0 | N/A | N/A | 43.99 | N/A | N/A | N/A | N/A | 43.99 | 43.99
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 43.99 | 0 | 532796 WICHITA7 345 532798 VIOLA 7 345 1 ftlo System Intact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | N/A | 0 | N/A | 43.99 | N/A | N/A | N/A | N/A | 43.99 | 43.99
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 43.99 | 43.99 | none | none | N/A | N/A | N/A | 43.99 | N/A | N/A | N/A | N/A | N/A | 43.99
GEN-2026-PR14 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 43.99 | 43.99 | none | none | N/A | N/A | N/A | 43.99 | N/A | N/A | N/A | N/A | N/A | 43.99

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2026-PR14 PSIS | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP, 29SP | System Intact | 829 | 829 | 110.31 | 110.63 | - | - | - | Rebuild the NEOSHO 7 to G24-240-TAP 138kV Line 1
04ALL | GEN-2026-PR14 PSIS | ERIS | Thermal | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 26SP, 29SP | System Intact | 830 | 830 | 122.01 | 122.3 | - | - | - | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
04ALL | GEN-2026-PR14 PSIS | ERIS | Thermal | None | 29WP, 29L | None | - | - | - | - | - | - | - | None
04ALL | GEN-2026-PR14 PSIS | ERIS | Voltage | None | 26SP, 29SP, 29WP, 29L | None | - | - | - | - | - | - | - | None
04ALL | GEN-2026-PR14 PSIS | ERIS | Non-Converged | None | 26SP, 29SP, 29WP, 29L | None | - | - | - | - | - | - | - | None
04ALL | GEN-2026-PR14 PSIS | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Stability | None | 29SP, 29WP | None | [7 empty] | None
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | System Intact | 829 | 829 | 103.99 | 104.35 | - | - | - | Build new VIOLA9 to WWARD9 765kV Line 1
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29SP | System Intact | 830 | 830 | 107.82 | 108.25 | - | - | - | Build new VIOLA9 to WWARD9 765kV Line 1
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29SP | System Intact | 830 | 830 | 107.78 | 108.21 | - | - | - | Build new VIOLA9 to WWARD9 765kV Line 1
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Thermal | None | 26SP, 29WP | None | - | - | - | - | - | - | - | None
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Voltage | None | 26SP, 29SP, 29WP | None | - | - | - | - | - | - | - | None
04ALL | GEN-2026-PR14 PSIS CF | ERIS | Non-Converged | None | 26SP, 29SP, 29WP | None | - | - | - | - | - | - | - | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2026-PR14 | GEN-2026-PR14 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | Contingent | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | 0 | 0% | 81488001.7662 | 0.04277
GEN-2026-PR14 | GEN-2026-PR14 PSIS | 04 SOUTHEAST | TBD | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 138kV Line 1 | Contingent | Rebuild the existing NEOSHO 7 to G24-240-TAP 138 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | 0 | 0% | 93984000 | 0.04953
GEN-2026-PR14 | GEN-2026-PR14 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Build new VIOLA9 to WWARD9 765kV Line 1 | Contingent | Build a new VIOLA9 to WWARD9 765 kV line (140.8 miles) to a standard rating of 5300 MVA | 0 | 0% | 883920000 | N/A
GEN-2026-PR14 | GEN-2026-PR14 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Build new VIOLA9 to ANTHEM9 765kV Line 1 | Contingent | Build a new VIOLA9 to ANTHEM9 765 kV line (166 miles) to a standard rating of 5300 MVA | 0 | 0% | 1044580000 | N/A
GEN-2026-PR14 | GEN-2026-PR14 PSIS CF | 04 SOUTHEAST | TBD | ERIS | Build new SEMINOLE9 to ANTHEM9 765kV Line 1 | Contingent | Build a new SEMINOLE9 to ANTHEM9 765 kV line (121.2 miles) to a standard rating of 5300 MVA | 0 | 0% | 762120000 | N/A
GEN-2026-PR14 | GEN-2026-PR14 PSIS | 04 SOUTHEAST | TBD | ERIS | Sooner - Cleveland 345 kV tap Substation GEN-2026-PR14 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR14 (43.99/Storage), on Sooner - Cleveland 345 kV tap | TBD | 100% | TBD | 1
GEN-2026-PR14 | GEN-2026-PR14 PSIS | 04 SOUTHEAST | TBD | ERIS | Sooner - Cleveland 345 kV tap Substation GEN-2026-PR13 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR14 (43.99/Storage), on Sooner - Cleveland 345 kV tap | TBD | 100% | TBD | 1
Total | [7 empty] | 0

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | GEN-2026-PR14 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1 | TBD | Rebuild the existing WICHITA7 to VIOLA 7 345 kV line 1 (37.04 miles) to a minimum rating of 1793 MVA | WERE | TBD | 81488001.7662
Contingent | GEN-2026-PR14 PSIS | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the NEOSHO 7 to G24-240-TAP 138kV Line 1 | TBD | Rebuild the existing NEOSHO 7 to G24-240-TAP 138 kV line 1 (42.72 miles) to a minimum rating of 1793 MVA | WERE/AEPW | TBD | 93984000
Contingent | GEN-2026-PR14 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Build new VIOLA9 to WWARD9 765kV Line 1 | 504291 | Build a new VIOLA9 to WWARD9 765 kV line (140.8 miles) to a standard rating of 5300 MVA | TBD | 4821400% | 883920000
Contingent | GEN-2026-PR14 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Build new VIOLA9 to ANTHEM9 765kV Line 1 | 504296 | Build a new VIOLA9 to ANTHEM9 765 kV line (166 miles) to a standard rating of 5300 MVA | TBD | 4821400% | 1044580000
Contingent | GEN-2026-PR14 PSIS CF | Steady State | 04 SOUTHEAST | 2025 ITP | ERIS | Build new SEMINOLE9 to ANTHEM9 765kV Line 1 | 504162 | Build a new SEMINOLE9 to ANTHEM9 765 kV line (121.2 miles) to a standard rating of 5300 MVA | TBD | 4821400% | 762120000
Interconnection | GEN-2026-PR14 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR14 PSIS | ERIS | Sooner - Cleveland 345 kV tap Substation GEN-2026-PR14 Interconnection (TOIF) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR14 (43.99/Storage), on Sooner - Cleveland 345 kV tap | OKGE | TBD | TBD
Interconnection | GEN-2026-PR14 PSIS | Steady State | 04 SOUTHEAST | GEN-2026-PR14 PSIS | ERIS | Sooner - Cleveland 345 kV tap Substation GEN-2026-PR13 Interconnection (Non-Shared NU) (OGE) | TBD | Interconnection upgrades and cost estimates needed to interconnect GEN-2026-PR14 (43.99/Storage), on Sooner - Cleveland 345 kV tap | OKGE | TBD | TBD
2866092001.7662

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 29L and 29SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504180 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem 765 kV Reactor | Install 150 MVAR reactor at Anthem 765 kV substation | 2025 ITP | Yes | N/A | 0.1074 | 4821400% | 15000000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504182 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 765 kV Reactor | Install 150 MVAR reactor at Minco 765 kV substation | 2025 ITP | Yes | N/A | -0.03007 | 4821400% | 15000000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504257 | Line - Seminole - Southwest Shreveport 765 kV | Seminole 765 kV Reactor | Install 150 MVAR reactor at Seminole 765 kV substation | 2025 ITP | Yes | N/A | -0.0562 | 4780500% | 15000000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504243 | Line - Woodward - Crawfish Draw 765 kV New Line | Woodward 765 kV Reactor | Install 375 MVAR reactor at Woodward 765 kV substation | 2025 ITP | Yes | N/A | 0.03041 | 4821400% | 30000000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504247 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Potter Co 765 kV Reactor | Install 225 MVAR reactor at Potter Co 765 kV substation | 2025 ITP | Yes | N/A | 0.03041 | 4821400% | 22500000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504223 | Line - Crawfish Draw - Phantom 765 kV New Line | Crawfish Draw 765 kV Reactor | Install 375 MVAR reactor at Crawfish Draw 765 kV substation | 2025 ITP | Yes | N/A | 0.03616 | 4780500% | 12271304.934
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504302 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Viola 765 kV Reactor | Install 150 MVAR reactor at Viola 765 kV substation | 2025 ITP | Yes | N/A | 0.03635 | 4821400% | 266653225
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504184 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Anthem | 2025 ITP | Yes | N/A | -0.03389 | 4821400% | 61500000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504188 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 2 Transformer | Install new 345/765 kV Ckt 2 transformer at Anthem | 2025 ITP | Yes | N/A | -0.03389 | 4821400% | 61500000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504191 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem 345/765 kV Ckt 3 Transformer | Install new 345/765 kV Ckt 3 transformer at Anthem | 2025 ITP | Yes | N/A | -0.03389 | 4821400% | 61500000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504162 | Multi - Anthem – Seminole 765 kV New Line, Anthem 345/138 kV New Transformer | Anthem - Seminole 765 kV Ckt 1 New Line | Build a 131.3-mile 765 kV Ckt 1 line from Anthem to Seminole | 2025 ITP | Yes | N/A | -0.0562 | 4821400% | 762120000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504296 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Anthem - Viola 765 kV Ckt 1 New Line | Build a 166-mile 765 kV Ckt 1 line from Anthem to Viola | 2025 ITP | Yes | N/A | -0.04546 | 4821400% | 1044580000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504194 | Minco - Seminole 765 kV New Line Minco - Crawfish Draw 765 kV New Line Minco 765 kV New Substation Minco 765 kV New Reactor Minco 345/765 kV New Transformer | Minco 345/765 kV Ckt 1 Transformer | Install new 345/765 kV Ckt 1 transformer at Minco | 2025 ITP | Yes | N/A | 0.03616 | 4821400% | 61500000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504237 | Woodward - Potter Co 765 kV New Line Woodward 765 kV New Reactor Woodward 345 kV New Reactor Potter Co 765 kV New Reactor | Woodward - Potter Co 765 kV Ckt 1 New Line | Build a 208-mile 765 kV Ckt 1 line from Woodward to Potter Co | 2025 ITP | Yes | N/A | 0.03041 | 4821400% | 1200600000
GEN-2026-PR14 | 04 SOUTHEAST | ER | TBD | 504291 | Woodward - Viola 765 kV New Line Anthem - Viola 765 kV New Line Viola 765 kV New Substation Anthem 765 kV New Reactor Viola 765 kV New Reactor Woodward 765 kV New Reactor Viola 345/765 kV New Transformer | Woodward - Viola 765 kV Ckt 1 New Line | Build a 140.8-mile 765 kV Ckt 1 line from Woodward to Viola | 2025 ITP | Yes | N/A | -0.05389 | 4821400% | 883920000

## JTIQ Screening Summary
Gen Number | Group | Meet JTIQ Facility Screening Criteria? | Meet MISO Facility Screening Criteria? | Screen into JTIQ Participant Group
GEN-2026-PR14 | 04 SOUTHEAST | No | No | No

## JTIQ Facility Screening Results
Gen Number | Group | Model | Project Name | Monitored Facility | PTDF | MW Impact | Meet JTIQ Facility Screening Criteria?
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1 | 0.00113 | 0.049709 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 783480 G24-217-TAP 345 1 | -0.00318 | -0.13989 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635200 RAUN 3 345 645552 S3452 REACT3 345 1 | -0.00195 | -0.08578 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645552 S3452 REACT3 345 Z1 | -0.00195 | -0.08578 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645459 S3459 3 345 1 | -0.00135 | -0.059387 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640139 COOPER 3 345 640601 S3771 345 1 | 0.00459 | 0.20191 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 532765 HOYT 7 345 640601 S3771 345 1 | 0.00557 | 0.24502 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541201 SIBLEY 7 345 996707 SIBLEY11 161 11 | -0.00033 | -0.014517 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541202 SIBLEY 5 161 996707 SIBLEY11 161 11 | -0.00033 | -0.014517 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 2 | 0.0009 | 0.039591 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645451 S3451 3 345 645452 S3452 3 345 1 | 0.00087 | 0.038271 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 645452 S3452 3 345 645454 S3454 3 345 1 | 0.00238 | 0.1047 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 0.00486 | 0.21379 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 635201 RAUN 5 161 646300 S1300 5 161 1 | -0.00057 | -0.025074 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | -0.00057 | -0.025074 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Sibley - 345 kV Bus Reconfiguration | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | -0.00724 | -0.31849 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Auburn – Hoyt 345 kV | 640590 OLIVECREEK 3 345 640601 S3771 345 1 | 0.00099 | 0.04355 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646226 S1226 5 161 646247 S1247 5 161 1 | 0.00029 | 0.012757 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 646247 S1247 5 161 646252 S1252 5 161 1 | 0.00029 | 0.012757 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Lyons Co.– Lakefield 345 kV | 601048 LYON CO 3 345 631138 LAKEFLD3 345 1 | 0.00035 | 0.015397 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Raun – S3452 345 kV | 640377 TEKAMAH5 161 646226 S1226 5 161 1 | 0.00055 | 0.024195 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 601067 BISON 3 345 620427 HANKINSON 3 345 1 | 0.00018 | 0.0079182 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620417 BSSOUTH3 345 620427 HANKINSON 3 345 1 | 0.00021 | 0.0092379 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996398 620:HANKINSO 230 2 | 1e-05 | 0.0004399 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620327 HANKSON4 230 996399 620:HANKINSO 230 1 | 1e-05 | 0.0004399 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996398 620:HANKINSO 230 2 | 1e-05 | 0.0004399 | No
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | Bison – Hankinson – Big Stone South 345 kV | 620427 HANKINSON 3 345 996399 620:HANKINSO 230 1 | 1e-05 | 0.0004399 | No

## MISO Facility Screening Results
Gen Number | Group | Model | Monitored Facility | CON Name | TDF
GEN-2026-PR14 | 04 SOUTHEAST | G04 29SP | None | None | N/A

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2026-PR14 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR14 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.04445 | 109.98 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR14 PSIS | 04ALL | 1 | 26SP | GEN-2026-PR14 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.05 | 101.98 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 138kV Line 1
Thermal | GEN-2026-PR14 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR14 | TO->FROM | 532796 WICHITA7 345 532798 VIOLA 7 345 1 | 830 | 830 | 0.04175 | 122.3 | System Intact | TDF Impact | Rebuild the WICHITA7 to VIOLA 7 345kV Line 1
Thermal | GEN-2026-PR14 PSIS | 04ALL | 1 | 29SP | GEN-2026-PR14 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.04873 | 110.63 | System Intact | TDF Impact | Rebuild the NEOSHO 7 to G24-240-TAP 138kV Line 1
Non-Converged | GEN-2026-PR14 PSIS | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR14 PSIS | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR14 PSIS | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR14 PSIS | 04ALL | 0 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR14 PSIS | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR14 PSIS | 04ALL | 1 | 29L | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.06704 | 108.25 | System Intact | TDF Impact | Build new VIOLA9 to WWARD9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.06704 | 108.21 | System Intact | TDF Impact | Build new VIOLA9 to WWARD9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.05301 | 104.35 | System Intact | TDF Impact | Build new VIOLA9 to WWARD9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.06704 | 108.25 | System Intact | TDF Impact | Build new VIOLA9 to ANTHEM9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.06704 | 108.21 | System Intact | TDF Impact | Build new VIOLA9 to ANTHEM9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.05301 | 104.35 | System Intact | TDF Impact | Build new VIOLA9 to ANTHEM9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.06704 | 108.25 | System Intact | TDF Impact | Build new SEMINOLE9 to ANTHEM9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 830 | 830 | 0.06704 | 108.21 | System Intact | TDF Impact | Build new SEMINOLE9 to ANTHEM9 765kV Line 1
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29SP | GEN-2026-PR14 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 829 | 829 | 0.05301 | 104.35 | System Intact | TDF Impact | Build new SEMINOLE9 to ANTHEM9 765kV Line 1
Non-Converged | GEN-2026-PR14 PSIS CF | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR14 PSIS CF | 04ALL | 0 | 29SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2026-PR14 PSIS CF | 04ALL | 0 | 29WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2026-PR14 PSIS CF | 04ALL | 1 | 29WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2026-PR14 PSIS | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR14 PSIS | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR14 PSIS | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR14 PSIS | 04ALL | 2 | 29L | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR14 PSIS CF | 04ALL | 2 | 26SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR14 PSIS CF | 04ALL | 2 | 29SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2026-PR14 PSIS CF | 04ALL | 2 | 29WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Simulation crashes following the fault. After reducing the fault clearing time to 1.5 cycles, the simulation completed successfully, and an oscillatory response was observed in the active power outputs of units G24-334 (786994, 786997), WCGS (532751), and G17-141 (760412). This behavior is also present in the base case, and the CQ units were not found to have any impact on the observed oscillations. | Reduce clearing time to 1.5 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COLINS 5 161.00 (512627) 161 kV Bus a. Apply fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.7. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.8. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW (300137) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW (300137) 138.0 kV to 4WOODY (300686) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX (300139) 138.0 kV to 4REMNGTON (301369) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY (300140) 138.0 kV to 4STILWTR (300141) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to 4RAMSEY (300844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on 2SILVCTY 69.000 (300943) 69 kV Bus a. Apply fault at the 2SILVCTY 69.000 (300943) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 2SILVCTYLD (301630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on 2SILVCTY 69.000 (300943) 69 kV Bus a. Apply fault at the 2SILVCTY 69.000 (300943) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 2SILVCTYTP (301631) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on 2SFORKK 69.000 (300948) 69 kV Bus a. Apply fault at the 2SFORKK 69.000 (300948) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to 2TALLANT (301005) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on CIP 4 138.00 (509714) 138 kV Bus a. Apply fault at the CIP 4 138.00 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 (509714) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on OWASO1_4 138.00 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 138.00 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 (509726) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on DENVR-E4 138.00 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 138.00 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 (509743) 138.0 kV to DENVTAP4 (509746) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to W.ED.-E4 (509822) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in G10-055 (560391). The issue is observed in PQ case. | Remove reclosing solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WED-TAP4 (509823) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in G10-055 (560391). The issue is observed in PQ case. | Remove reclosing and reduce clearing time to 4 cycles solve the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Rotor angle violations is identified in G10-055 (560391). The issue is observed in PQ case. | Remove reclosing and reduce clearing time to 4 cycles solve the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on A.A.---4 138.00 (509784) 138 kV Bus a. Apply fault at the A.A.---4 138.00 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 (509784) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on PP----W4 138.00 (509805) 138 kV Bus a. Apply fault at the PP----W4 138.00 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 (509805) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to TNOXF2 (760152) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on 46ST--E4 138.00 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 138.00 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 (509837) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WHIRLPO4 138.00 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 138.00 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 (509840) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on OWASO2_4 138.00 (509843) 138 kV Bus a. Apply fault at the OWASO2_4 138.00 (509843) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on OWASOTP4 138.00 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 138.00 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASOTP4 (509844) 138.0 kV to OWAS1094 (509860) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on VERDIGS4 138.00 (509854) 138 kV Bus a. Apply fault at the VERDIGS4 138.00 (509854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDIGS4 (509854) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on OWAS1094 138.00 (509860) 138 kV Bus a. Apply fault at the OWAS1094 138.00 (509860) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 (509860) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on PPTAP 4 138.00 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 138.00 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 (509863) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on WATOVA 4 138.00 (510384) 138 kV Bus a. Apply fault at the WATOVA 4 138.00 (510384) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 (510384) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on RICE CK4 138.00 (510385) 138 kV Bus a. Apply fault at the RICE CK4 138.00 (510385) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE CK4 (510385) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on N.E.S.-4 138.00 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 138.00 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to OOLOGAH 4 (513124) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on N.E.S.-7 345.00 (510406) 345 kV Bus a. Apply fault at the N.E.S.-7 345.00 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on PAWNEGR2 69.000 (512675) 69 kV Bus a. Apply fault at the PAWNEGR2 69.000 (512675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEGR2 (512675) 69.0 kV to HALLETTAP 2 (513098) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on CLEVDSTK2 69.000 (512877) 69 kV Bus a. Apply fault at the CLEVDSTK2 69.000 (512877) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVDSTK2 (512877) 69.0 kV to HALLETTAP 2 (513098) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Simulation crashes following the fault. After reducing the fault clearing time to 2 cycles, the simulation completed successfully, and an oscillatory response was observed in the active power outputs of units G24-334 (786994, 786997), WCGS (532751), and G17-141 (760412). This behavior is also present in the base case, and the CQ units were not found to have any impact on the observed oscillations. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on G21-047-TAP 345.00 (765721) 345 kV Bus a. Apply fault at the G21-047-TAP 345.00 (765721) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G21-047-TAP (765721) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW (300889) 69.0 kV to 4BRISTOW (300137) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRFAX (300929) 69.0 kV to 4FAIRFAX (300139) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRFAX (300929) 69.0 kV to 4FAIRFAX (300139) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 4SILVCTY (300140) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 4SILVCTY (300140) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO (301413) 69.0 kV to 4STILWTR (300141) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO (301413) 69.0 kV to 4STILWTR (300141) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on 4SFORKK 138.00 (300165) 138 kV Bus a. Apply fault at the 4SFORKK 138.00 (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to 4SFORKK (300165) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to TNOXF2 (760152) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997), OMCDLEC1 (529201) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 2 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 4 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Simulation crashes following the fault. After reducing the fault clearing time to 1.5 cycles, the simulation completed successfully, and an oscillatory response was observed in the active power outputs of units G24-334 (786994, 786997) and G17-141 (760412). This behavior is also present in the base case, and the CQ units were not found to have any impact on the observed oscillations. | Reduce clearing time to 1.5 cycles solves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G18-115 (763321, 763324) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-4 (509757) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-4 (509757) 138.0 kV to SHEFFD-4 (509812) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.3. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.3. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.6. OSAGE 4 (514743) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STDBEAR4 138.00 (514758) 138 kV Bus a. Apply Fault at the STDBEAR4 138.00 (514758) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.2. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on STILWTR4 138.00 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to STILWTR4 (515011) 138.0 kV Transmission Circuit #1 b.2. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. STILWTR4 (515011) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply Fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 b.3. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.4. KEYSTON4 (505610) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KEYSTON5 161.00 (505609) 161 kV Bus a. Apply Fault at the KEYSTON5 161.00 (505609) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 b.3. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.4. KEY1&2 1 (505612) 13.8 kV to KEYSTON5 (505609) 161.0 kV to KEYSTON4 (505610) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.5. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.6. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 2SFORKK (300948) 69.0 kV to 4SFORKK (300165) 138.0 kV Two Winding #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.8. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.9. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.11. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER1G (514805) 22.0 kV Two Winding #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-066T (515975) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply Fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply Fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4BRISTOW (300137) 138.0 kV to 4WOODY (300686) 138.0 kV Transmission Circuit #1 b.2. 4BRISTOW (300137) 138.0 kV to 2BRIISTOW (300889) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips R26FRMRCTYW1 (635020) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to CLEVLND 4 (512729) 138.0 kV Transmission Circuit #z1 b.2. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply Fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FAIRFAX (300139) 138.0 kV to 4REMNGTON (301369) 138.0 kV Transmission Circuit #1 b.2. 4FAIRFAX (300139) 138.0 kV to 2FAIRFAX (300929) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4SILVCTY (300140) 138.0 kV to 4STILWTR (300141) 138.0 kV Transmission Circuit #1 b.2. 4SILVCTY (300140) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLEVLND (300927) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.2. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on 4JAVINE 138.00 (300996) 138 kV Bus a. Apply Fault at the 4JAVINE 138.00 (300996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to TNOXF2 (760152) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-028 (762639) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply Fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 b.2. ANTHEM7 (509915) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply Fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on N.E.S.-7 345.00 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 345.00 (510406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.E.S.-7 (510406) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips R26FRMRCTYW1 (635020) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNSW4 (512749) 138.0 kV to 4CLEVLND (300138) 138.0 kV Transmission Circuit #1 b.2. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G23-057 (773124) unit. | Protection disabled with no impact to stability.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on MILLERT4 138.00 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to WEBBTAP4 (510376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to CONTEMP4 (514748) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MORRISN4 138.00 (515006) 138 kV Bus a. Apply Fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on STILWTR4 138.00 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.2. STILWTR4 (515011) 138.0 kV to MCELROY4 (515009) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on THUNDER7 345.00 (515894) 345 kV Bus a. Apply Fault at the THUNDER7 345.00 (515894) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THUNDER7 (515894) 345.0 kV to GEN-2021-018 (765470) 345.0 kV Transmission Circuit #1 b.2. THUNDER7 (515894) 345.0 kV to GEN-2021-019 (765480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on GEN-2015-066345.00 (515974) 345 kV Bus a. Apply Fault at the GEN-2015-066345.00 (515974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-066 (515974) 345.0 kV to G15-066XFMR1 (515972) 34.5 kV Two Winding #1 b.2. GEN-2015-066 (515974) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G15-066T 345.00 (515975) 345 kV Bus a. Apply Fault at the G15-066T 345.00 (515975) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-066T (515975) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. G15-066T (515975) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on G24-171-TAP 345.00 (782100) 345 kV Bus a. Apply Fault at the G24-171-TAP 345.00 (782100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-171-TAP (782100) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. G24-171-TAP (782100) 345.0 kV to ANTHEM7 (509915) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on G24-235-TAP 345.00 (784020) 345 kV Bus a. Apply Fault at the G24-235-TAP 345.00 (784020) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-235-TAP (784020) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 b.2. G24-235-TAP (784020) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on GADWALL7 (516207) 345 kV Bus a. Apply Fault at the GADWALL7 (516207) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GADWALL7 (516207) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on THUNDER7 (515894) 345 kV Bus a. Apply Fault at the THUNDER7 (515894) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THUNDER7 (515894) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) and WCGS (532751) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_GRDA_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_GRDA_FAULT_004 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_GRDA_FAULT_005 | Single Phase Fault with Stuck Breaker on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. COLLIN1 1 (512838) 13.8 kV to remove bus # b.2. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.3. OSAGEK2 (512876) 69.0 kV to CLEVDSTK2 (512877) 69.0 kV Transmission Circuit #1 b.4. 4SFORKK (300165) 138.0 kV to remove bus # b.5. 4SFORKKTP (301339) 138.0 kV to remove bus # b.6. 4JAVINE (300996) 138.0 kV to remove bus # b.7. 4SKIAETP (300146) 138.0 kV to remove bus # b.8. SKIAEAS4 (512649) 138.0 kV to remove bus # b.9. COLLINS4 (512705) 138.0 kV to remove bus # b.10. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.11. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.12. 4CLEVLND (300138) 138.0 kV to 2CLEVLND (300927) 69.0 kV Two Winding #1 b.13. 4CLEVLND (300138) 138.0 kV to 2CLEVLND (300927) 69.0 kV Two Winding #2 b.14. PARKMEDTP (512703) 69.0 kV to remove bus # b.15. 2PARKMDWS (301999) 69.0 kV to remove bus # b.16. SKIATTP2 (512871) 69.0 kV to remove bus # b.17. SKIATOK2 (512872) 69.0 kV to remove bus # b.18. SKIATCTY2 (512873) 69.0 kV to remove bus # b.19. GREENTP2 (512874) 69.0 kV to remove bus # b.20. 2GREEN (300994) 69.0 kV to remove bus # b.21. PRUEK2 (512875) 69.0 kV to remove bus # b.22. OSAGEK2 (512876) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWIND7 (514825) 345.0 kV to remove bus # b.6. KAYWNDT1 (515619) 12.5 kV to remove bus # b.7. KAYWNDT2 (515620) 12.5 kV to remove bus # b.8. OPENSKY7 (515621) 345.0 kV to remove bus # b.9. KAYWND11 (515622) 34.5 kV to remove bus # b.10. KAYWND12 (515623) 34.5 kV to remove bus # b.11. KAYWNDG1 (515651) 0.7 kV to remove bus # b.12. KAYWNDG2 (515652) 0.7 kV to remove bus # b.13. KAYWNDC1 (515653) 34.5 kV to remove bus # b.14. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to remove bus # b.5. FRNTWD11 (515689) 34.5 kV to remove bus # b.6. FRNTWDC1 (515690) 34.5 kV to remove bus # b.7. FRNTWDG1 (515691) 0.6 kV to remove bus # b.8. FRNTWDT1 (515692) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_R3_FAULT_001 | Single Phase Fault with Stuck Breaker on Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.3. ONETA--7 (509807) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.4. ONETA--7 (509807) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.5. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.6. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.7. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 b.8. ONETA--4 (509806) 138.0 kV to BA101-N4 (509769) 138.0 kV Transmission Circuit #1 b.9. ONETA--4 (509806) 138.0 kV to BA.N-ST4 (509786) 138.0 kV Transmission Circuit #1 b.10. OECSTM 1 (511938) 18.0 kV to Generator #1 b.11. OECGT1-1 (511939) 18.0 kV to Generator #1 b.12. OECGT1-2 (511940) 18.0 kV to Generator #1 b.13. OECSTM 2 (511941) 18.0 kV to Generator #1 b.14. OECGT2-1 (511942) 18.0 kV to Generator #1 b.15. OECGT2-2 (511943) 18.0 kV to Generator #1 b.16. ONETA--4 (509806) 138.0 kV to remove bus # b.17. ONETA--7 (509807) 345.0 kV to remove bus # b.18. OEC 7 (509836) 345.0 kV to remove bus # b.19. ONETA2-1 (509868) 34.5 kV to remove bus # b.20. ONETA5-1 (509874) 34.5 kV to remove bus # b.21. ONETA1-1 (509881) 13.8 kV to remove bus # b.22. OECSTM 1 (511938) 18.0 kV to remove bus # b.23. OECGT1-1 (511939) 18.0 kV to remove bus # b.24. OECGT1-2 (511940) 18.0 kV to remove bus # b.25. OECSTM 2 (511941) 18.0 kV to remove bus # b.26. OECGT2-1 (511942) 18.0 kV to remove bus # b.27. OECGT2-2 (511943) 18.0 kV to remove bus # b.28. ONETA--4 (509806) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_R3_FAULT_002 | Single Phase Fault with Stuck Breaker on Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. CDC-WT 4 (509842) 138.0 kV to A.A.---4 (509784) 138.0 kV Transmission Circuit #1 b.2. PPTAP 4 (509863) 138.0 kV to MOHAWK 4 (509801) 138.0 kV Transmission Circuit #1 b.3. OWASOTP4 (509844) 138.0 kV to OWAS1094 (509860) 138.0 kV Transmission Circuit #1 b.4. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.5. CDC-ET 4 (509839) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit #1 b.6. P&P WTP4 (509851) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 b.7. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 b.8. SKIATOK4 (509884) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 b.9. CIP 4 (509714) 138.0 kV to remove bus # b.10. CDC 4 (509715) 138.0 kV to remove bus # b.11. OWASO1_4 (509726) 138.0 kV to remove bus # b.12. DENVR-E4 (509743) 138.0 kV to remove bus # b.13. DENVTAP4 (509746) 138.0 kV to remove bus # b.14. PP----W4 (509805) 138.0 kV to remove bus # b.15. T.NO.--4 (509817) 138.0 kV to remove bus # b.16. PP----E4 (509818) 138.0 kV to remove bus # b.17. W.ED.-E4 (509822) 138.0 kV to remove bus # b.18. YARCH-N4 (509825) 138.0 kV to remove bus # b.19. 46ST--E4 (509837) 138.0 kV to remove bus # b.20. CDC-ET 4 (509839) 138.0 kV to remove bus # b.21. WHIRLPO4 (509840) 138.0 kV to remove bus # b.22. CDC-WT 4 (509842) 138.0 kV to remove bus # b.23. OWASOTP4 (509844) 138.0 kV to remove bus # b.24. P&P WTP4 (509851) 138.0 kV to remove bus # b.25. YARCHT 4 (509862) 138.0 kV to remove bus # b.26. PPTAP 4 (509863) 138.0 kV to remove bus # b.27. SKIATOK4 (509884) 138.0 kV to remove bus # b.28. 46ST-TP-4 (509900) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-079-TAP (763113) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.5. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRVR_GEN 1 0.6900 (523050) 0.689999998 kV Bus a. Apply Fault at the GRVR_GEN 1 0.6900 (523050) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G24-334 (786994, 786997) units. The issue was also observed in the base case and CQ unit were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on SILVCTYGR4 138.00 (512726) 138 kV Bus a. Apply fault at the SILVCTYGR4 138.00 (512726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY (300140) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on SKIATKTP4 138.00 (509908) 138 kV Bus a. Apply fault at the SKIATKTP4 138.00 (509908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to SKIATKTP4 (509908) 138.0 kV Transmission Circuit #1 b.2. SKIATOK4 (509884) 138.0 kV to SKIATKTP4 (509908) 138.0 kV Transmission Circuit #1 b.3. SKIATKTP4 (509908) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CDC-ET 4 138.00 (509839) 138 kV Bus a. Apply fault at the CDC-ET 4 138.00 (509839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDC-ET 4 (509839) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on HAWTHRN4 138.00 (510413) 138 kV Bus a. Apply fault at the HAWTHRN4 138.00 (510413) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.2. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.4. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to SHEFFD-4 (509812) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on KEYSTON4 138.00 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 138.00 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 (505610) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to CLEVLND 4 (512729) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to NORTHTP4 (512731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on GLENCO 4 138.00 (513095) 138 kV Bus a. Apply fault at the GLENCO 4 138.00 (513095) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.2. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on 2MANFORD 69.000 (300936) 69 kV Bus a. Apply fault at the 2MANFORD 69.000 (300936) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CEDARPT (300923) 69.0 kV to MANFORD2 (512641) 69.0 kV Transmission Circuit #1 b.2. 2FISHER (300931) 69.0 kV to 2MANFORD (300936) 69.0 kV Transmission Circuit #1 b.3. 2MANFORD (300936) 69.0 kV to 2SILVCTY (300943) 69.0 kV Transmission Circuit #1 b.4. 2MANFORD (300936) 69.0 kV to MANFORD2 (512641) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on OSAGEK2 69.000 (512876) 69 kV Bus a. Apply fault at the OSAGEK2 69.000 (512876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.2. 2GREEN (300994) 69.0 kV to GREENTP2 (512874) 69.0 kV Transmission Circuit #1 b.3. 2PARKMDWS (301999) 69.0 kV to PARKMEDTP (512703) 69.0 kV Transmission Circuit #1 b.4. PARKMEDTP (512703) 69.0 kV to COLNSGR2 (512870) 69.0 kV Transmission Circuit #1 b.5. PARKMEDTP (512703) 69.0 kV to SKIATTP2 (512871) 69.0 kV Transmission Circuit #1 b.6. SKIATTP2 (512871) 69.0 kV to SKIATOK2 (512872) 69.0 kV Transmission Circuit #1 b.7. SKIATTP2 (512871) 69.0 kV to GREENTP2 (512874) 69.0 kV Transmission Circuit #1 b.8. SKIATOK2 (512872) 69.0 kV to SKIATCTY2 (512873) 69.0 kV Transmission Circuit #1 b.9. GREENTP2 (512874) 69.0 kV to PRUEK2 (512875) 69.0 kV Transmission Circuit #1 b.10. PRUEK2 (512875) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.11. OSAGEK2 (512876) 69.0 kV to CLEVDSTK2 (512877) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on RAMONA 2 69.000 (510392) 69 kV Bus a. Apply fault at the RAMONA 2 69.000 (510392) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to RAMONA 2 (510392) 69.0 kV Transmission Circuit #1 b.2. 2RAMONA K (301000) 69.0 kV to 2VERA (301006) 69.0 kV Transmission Circuit #1 b.3. 2RAMONA K (301000) 69.0 kV to 2WMARTTP (301471) 69.0 kV Transmission Circuit #1 b.4. 2VERA (301006) 69.0 kV to COLNSGR2 (512870) 69.0 kV Transmission Circuit #1 b.5. 2WMARTTP (301471) 69.0 kV to WALMART2 (510436) 69.0 kV Transmission Circuit #1 b.6. RAMONA 2 (510392) 69.0 kV to WALMART2 (510436) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.3. WEBBTAP4 (510376) 138.0 kV to SHIDWFC4 (520442) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on OTOETAP4 138.00 (515978) 138 kV Bus a. Apply fault at the OTOETAP4 138.00 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.3. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.5. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.6. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.3. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.4. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 b.5. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.3. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on OMWW 69.000 (529249) 69 kV Bus a. Apply fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.3. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to CONORTH4 (514753) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on CONORTH4 138.00 (514753) 138 kV Bus a. Apply fault at the CONORTH4 138.00 (514753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on MCELROY4 138.00 (515009) 138 kV Bus a. Apply fault at the MCELROY4 138.00 (515009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCELROY4 (515009) 138.0 kV to STILWTR4 (515011) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on STILWTR4 138.00 (515011) 138 kV Bus a. Apply fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 (515011) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COLINS 5 161.00 (512627) 161 kV Bus a. Apply fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.7. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.8. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW (300137) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW (300137) 138.0 kV to 4WOODY (300686) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX (300139) 138.0 kV to 4REMNGTON (301369) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY (300140) 138.0 kV to 4STILWTR (300141) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to 4RAMSEY (300844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on 2SILVCTY 69.000 (300943) 69 kV Bus a. Apply fault at the 2SILVCTY 69.000 (300943) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 2SILVCTYLD (301630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on 2SILVCTY 69.000 (300943) 69 kV Bus a. Apply fault at the 2SILVCTY 69.000 (300943) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 2SILVCTYTP (301631) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on 2SFORKK 69.000 (300948) 69 kV Bus a. Apply fault at the 2SFORKK 69.000 (300948) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to 2TALLANT (301005) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on CIP 4 138.00 (509714) 138 kV Bus a. Apply fault at the CIP 4 138.00 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 (509714) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on OWASO1_4 138.00 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 138.00 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 (509726) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on DENVR-E4 138.00 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 138.00 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 (509743) 138.0 kV to DENVTAP4 (509746) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to W.ED.-E4 (509822) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WED-TAP4 (509823) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on A.A.---4 138.00 (509784) 138 kV Bus a. Apply fault at the A.A.---4 138.00 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 (509784) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on PP----W4 138.00 (509805) 138 kV Bus a. Apply fault at the PP----W4 138.00 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 (509805) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to TNOXF2 (760152) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on 46ST--E4 138.00 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 138.00 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 (509837) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WHIRLPO4 138.00 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 138.00 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 (509840) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on OWASO2_4 138.00 (509843) 138 kV Bus a. Apply fault at the OWASO2_4 138.00 (509843) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on OWASOTP4 138.00 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 138.00 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASOTP4 (509844) 138.0 kV to OWAS1094 (509860) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on VERDIGS4 138.00 (509854) 138 kV Bus a. Apply fault at the VERDIGS4 138.00 (509854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDIGS4 (509854) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on OWAS1094 138.00 (509860) 138 kV Bus a. Apply fault at the OWAS1094 138.00 (509860) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 (509860) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on PPTAP 4 138.00 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 138.00 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 (509863) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on WATOVA 4 138.00 (510384) 138 kV Bus a. Apply fault at the WATOVA 4 138.00 (510384) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 (510384) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on RICE CK4 138.00 (510385) 138 kV Bus a. Apply fault at the RICE CK4 138.00 (510385) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE CK4 (510385) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on N.E.S.-4 138.00 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 138.00 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to OOLOGAH 4 (513124) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on N.E.S.-7 345.00 (510406) 345 kV Bus a. Apply fault at the N.E.S.-7 345.00 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on PAWNEGR2 69.000 (512675) 69 kV Bus a. Apply fault at the PAWNEGR2 69.000 (512675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEGR2 (512675) 69.0 kV to HALLETTAP 2 (513098) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on CLEVDSTK2 69.000 (512877) 69 kV Bus a. Apply fault at the CLEVDSTK2 69.000 (512877) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVDSTK2 (512877) 69.0 kV to HALLETTAP 2 (513098) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on G21-047-TAP 345.00 (765721) 345 kV Bus a. Apply fault at the G21-047-TAP 345.00 (765721) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G21-047-TAP (765721) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW (300889) 69.0 kV to 4BRISTOW (300137) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRFAX (300929) 69.0 kV to 4FAIRFAX (300139) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRFAX (300929) 69.0 kV to 4FAIRFAX (300139) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 4SILVCTY (300140) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 4SILVCTY (300140) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO (301413) 69.0 kV to 4STILWTR (300141) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO (301413) 69.0 kV to 4STILWTR (300141) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on 4SFORKK 138.00 (300165) 138 kV Bus a. Apply fault at the 4SFORKK 138.00 (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to 4SFORKK (300165) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to TNOXF2 (760152) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-4 (509757) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-4 (509757) 138.0 kV to SHEFFD-4 (509812) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.3. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.3. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.6. OSAGE 4 (514743) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STDBEAR4 138.00 (514758) 138 kV Bus a. Apply Fault at the STDBEAR4 138.00 (514758) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.2. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on STILWTR4 138.00 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to STILWTR4 (515011) 138.0 kV Transmission Circuit #1 b.2. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. STILWTR4 (515011) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply Fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 b.3. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.4. KEYSTON4 (505610) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KEYSTON5 161.00 (505609) 161 kV Bus a. Apply Fault at the KEYSTON5 161.00 (505609) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 b.3. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.4. KEY1&2 1 (505612) 13.8 kV to KEYSTON5 (505609) 161.0 kV to KEYSTON4 (505610) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.5. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.6. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 2SFORKK (300948) 69.0 kV to 4SFORKK (300165) 138.0 kV Two Winding #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.8. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.9. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.11. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER1G (514805) 22.0 kV Two Winding #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-066T (515975) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply Fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply Fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4BRISTOW (300137) 138.0 kV to 4WOODY (300686) 138.0 kV Transmission Circuit #1 b.2. 4BRISTOW (300137) 138.0 kV to 2BRIISTOW (300889) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to CLEVLND 4 (512729) 138.0 kV Transmission Circuit #z1 b.2. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply Fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FAIRFAX (300139) 138.0 kV to 4REMNGTON (301369) 138.0 kV Transmission Circuit #1 b.2. 4FAIRFAX (300139) 138.0 kV to 2FAIRFAX (300929) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4SILVCTY (300140) 138.0 kV to 4STILWTR (300141) 138.0 kV Transmission Circuit #1 b.2. 4SILVCTY (300140) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLEVLND (300927) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.2. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on 4JAVINE 138.00 (300996) 138 kV Bus a. Apply Fault at the 4JAVINE 138.00 (300996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to TNOXF2 (760152) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply Fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 b.2. ANTHEM7 (509915) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply Fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on N.E.S.-7 345.00 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 345.00 (510406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.E.S.-7 (510406) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNSW4 (512749) 138.0 kV to 4CLEVLND (300138) 138.0 kV Transmission Circuit #1 b.2. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on MILLERT4 138.00 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to WEBBTAP4 (510376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to CONTEMP4 (514748) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MORRISN4 138.00 (515006) 138 kV Bus a. Apply Fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on STILWTR4 138.00 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.2. STILWTR4 (515011) 138.0 kV to MCELROY4 (515009) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on THUNDER7 345.00 (515894) 345 kV Bus a. Apply Fault at the THUNDER7 345.00 (515894) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THUNDER7 (515894) 345.0 kV to GEN-2021-018 (765470) 345.0 kV Transmission Circuit #1 b.2. THUNDER7 (515894) 345.0 kV to GEN-2021-019 (765480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on GEN-2015-066345.00 (515974) 345 kV Bus a. Apply Fault at the GEN-2015-066345.00 (515974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-066 (515974) 345.0 kV to G15-066XFMR1 (515972) 34.5 kV Two Winding #1 b.2. GEN-2015-066 (515974) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G15-066T 345.00 (515975) 345 kV Bus a. Apply Fault at the G15-066T 345.00 (515975) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-066T (515975) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. G15-066T (515975) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on G24-171-TAP 345.00 (782100) 345 kV Bus a. Apply Fault at the G24-171-TAP 345.00 (782100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-171-TAP (782100) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. G24-171-TAP (782100) 345.0 kV to ANTHEM7 (509915) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on G24-235-TAP 345.00 (784020) 345 kV Bus a. Apply Fault at the G24-235-TAP 345.00 (784020) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-235-TAP (784020) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 b.2. G24-235-TAP (784020) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on GADWALL7 (516207) 345 kV Bus a. Apply Fault at the GADWALL7 (516207) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GADWALL7 (516207) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on THUNDER7 (515894) 345 kV Bus a. Apply Fault at the THUNDER7 (515894) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THUNDER7 (515894) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_GRDA_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_GRDA_FAULT_004 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_GRDA_FAULT_005 | Single Phase Fault with Stuck Breaker on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. COLLIN1 1 (512838) 13.8 kV to remove bus # b.2. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.3. OSAGEK2 (512876) 69.0 kV to CLEVDSTK2 (512877) 69.0 kV Transmission Circuit #1 b.4. 4SFORKK (300165) 138.0 kV to remove bus # b.5. 4SFORKKTP (301339) 138.0 kV to remove bus # b.6. 4JAVINE (300996) 138.0 kV to remove bus # b.7. 4SKIAETP (300146) 138.0 kV to remove bus # b.8. SKIAEAS4 (512649) 138.0 kV to remove bus # b.9. COLLINS4 (512705) 138.0 kV to remove bus # b.10. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.11. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.12. 4CLEVLND (300138) 138.0 kV to 2CLEVLND (300927) 69.0 kV Two Winding #1 b.13. 4CLEVLND (300138) 138.0 kV to 2CLEVLND (300927) 69.0 kV Two Winding #2 b.14. PARKMEDTP (512703) 69.0 kV to remove bus # b.15. 2PARKMDWS (301999) 69.0 kV to remove bus # b.16. SKIATTP2 (512871) 69.0 kV to remove bus # b.17. SKIATOK2 (512872) 69.0 kV to remove bus # b.18. SKIATCTY2 (512873) 69.0 kV to remove bus # b.19. GREENTP2 (512874) 69.0 kV to remove bus # b.20. 2GREEN (300994) 69.0 kV to remove bus # b.21. PRUEK2 (512875) 69.0 kV to remove bus # b.22. OSAGEK2 (512876) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWIND7 (514825) 345.0 kV to remove bus # b.6. KAYWNDT1 (515619) 12.5 kV to remove bus # b.7. KAYWNDT2 (515620) 12.5 kV to remove bus # b.8. OPENSKY7 (515621) 345.0 kV to remove bus # b.9. KAYWND11 (515622) 34.5 kV to remove bus # b.10. KAYWND12 (515623) 34.5 kV to remove bus # b.11. KAYWNDG1 (515651) 0.7 kV to remove bus # b.12. KAYWNDG2 (515652) 0.7 kV to remove bus # b.13. KAYWNDC1 (515653) 34.5 kV to remove bus # b.14. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to remove bus # b.5. FRNTWD11 (515689) 34.5 kV to remove bus # b.6. FRNTWDC1 (515690) 34.5 kV to remove bus # b.7. FRNTWDG1 (515691) 0.6 kV to remove bus # b.8. FRNTWDT1 (515692) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_R3_FAULT_001 | Single Phase Fault with Stuck Breaker on Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.3. ONETA--7 (509807) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.4. ONETA--7 (509807) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.5. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.6. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.7. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 b.8. ONETA--4 (509806) 138.0 kV to BA101-N4 (509769) 138.0 kV Transmission Circuit #1 b.9. ONETA--4 (509806) 138.0 kV to BA.N-ST4 (509786) 138.0 kV Transmission Circuit #1 b.10. OECSTM 1 (511938) 18.0 kV to Generator #1 b.11. OECGT1-1 (511939) 18.0 kV to Generator #1 b.12. OECGT1-2 (511940) 18.0 kV to Generator #1 b.13. OECSTM 2 (511941) 18.0 kV to Generator #1 b.14. OECGT2-1 (511942) 18.0 kV to Generator #1 b.15. OECGT2-2 (511943) 18.0 kV to Generator #1 b.16. ONETA--4 (509806) 138.0 kV to remove bus # b.17. ONETA--7 (509807) 345.0 kV to remove bus # b.18. OEC 7 (509836) 345.0 kV to remove bus # b.19. ONETA2-1 (509868) 34.5 kV to remove bus # b.20. ONETA5-1 (509874) 34.5 kV to remove bus # b.21. ONETA1-1 (509881) 13.8 kV to remove bus # b.22. OECSTM 1 (511938) 18.0 kV to remove bus # b.23. OECGT1-1 (511939) 18.0 kV to remove bus # b.24. OECGT1-2 (511940) 18.0 kV to remove bus # b.25. OECSTM 2 (511941) 18.0 kV to remove bus # b.26. OECGT2-1 (511942) 18.0 kV to remove bus # b.27. OECGT2-2 (511943) 18.0 kV to remove bus # b.28. ONETA--4 (509806) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_R3_FAULT_002 | Single Phase Fault with Stuck Breaker on Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. CDC-WT 4 (509842) 138.0 kV to A.A.---4 (509784) 138.0 kV Transmission Circuit #1 b.2. PPTAP 4 (509863) 138.0 kV to MOHAWK 4 (509801) 138.0 kV Transmission Circuit #1 b.3. OWASOTP4 (509844) 138.0 kV to OWAS1094 (509860) 138.0 kV Transmission Circuit #1 b.4. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.5. CDC-ET 4 (509839) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit #1 b.6. P&P WTP4 (509851) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 b.7. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 b.8. SKIATOK4 (509884) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 b.9. CIP 4 (509714) 138.0 kV to remove bus # b.10. CDC 4 (509715) 138.0 kV to remove bus # b.11. OWASO1_4 (509726) 138.0 kV to remove bus # b.12. DENVR-E4 (509743) 138.0 kV to remove bus # b.13. DENVTAP4 (509746) 138.0 kV to remove bus # b.14. PP----W4 (509805) 138.0 kV to remove bus # b.15. T.NO.--4 (509817) 138.0 kV to remove bus # b.16. PP----E4 (509818) 138.0 kV to remove bus # b.17. W.ED.-E4 (509822) 138.0 kV to remove bus # b.18. YARCH-N4 (509825) 138.0 kV to remove bus # b.19. 46ST--E4 (509837) 138.0 kV to remove bus # b.20. CDC-ET 4 (509839) 138.0 kV to remove bus # b.21. WHIRLPO4 (509840) 138.0 kV to remove bus # b.22. CDC-WT 4 (509842) 138.0 kV to remove bus # b.23. OWASOTP4 (509844) 138.0 kV to remove bus # b.24. P&P WTP4 (509851) 138.0 kV to remove bus # b.25. YARCHT 4 (509862) 138.0 kV to remove bus # b.26. PPTAP 4 (509863) 138.0 kV to remove bus # b.27. SKIATOK4 (509884) 138.0 kV to remove bus # b.28. 46ST-TP-4 (509900) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-079-TAP (763113) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.5. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRVR_GEN 1 0.6900 (523050) 0.689999998 kV Bus a. Apply Fault at the GRVR_GEN 1 0.6900 (523050) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on SILVCTYGR4 138.00 (512726) 138 kV Bus a. Apply fault at the SILVCTYGR4 138.00 (512726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY (300140) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on SKIATKTP4 138.00 (509908) 138 kV Bus a. Apply fault at the SKIATKTP4 138.00 (509908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to SKIATKTP4 (509908) 138.0 kV Transmission Circuit #1 b.2. SKIATOK4 (509884) 138.0 kV to SKIATKTP4 (509908) 138.0 kV Transmission Circuit #1 b.3. SKIATKTP4 (509908) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on CDC-ET 4 138.00 (509839) 138 kV Bus a. Apply fault at the CDC-ET 4 138.00 (509839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDC-ET 4 (509839) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on HAWTHRN4 138.00 (510413) 138 kV Bus a. Apply fault at the HAWTHRN4 138.00 (510413) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.2. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.4. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to SHEFFD-4 (509812) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on KEYSTON4 138.00 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 138.00 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 (505610) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to CLEVLND 4 (512729) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to NORTHTP4 (512731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on GLENCO 4 138.00 (513095) 138 kV Bus a. Apply fault at the GLENCO 4 138.00 (513095) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.2. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on 2MANFORD 69.000 (300936) 69 kV Bus a. Apply fault at the 2MANFORD 69.000 (300936) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CEDARPT (300923) 69.0 kV to MANFORD2 (512641) 69.0 kV Transmission Circuit #1 b.2. 2FISHER (300931) 69.0 kV to 2MANFORD (300936) 69.0 kV Transmission Circuit #1 b.3. 2MANFORD (300936) 69.0 kV to 2SILVCTY (300943) 69.0 kV Transmission Circuit #1 b.4. 2MANFORD (300936) 69.0 kV to MANFORD2 (512641) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on OSAGEK2 69.000 (512876) 69 kV Bus a. Apply fault at the OSAGEK2 69.000 (512876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.2. 2GREEN (300994) 69.0 kV to GREENTP2 (512874) 69.0 kV Transmission Circuit #1 b.3. 2PARKMDWS (301999) 69.0 kV to PARKMEDTP (512703) 69.0 kV Transmission Circuit #1 b.4. PARKMEDTP (512703) 69.0 kV to COLNSGR2 (512870) 69.0 kV Transmission Circuit #1 b.5. PARKMEDTP (512703) 69.0 kV to SKIATTP2 (512871) 69.0 kV Transmission Circuit #1 b.6. SKIATTP2 (512871) 69.0 kV to SKIATOK2 (512872) 69.0 kV Transmission Circuit #1 b.7. SKIATTP2 (512871) 69.0 kV to GREENTP2 (512874) 69.0 kV Transmission Circuit #1 b.8. SKIATOK2 (512872) 69.0 kV to SKIATCTY2 (512873) 69.0 kV Transmission Circuit #1 b.9. GREENTP2 (512874) 69.0 kV to PRUEK2 (512875) 69.0 kV Transmission Circuit #1 b.10. PRUEK2 (512875) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.11. OSAGEK2 (512876) 69.0 kV to CLEVDSTK2 (512877) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on RAMONA 2 69.000 (510392) 69 kV Bus a. Apply fault at the RAMONA 2 69.000 (510392) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to RAMONA 2 (510392) 69.0 kV Transmission Circuit #1 b.2. 2RAMONA K (301000) 69.0 kV to 2VERA (301006) 69.0 kV Transmission Circuit #1 b.3. 2RAMONA K (301000) 69.0 kV to 2WMARTTP (301471) 69.0 kV Transmission Circuit #1 b.4. 2VERA (301006) 69.0 kV to COLNSGR2 (512870) 69.0 kV Transmission Circuit #1 b.5. 2WMARTTP (301471) 69.0 kV to WALMART2 (510436) 69.0 kV Transmission Circuit #1 b.6. RAMONA 2 (510392) 69.0 kV to WALMART2 (510436) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.3. WEBBTAP4 (510376) 138.0 kV to SHIDWFC4 (520442) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on BLLNGTP4 138.00 (515635) 138 kV Bus a. Apply fault at the BLLNGTP4 138.00 (515635) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 (514701) 138.0 kV to BRECKNR4 (514815) 138.0 kV Transmission Circuit #1 b.2. BUNCHCK4 (514701) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.4. MARLNDT4 (514770) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.5. MARLNDT4 (514770) 138.0 kV to MARLAND_138 (521007) 138.0 kV Transmission Circuit #1 b.6. FNTANTP4 (515403) 138.0 kV to CWBOYHT4 (515542) 138.0 kV Transmission Circuit #1 b.7. FNTANTP4 (515403) 138.0 kV to BLLNGTP4 (515635) 138.0 kV Transmission Circuit #1 b.8. BLLNGTP4 (515635) 138.0 kV to BILLING4 (520836) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on OTOETAP4 138.00 (515978) 138 kV Bus a. Apply fault at the OTOETAP4 138.00 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.3. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.4. MILLERT4 (514704) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.5. OTOE 4 (514737) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 b.6. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.7. DMANCRK4 (515400) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on WF KAY 2 69.000 (514768) 69 kV Bus a. Apply fault at the WF KAY 2 69.000 (514768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. ORLANDO2 (514766) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.3. WF KAY 2 (514768) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 b.4. WF KAY 2 (514768) 69.0 kV to PERRY 2 (521034) 69.0 kV Transmission Circuit #1 b.5. BRONRD 2 (514797) 69.0 kV to BRRDTP 2 (514800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on PERRY 4 138.00 (514707) 138 kV Bus a. Apply fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on WRVALLY4 138.00 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 138.00 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.2. OTTER 4 (514708) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.3. WRVALLY4 (514713) 138.0 kV to WARREN 4 (521100) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on MORISNT4 138.00 (515447) 138 kV Bus a. Apply fault at the MORISNT4 138.00 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.4. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on FRMNTAP4 138.00 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 138.00 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 (514709) 138.0 kV to FAIRMON4 (514712) 138.0 kV Transmission Circuit #1 b.2. FRMNTAP4 (514709) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.3. FRMNTAP4 (514709) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on WAUKOTP4 138.00 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 138.00 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 (514710) 138.0 kV to WAUKOTP4 (514711) 138.0 kV Transmission Circuit #1 b.2. WAUKOMI4 (514710) 138.0 kV to HENESEY4 (514774) 138.0 kV Transmission Circuit #1 b.3. WAUKOTP4 (514711) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.4. WAUKOTP4 (514711) 138.0 kV to SO4TH 4 (514731) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on MARSHL 4 138.00 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 138.00 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. MARSHL 4 (514733) 138.0 kV to CTNWOOD4 (514827) 138.0 kV Transmission Circuit #1 b.3. MARSHL 4 (514733) 138.0 kV to MARSHAL4 (521006) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on MATHWSN7 345.00 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 345.00 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on OMMORANT 69.000 (529241) 69 kV Bus a. Apply fault at the OMMORANT 69.000 (529241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.2. OMMORANT (529241) 69.0 kV to OMHUFFYT (529242) 69.0 kV Transmission Circuit #1 b.3. OMHUFFYT (529242) 69.0 kV to OMRIGGS (529251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on OMWW 69.000 (529249) 69 kV Bus a. Apply fault at the OMWW 69.000 (529249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.2. OMKAWS (529246) 69.0 kV to OMPECANT (529248) 69.0 kV Transmission Circuit #1 b.3. OMPECANT (529248) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SNRPMP 4 (514799) 138.0 kV Transmission Circuit #1 b.3. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to CONORTH4 (514753) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on CONTEMP4 138.00 (514748) 138 kV Bus a. Apply fault at the CONTEMP4 138.00 (514748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on CONORTH4 138.00 (514753) 138 kV Bus a. Apply fault at the CONORTH4 138.00 (514753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to CIMARON7 (514901) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to ARCADIA7 (514908) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on MCELROY4 138.00 (515009) 138 kV Bus a. Apply fault at the MCELROY4 138.00 (515009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCELROY4 (515009) 138.0 kV to STILWTR4 (515011) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on STILWTR4 138.00 (515011) 138 kV Bus a. Apply fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 (515011) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS41 (514885) 13.8 kV Three Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_073 | 3 Phase fault on NORTWST7 345.00 (514880) 345 kV Bus a. Apply fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS31 (515743) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_074 | 3 Phase fault on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAGE 4 (514743) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_075 | 3 Phase fault on 4REDRCK 138.00 (301011) 138 kV Bus a. Apply fault at the 4REDRCK 138.00 (301011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4REDRCK (301011) 138.0 kV to OTOETAP4 (515978) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_076 | 3 Phase fault on COLINS 5 161.00 (512627) 161 kV Bus a. Apply fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.7. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.8. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_077 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_078 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_079 | 3 Phase fault on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_080 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW (300137) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_081 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4BRISTOW (300137) 138.0 kV to 4WOODY (300686) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_082 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_083 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4FAIRFAX (300139) 138.0 kV to 4REMNGTON (301369) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_084 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4SILVCTY (300140) 138.0 kV to 4STILWTR (300141) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_085 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STILWTR (300141) 138.0 kV to 4RAMSEY (300844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_086 | 3 Phase fault on 2SILVCTY 69.000 (300943) 69 kV Bus a. Apply fault at the 2SILVCTY 69.000 (300943) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 2SILVCTYLD (301630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_087 | 3 Phase fault on 2SILVCTY 69.000 (300943) 69 kV Bus a. Apply fault at the 2SILVCTY 69.000 (300943) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 2SILVCTYTP (301631) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_088 | 3 Phase fault on 2SFORKK 69.000 (300948) 69 kV Bus a. Apply fault at the 2SFORKK 69.000 (300948) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to 2TALLANT (301005) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_089 | 3 Phase fault on CIP 4 138.00 (509714) 138 kV Bus a. Apply fault at the CIP 4 138.00 (509714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIP 4 (509714) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_090 | 3 Phase fault on OWASO1_4 138.00 (509726) 138 kV Bus a. Apply fault at the OWASO1_4 138.00 (509726) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO1_4 (509726) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_091 | 3 Phase fault on DENVR-E4 138.00 (509743) 138 kV Bus a. Apply fault at the DENVR-E4 138.00 (509743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-E4 (509743) 138.0 kV to DENVTAP4 (509746) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_092 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_093 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to W.ED.-E4 (509822) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_094 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_095 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WED-TAP4 (509823) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_096 | 3 Phase fault on WEKIWA-4 138.00 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 138.00 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_097 | 3 Phase fault on A.A.---4 138.00 (509784) 138 kV Bus a. Apply fault at the A.A.---4 138.00 (509784) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. A.A.---4 (509784) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_098 | 3 Phase fault on PP----W4 138.00 (509805) 138 kV Bus a. Apply fault at the PP----W4 138.00 (509805) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PP----W4 (509805) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_099 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_100 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_101 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_102 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_103 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_104 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_105 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_106 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to TNOXF2 (760152) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_107 | 3 Phase fault on 46ST--E4 138.00 (509837) 138 kV Bus a. Apply fault at the 46ST--E4 138.00 (509837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 46ST--E4 (509837) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_108 | 3 Phase fault on WHIRLPO4 138.00 (509840) 138 kV Bus a. Apply fault at the WHIRLPO4 138.00 (509840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHIRLPO4 (509840) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_109 | 3 Phase fault on OWASO2_4 138.00 (509843) 138 kV Bus a. Apply fault at the OWASO2_4 138.00 (509843) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASO2_4 (509843) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_110 | 3 Phase fault on OWASOTP4 138.00 (509844) 138 kV Bus a. Apply fault at the OWASOTP4 138.00 (509844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWASOTP4 (509844) 138.0 kV to OWAS1094 (509860) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_111 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_112 | 3 Phase fault on VERDIGS4 138.00 (509854) 138 kV Bus a. Apply fault at the VERDIGS4 138.00 (509854) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDIGS4 (509854) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_113 | 3 Phase fault on OWAS1094 138.00 (509860) 138 kV Bus a. Apply fault at the OWAS1094 138.00 (509860) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OWAS1094 (509860) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_114 | 3 Phase fault on PPTAP 4 138.00 (509863) 138 kV Bus a. Apply fault at the PPTAP 4 138.00 (509863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PPTAP 4 (509863) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_115 | 3 Phase fault on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_116 | 3 Phase fault on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_117 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_118 | 3 Phase fault on WATOVA 4 138.00 (510384) 138 kV Bus a. Apply fault at the WATOVA 4 138.00 (510384) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATOVA 4 (510384) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_119 | 3 Phase fault on RICE CK4 138.00 (510385) 138 kV Bus a. Apply fault at the RICE CK4 138.00 (510385) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE CK4 (510385) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_120 | 3 Phase fault on N.E.S.-4 138.00 (510396) 138 kV Bus a. Apply fault at the N.E.S.-4 138.00 (510396) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to OOLOGAH 4 (513124) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_121 | 3 Phase fault on N.E.S.-7 345.00 (510406) 345 kV Bus a. Apply fault at the N.E.S.-7 345.00 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_122 | 3 Phase fault on PAWNEGR2 69.000 (512675) 69 kV Bus a. Apply fault at the PAWNEGR2 69.000 (512675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEGR2 (512675) 69.0 kV to HALLETTAP 2 (513098) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_123 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_124 | 3 Phase fault on CLEVDSTK2 69.000 (512877) 69 kV Bus a. Apply fault at the CLEVDSTK2 69.000 (512877) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVDSTK2 (512877) 69.0 kV to HALLETTAP 2 (513098) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_125 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_126 | 3 Phase fault on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_127 | 3 Phase fault on OSGE 2 69.000 (514742) 69 kV Bus a. Apply fault at the OSGE 2 69.000 (514742) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_128 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_129 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_130 | 3 Phase fault on MORRISN4 138.00 (515006) 138 kV Bus a. Apply fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_131 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_132 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_133 | 3 Phase fault on G21-047-TAP 345.00 (765721) 345 kV Bus a. Apply fault at the G21-047-TAP 345.00 (765721) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G21-047-TAP (765721) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_134 | 3 Phase fault on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRIISTOW (300889) 69.0 kV to 4BRISTOW (300137) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_135 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_136 | 3 Phase fault on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_137 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRFAX (300929) 69.0 kV to 4FAIRFAX (300139) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_138 | 3 Phase fault on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRFAX (300929) 69.0 kV to 4FAIRFAX (300139) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_139 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 4SILVCTY (300140) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_140 | 3 Phase fault on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILVCTY (300943) 69.0 kV to 4SILVCTY (300140) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_141 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO (301413) 69.0 kV to 4STILWTR (300141) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_142 | 3 Phase fault on 4STILWTR 138.00 (300141) 138 kV Bus a. Apply fault at the 4STILWTR 138.00 (300141) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STILWTRKAMO (301413) 69.0 kV to 4STILWTR (300141) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_143 | 3 Phase fault on 4SFORKK 138.00 (300165) 138 kV Bus a. Apply fault at the 4SFORKK 138.00 (300165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SFORKK (300948) 69.0 kV to 4SFORKK (300165) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_144 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to TNOXF2 (760152) 138.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_LOCAL_FAULT_145 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_001 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_002 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_003 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_005 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_006 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_007 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_008 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_009 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_010 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_012 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_013 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_014 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_015 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_016 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_017 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_018 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_019 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_020 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_021 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_022 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_023 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_024 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_025 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_026 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_027 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_028 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_029 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_031 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_032 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_033 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_034 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_035 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_036 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_038 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to MONETT345 (580555) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_039 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_040 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_041 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_042 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_043 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_044 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_045 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_046 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_047 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P1_REGIOINAL_FAULT_048 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD7 (509870) 345.0 kV to SAPLPRD4 (509871) 138.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-4 (509757) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-4 (509757) 138.0 kV to SHEFFD-4 (509812) 138.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to WEKIWA-4 (509757) 138.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.3. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4FAIRFAX (300139) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.2. 4STILWTR (300141) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 b.3. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 b.6. OSAGE 4 (514743) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STDBEAR4 138.00 (514758) 138 kV Bus a. Apply Fault at the STDBEAR4 138.00 (514758) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.2. CONORTH4 (514753) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on STILWTR4 138.00 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCELROY4 (515009) 138.0 kV to STILWTR4 (515011) 138.0 kV Transmission Circuit #1 b.2. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.3. STILWTR4 (515011) 138.0 kV to SPGVLLY4 (515574) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply Fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 b.3. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.4. KEYSTON4 (505610) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on KEYSTON5 161.00 (505609) 161 kV Bus a. Apply Fault at the KEYSTON5 161.00 (505609) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 b.3. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.4. KEY1&2 1 (505612) 13.8 kV to KEYSTON5 (505609) 161.0 kV to KEYSTON4 (505610) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.2. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.5. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.6. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COLINS 5 161.00 (512627) 161 kV Bus a. Apply Fault at the COLINS 5 161.00 (512627) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4SKIAETP (300146) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.3. 4SKIAETP (300146) 138.0 kV to SKIAEAS4 (512649) 138.0 kV Transmission Circuit #1 b.4. 4SKIAETP (300146) 138.0 kV to COLLINS4 (512705) 138.0 kV Transmission Circuit #1 b.5. 4SFORKK (300165) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.6. 2SFORKK (300948) 69.0 kV to 4SFORKK (300165) 138.0 kV Two Winding #1 b.7. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 b.8. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.9. COLINS 5 (512627) 161.0 kV to COLLINS4 (512705) 138.0 kV to COLLIN1 1 (512838) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 2 (514705) 69.0 kV to WF KAY 2 (514768) 69.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.3. COWCRK 4 (514706) 138.0 kV to WRVALLY4 (514713) 138.0 kV Transmission Circuit #1 b.4. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.5. COWCRK 2 (514705) 69.0 kV to COWCRK 4 (514706) 138.0 kV to COWCRK 1 (515717) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. OSGE 2 (514742) 69.0 kV to CONBLKT2 (515402) 69.0 kV Transmission Circuit #1 b.3. OSGE 2 (514742) 69.0 kV to CONTCBN2 (515947) 69.0 kV Transmission Circuit #1 b.4. OSGE 2 (514742) 69.0 kV to OMMORANT (529241) 69.0 kV Transmission Circuit #1 b.5. OSGE 2 (514742) 69.0 kV to OMWW (529249) 69.0 kV Transmission Circuit #1 b.6. OSAGE 4 (514743) 138.0 kV to STDBEAR4 (514758) 138.0 kV Transmission Circuit #1 b.7. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.8. OSAGE 4 (514743) 138.0 kV to MARLNDT4 (514770) 138.0 kV Transmission Circuit #1 b.9. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.10. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 31 (515744) 13.2 kV Three Winding #3 b.11. OSGE 2 (514742) 69.0 kV to OSAGE 4 (514743) 138.0 kV to OSAGE 41 (515745) 13.2 kV Three Winding #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to KINGWD 7 (516019) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER1G (514805) 22.0 kV Two Winding #1 b.2. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-066T (515975) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to SOONER2G (514806) 20.0 kV Two Winding #1 b.2. SOONER 7 (514803) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to SPGCK1&2 (514882) 13.8 kV Two Winding #1 b.3. SPRNGCK7 (514881) 345.0 kV to SPGCK3&4 (514883) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. WHEAGLE4 (514761) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.2. CONTEMP4 (514748) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.4. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.5. WOODRNG4 (514714) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on 4FISHERTP 138.00 (300131) 138 kV Bus a. Apply Fault at the 4FISHERTP 138.00 (300131) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FISHERTP (300131) 138.0 kV to KEYSTON4 (505610) 138.0 kV Transmission Circuit #1 b.2. 4FISHERTP (300131) 138.0 kV to 4FISHER (300145) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on 4BRISTOW 138.00 (300137) 138 kV Bus a. Apply Fault at the 4BRISTOW 138.00 (300137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4BRISTOW (300137) 138.0 kV to 4WOODY (300686) 138.0 kV Transmission Circuit #1 b.2. 4BRISTOW (300137) 138.0 kV to 2BRIISTOW (300889) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to CLEVLND 4 (512729) 138.0 kV Transmission Circuit #z1 b.2. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on 4FAIRFAX 138.00 (300139) 138 kV Bus a. Apply Fault at the 4FAIRFAX 138.00 (300139) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4FAIRFAX (300139) 138.0 kV to 4REMNGTON (301369) 138.0 kV Transmission Circuit #1 b.2. 4FAIRFAX (300139) 138.0 kV to 2FAIRFAX (300929) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on 4SILVCTY 138.00 (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY 138.00 (300140) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4SILVCTY (300140) 138.0 kV to 4STILWTR (300141) 138.0 kV Transmission Circuit #1 b.2. 4SILVCTY (300140) 138.0 kV to SILVCTYGR4 (512726) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on 4CLEVLND 138.00 (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND 138.00 (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLEVLND (300927) 69.0 kV to OSAGEK2 (512876) 69.0 kV Transmission Circuit #1 b.2. 2CLEVLND (300927) 69.0 kV to 4CLEVLND (300138) 138.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on 4JAVINE 138.00 (300996) 138 kV Bus a. Apply Fault at the 4JAVINE 138.00 (300996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4JAVINE (300996) 138.0 kV to 4HOMNYTP (301640) 138.0 kV Transmission Circuit #1 b.2. 4JAVINE (300996) 138.0 kV to 4SFORKKTP (301339) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply Fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to TNOXF2 (760152) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on ANTHEM7 345.00 (509915) 345 kV Bus a. Apply Fault at the ANTHEM7 345.00 (509915) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTHEM7 (509915) 345.0 kV to G24-171-TAP (782100) 345.0 kV Transmission Circuit #1 b.2. ANTHEM7 (509915) 345.0 kV to G24-294-TAP (785790) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on WEBBTAP4 138.00 (510376) 138 kV Bus a. Apply Fault at the WEBBTAP4 138.00 (510376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEBBTAP4 (510376) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 b.2. WEBBTAP4 (510376) 138.0 kV to SHIDLER4 (510403) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on N.E.S.-7 345.00 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 345.00 (510406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.E.S.-7 (510406) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. N.E.S.-7 (510406) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PAWNSW4 138.00 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 138.00 (512749) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNSW4 (512749) 138.0 kV to 4CLEVLND (300138) 138.0 kV Transmission Circuit #1 b.2. PAWNSW4 (512749) 138.0 kV to GLENCO 4 (513095) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on MILLERT4 138.00 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 138.00 (514704) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLERT4 (514704) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. MILLERT4 (514704) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on COWCRK 4 138.00 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 138.00 (514706) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWCRK 4 (514706) 138.0 kV to PERRY 4 (514707) 138.0 kV Transmission Circuit #1 b.2. COWCRK 4 (514706) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PERRY 4 138.00 (514707) 138 kV Bus a. Apply Fault at the PERRY 4 138.00 (514707) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PERRY 4 (514707) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. PERRY 4 (514707) 138.0 kV to COWCRK 4 (514706) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #2 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on OSAGE 4 138.00 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 138.00 (514743) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE 4 (514743) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 b.2. OSAGE 4 (514743) 138.0 kV to WEBBTAP4 (510376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply Fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEAGLE4 (514761) 138.0 kV to DMNCRKT4 (515412) 138.0 kV Transmission Circuit #1 b.2. WHEAGLE4 (514761) 138.0 kV to CONTEMP4 (514748) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on SNRPMPT4 138.00 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 138.00 (514798) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNRPMPT4 (514798) 138.0 kV to SOONER 4 (514802) 138.0 kV Transmission Circuit #1 b.2. SNRPMPT4 (514798) 138.0 kV to OSAGE 4 (514743) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SOONER 4 138.00 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 138.00 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.2. SOONER 4 (514802) 138.0 kV to SNRPMPT4 (514798) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to G24-235-TAP (784020) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on NORTWST7 345.00 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 345.00 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST7 (514880) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on SPRNGCK7 345.00 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 345.00 (514881) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRNGCK7 (514881) 345.0 kV to NORTWST7 (514880) 345.0 kV Transmission Circuit #1 b.2. SPRNGCK7 (514881) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on MORRISN4 138.00 (515006) 138 kV Bus a. Apply Fault at the MORRISN4 138.00 (515006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRISN4 (515006) 138.0 kV to G24-056-TAP (778650) 138.0 kV Transmission Circuit #1 b.2. MORRISN4 (515006) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on STILWTR4 138.00 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 138.00 (515011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWTR4 (515011) 138.0 kV to MORISNT4 (515447) 138.0 kV Transmission Circuit #1 b.2. STILWTR4 (515011) 138.0 kV to MCELROY4 (515009) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on THUNDER7 345.00 (515894) 345 kV Bus a. Apply Fault at the THUNDER7 345.00 (515894) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THUNDER7 (515894) 345.0 kV to GEN-2021-018 (765470) 345.0 kV Transmission Circuit #1 b.2. THUNDER7 (515894) 345.0 kV to GEN-2021-019 (765480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on GEN-2015-066345.00 (515974) 345 kV Bus a. Apply Fault at the GEN-2015-066345.00 (515974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-066 (515974) 345.0 kV to G15-066XFMR1 (515972) 34.5 kV Two Winding #1 b.2. GEN-2015-066 (515974) 345.0 kV to G15-066T (515975) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on G15-066T 345.00 (515975) 345 kV Bus a. Apply Fault at the G15-066T 345.00 (515975) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-066T (515975) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. G15-066T (515975) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PINTAIL7 345.00 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 345.00 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. PINTAIL7 (516010) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WAGNWTIE7 345.00 (516192) 345 kV Bus a. Apply Fault at the WAGNWTIE7 345.00 (516192) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGNWTIE7 (516192) 345.0 kV to GADWALL7 (516207) 345.0 kV Transmission Circuit #1 b.2. WAGNWTIE7 (516192) 345.0 kV to WAGNWL7 (516198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on G24-171-TAP 345.00 (782100) 345 kV Bus a. Apply Fault at the G24-171-TAP 345.00 (782100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-171-TAP (782100) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. G24-171-TAP (782100) 345.0 kV to ANTHEM7 (509915) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on G24-235-TAP 345.00 (784020) 345 kV Bus a. Apply Fault at the G24-235-TAP 345.00 (784020) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G24-235-TAP (784020) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 b.2. G24-235-TAP (784020) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CLEVLND (300138) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on GADWALL7 (516207) 345 kV Bus a. Apply Fault at the GADWALL7 (516207) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GADWALL7 (516207) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on THUNDER7 (515894) 345 kV Bus a. Apply Fault at the THUNDER7 (515894) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THUNDER7 (515894) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PINTAIL7 (516010) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_GRDA_FAULT_002 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_GRDA_FAULT_003 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_GRDA_FAULT_004 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_GRDA_FAULT_005 | Single Phase Fault with Stuck Breaker on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. COLLIN1 1 (512838) 13.8 kV to remove bus # b.2. 4CLEVLND (300138) 138.0 kV to PAWNSW4 (512749) 138.0 kV Transmission Circuit #1 b.3. OSAGEK2 (512876) 69.0 kV to CLEVDSTK2 (512877) 69.0 kV Transmission Circuit #1 b.4. 4SFORKK (300165) 138.0 kV to remove bus # b.5. 4SFORKKTP (301339) 138.0 kV to remove bus # b.6. 4JAVINE (300996) 138.0 kV to remove bus # b.7. 4SKIAETP (300146) 138.0 kV to remove bus # b.8. SKIAEAS4 (512649) 138.0 kV to remove bus # b.9. COLLINS4 (512705) 138.0 kV to remove bus # b.10. 4CLEVLND (300138) 138.0 kV to 4SILVCTY (300140) 138.0 kV Transmission Circuit #1 b.11. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.12. 4CLEVLND (300138) 138.0 kV to 2CLEVLND (300927) 69.0 kV Two Winding #1 b.13. 4CLEVLND (300138) 138.0 kV to 2CLEVLND (300927) 69.0 kV Two Winding #2 b.14. PARKMEDTP (512703) 69.0 kV to remove bus # b.15. 2PARKMDWS (301999) 69.0 kV to remove bus # b.16. SKIATTP2 (512871) 69.0 kV to remove bus # b.17. SKIATOK2 (512872) 69.0 kV to remove bus # b.18. SKIATCTY2 (512873) 69.0 kV to remove bus # b.19. GREENTP2 (512874) 69.0 kV to remove bus # b.20. 2GREEN (300994) 69.0 kV to remove bus # b.21. PRUEK2 (512875) 69.0 kV to remove bus # b.22. OSAGEK2 (512876) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWIND7 (514825) 345.0 kV to remove bus # b.6. KAYWNDT1 (515619) 12.5 kV to remove bus # b.7. KAYWNDT2 (515620) 12.5 kV to remove bus # b.8. OPENSKY7 (515621) 345.0 kV to remove bus # b.9. KAYWND11 (515622) 34.5 kV to remove bus # b.10. KAYWND12 (515623) 34.5 kV to remove bus # b.11. KAYWNDG1 (515651) 0.7 kV to remove bus # b.12. KAYWNDG2 (515652) 0.7 kV to remove bus # b.13. KAYWNDC1 (515653) 34.5 kV to remove bus # b.14. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_OKGE_FAULT_002 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.3. FRNTWDG1 (515691) 0.6 kV to Generator #1 b.4. FRNTWND7 (515688) 345.0 kV to remove bus # b.5. FRNTWD11 (515689) 34.5 kV to remove bus # b.6. FRNTWDC1 (515690) 34.5 kV to remove bus # b.7. FRNTWDG1 (515691) 0.6 kV to remove bus # b.8. FRNTWDT1 (515692) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_OKGE_FAULT_003 | Single Phase Fault with Stuck Breaker on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 4 (514802) 138.0 kV to SOONER 7 (514803) 345.0 kV to SOONER 1 (515760) 13.8 kV Three Winding #5 b.2. CLEVLND7 (512694) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_OKGE_FAULT_004 | Single Phase Fault with Stuck Breaker on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTWST7 (514880) 345.0 kV to SPRNGCK7 (514881) 345.0 kV Transmission Circuit #1 b.2. NORTWST4 (514879) 138.0 kV to NORTWST7 (514880) 345.0 kV to NORTWS21 (515742) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_R3_FAULT_001 | Single Phase Fault with Stuck Breaker on Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.3. ONETA--7 (509807) 345.0 kV to R.S.S.-7 (509782) 345.0 kV Transmission Circuit #1 b.4. ONETA--7 (509807) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.5. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.6. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.7. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 b.8. ONETA--4 (509806) 138.0 kV to BA101-N4 (509769) 138.0 kV Transmission Circuit #1 b.9. ONETA--4 (509806) 138.0 kV to BA.N-ST4 (509786) 138.0 kV Transmission Circuit #1 b.10. OECSTM 1 (511938) 18.0 kV to Generator #1 b.11. OECGT1-1 (511939) 18.0 kV to Generator #1 b.12. OECGT1-2 (511940) 18.0 kV to Generator #1 b.13. OECSTM 2 (511941) 18.0 kV to Generator #1 b.14. OECGT2-1 (511942) 18.0 kV to Generator #1 b.15. OECGT2-2 (511943) 18.0 kV to Generator #1 b.16. ONETA--4 (509806) 138.0 kV to remove bus # b.17. ONETA--7 (509807) 345.0 kV to remove bus # b.18. OEC 7 (509836) 345.0 kV to remove bus # b.19. ONETA2-1 (509868) 34.5 kV to remove bus # b.20. ONETA5-1 (509874) 34.5 kV to remove bus # b.21. ONETA1-1 (509881) 13.8 kV to remove bus # b.22. OECSTM 1 (511938) 18.0 kV to remove bus # b.23. OECGT1-1 (511939) 18.0 kV to remove bus # b.24. OECGT1-2 (511940) 18.0 kV to remove bus # b.25. OECSTM 2 (511941) 18.0 kV to remove bus # b.26. OECGT2-1 (511942) 18.0 kV to remove bus # b.27. OECGT2-2 (511943) 18.0 kV to remove bus # b.28. ONETA--4 (509806) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_R3_FAULT_002 | Single Phase Fault with Stuck Breaker on Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. CDC-WT 4 (509842) 138.0 kV to A.A.---4 (509784) 138.0 kV Transmission Circuit #1 b.2. PPTAP 4 (509863) 138.0 kV to MOHAWK 4 (509801) 138.0 kV Transmission Circuit #1 b.3. OWASOTP4 (509844) 138.0 kV to OWAS1094 (509860) 138.0 kV Transmission Circuit #1 b.4. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.5. CDC-ET 4 (509839) 138.0 kV to OWAS88_4 (509887) 138.0 kV Transmission Circuit #1 b.6. P&P WTP4 (509851) 138.0 kV to WEKIWA-4 (509757) 138.0 kV Transmission Circuit #1 b.7. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 b.8. SKIATOK4 (509884) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 b.9. CIP 4 (509714) 138.0 kV to remove bus # b.10. CDC 4 (509715) 138.0 kV to remove bus # b.11. OWASO1_4 (509726) 138.0 kV to remove bus # b.12. DENVR-E4 (509743) 138.0 kV to remove bus # b.13. DENVTAP4 (509746) 138.0 kV to remove bus # b.14. PP----W4 (509805) 138.0 kV to remove bus # b.15. T.NO.--4 (509817) 138.0 kV to remove bus # b.16. PP----E4 (509818) 138.0 kV to remove bus # b.17. W.ED.-E4 (509822) 138.0 kV to remove bus # b.18. YARCH-N4 (509825) 138.0 kV to remove bus # b.19. 46ST--E4 (509837) 138.0 kV to remove bus # b.20. CDC-ET 4 (509839) 138.0 kV to remove bus # b.21. WHIRLPO4 (509840) 138.0 kV to remove bus # b.22. CDC-WT 4 (509842) 138.0 kV to remove bus # b.23. OWASOTP4 (509844) 138.0 kV to remove bus # b.24. P&P WTP4 (509851) 138.0 kV to remove bus # b.25. YARCHT 4 (509862) 138.0 kV to remove bus # b.26. PPTAP 4 (509863) 138.0 kV to remove bus # b.27. SKIATOK4 (509884) 138.0 kV to remove bus # b.28. 46ST-TP-4 (509900) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on TENGEN 7 345.00 (508586) 345 kV Bus a. Apply Fault at the TENGEN 7 345.00 (508586) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.2. TENGEN 7 (508586) 345.0 kV to TENGAS 1 (506745) 18.0 kV Two Winding #1 b.3. TENGEN 7 (508586) 345.0 kV to TENGAS 2 (506746) 18.0 kV Two Winding #1 b.4. TENGEN 7 (508586) 345.0 kV to TENGAS 3 (506747) 18.0 kV Two Winding #1 b.5. TENGEN 7 (508586) 345.0 kV to TENSTM 1 (506748) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.4. TENRUSK7 (508585) 345.0 kV to GEN-2020-081 (764120) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to MUSKOG4G (515223) 18.0 kV Two Winding #1 b.3. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.4. MUSKOGE7 (515224) 345.0 kV to MUSKOG6G (515226) 24.0 kV Two Winding #1 b.5. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.6. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.7. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #2 b.8. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.9. MUSKOGE7 (515224) 345.0 kV to OKTAHA 7 (516091) 345.0 kV Transmission Circuit #1 b.10. MUSKOGE7 (515224) 345.0 kV to RAVEN 7 (516210) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCG1 (506752) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.2. LEBROCG2 (506753) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.3. LEBROCS1 (506754) 18.0 kV to LEBROCK7 (508572) 345.0 kV Two Winding #1 b.4. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.5. PIRKEY 7 (508563) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #2 b.6. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.3. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #zo | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-079-TAP (763113) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP7 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP7 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP7 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NRSS7 (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply Fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 b.3. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to PONDRSA7 (516074) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR1W7 (515634) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #2 b.3. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (525839) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (525839) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.4. O.K.U.-7 (511456) 345.0 kV to O.K.U.2-7 (511584) 345.0 kV Transmission Circuit #z1 b.5. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on GRVR_GEN 1 0.6900 (523050) 0.689999998 kV Bus a. Apply Fault at the GRVR_GEN 1 0.6900 (523050) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. GRVR_GEN 1 (523050) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to LEBROCK7 (508572) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to SW SHV 7 (507760) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to 7SAREPTA% (337376) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to O.K.U.3-7 (511607) 345.0 kV Transmission Circuit #z1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (525750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to GRIFFIN7 (515778) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (532837) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #3 b.2. DGRASSE7 (515852) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 b.2. FTSMITH7 (515302) 345.0 kV to FTSMTHW5 (515301) 161.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2026-PR14 PSIS - CF | 29W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMITH71 (519010) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2026-PR14 | 04 SOUTHEAST | 915975 | WILLOW_CR_HV345.00 | 345 | 17.527 | 17.6214 | 0.0944
GEN-2026-PR14 | 04 SOUTHEAST | 515975 | G15-066T 345.00 | 345 | 20.5144 | 20.6088 | 0.0944
GEN-2026-PR14 | 04 SOUTHEAST | 514803 | SOONER 7 345.00 | 345 | 30.2832 | 30.3542 | 0.071
GEN-2026-PR14 | 04 SOUTHEAST | 515974 | GEN-2015-066345.00 | 345 | 17.649 | 17.7184 | 0.0694
GEN-2026-PR14 | 04 SOUTHEAST | 512694 | CLEVLND7 345.00 | 345 | 16.5542 | 16.5769 | 0.0227
GEN-2026-PR14 | 04 SOUTHEAST | 515894 | THUNDER7 345.00 | 345 | 13.4563 | 13.4689 | 0.0126
GEN-2026-PR14 | 04 SOUTHEAST | 765480 | GEN-2021-019345.00 | 345 | 13.3103 | 13.3226 | 0.0123
GEN-2026-PR14 | 04 SOUTHEAST | 509852 | T.NO.--7 345.00 | 345 | 25.1006 | 25.1108 | 0.0102
GEN-2026-PR14 | 04 SOUTHEAST | 516010 | PINTAIL7 345.00 | 345 | 17.2734 | 17.2835 | 0.0101
GEN-2026-PR14 | 04 SOUTHEAST | 516019 | KINGWD 7 345.00 | 345 | 17.2093 | 17.2193 | 0.01
GEN-2026-PR14 | 04 SOUTHEAST | 784020 | G24-235-TAP 345.00 | 345 | 13.8578 | 13.8666 | 0.0088
GEN-2026-PR14 | 04 SOUTHEAST | 784021 | GEN-2024-235345.00 | 345 | 13.8578 | 13.8666 | 0.0088
GEN-2026-PR14 | 04 SOUTHEAST | 509817 | T.NO.--4 138.00 | 138 | 45.3633 | 45.3716 | 0.0083
GEN-2026-PR14 | 04 SOUTHEAST | 509895 | T.NO.2-4 138.00 | 138 | 44.7953 | 44.8036 | 0.0083
GEN-2026-PR14 | 04 SOUTHEAST | 760152 | TNOXF2 138.00 | 138 | 44.7422 | 44.7504 | 0.0082
GEN-2026-PR14 | 04 SOUTHEAST | 514802 | SOONER 4 138.00 | 138 | 32.7104 | 32.7182 | 0.0078
GEN-2026-PR14 | 04 SOUTHEAST | 786991 | GEN-2024-334345.00 | 345 | 16.2234 | 16.2307 | 0.0073
GEN-2026-PR14 | 04 SOUTHEAST | 515576 | RANCHRD7 345.00 | 345 | 16.2787 | 16.286 | 0.0073
GEN-2026-PR14 | 04 SOUTHEAST | 529200 | OMCDLEC7 345.00 | 345 | 16.2483 | 16.2556 | 0.0073
GEN-2026-PR14 | 04 SOUTHEAST | 786998 | G24-334-C1 345.00 | 345 | 16.1451 | 16.1522 | 0.0071
GEN-2026-PR14 | 04 SOUTHEAST | 786999 | G24-334-C2 345.00 | 345 | 16.1611 | 16.1682 | 0.0071
GEN-2026-PR14 | 04 SOUTHEAST | 516192 | WAGNWTIE7 345.00 | 345 | 16.2806 | 16.2875 | 0.0069
GEN-2026-PR14 | 04 SOUTHEAST | 516198 | WAGNWL7 345.00 | 345 | 16.2806 | 16.2875 | 0.0069
GEN-2026-PR14 | 04 SOUTHEAST | 516207 | GADWALL7 345.00 | 345 | 16.2806 | 16.2875 | 0.0069
GEN-2026-PR14 | 04 SOUTHEAST | 782100 | G24-171-TAP 345.00 | 345 | 21.384 | 21.3909 | 0.0069
GEN-2026-PR14 | 04 SOUTHEAST | 782101 | GEN-2024-171345.00 | 345 | 21.3605 | 21.3673 | 0.0068
GEN-2026-PR14 | 04 SOUTHEAST | 763069 | G18-071-TAP 345.00 | 345 | 15.7983 | 15.8051 | 0.0068
GEN-2026-PR14 | 04 SOUTHEAST | 763065 | GEN-2018-071345.00 | 345 | 15.7333 | 15.74 | 0.0067
GEN-2026-PR14 | 04 SOUTHEAST | 509755 | WEKIWA-7 345.00 | 345 | 22.8516 | 22.8579 | 0.0063
GEN-2026-PR14 | 04 SOUTHEAST | 300138 | 4CLEVLND 138.00 | 138 | 24.7765 | 24.7818 | 0.0053
GEN-2026-PR14 | 04 SOUTHEAST | 762636 | GEN-2018-028138.00 | 138 | 35.7537 | 35.7589 | 0.0052
GEN-2026-PR14 | 04 SOUTHEAST | 512729 | CLEVLND 4 138.00 | 138 | 24.775 | 24.7802 | 0.0052
GEN-2026-PR14 | 04 SOUTHEAST | 514715 | WOODRNG7 345.00 | 345 | 20.3186 | 20.3238 | 0.0052
GEN-2026-PR14 | 04 SOUTHEAST | 515688 | FRNTWND7 345.00 | 345 | 13.4917 | 13.4967 | 0.005
GEN-2026-PR14 | 04 SOUTHEAST | 914720 | SKELETON__HV345.00 | 345 | 19.2168 | 19.2214 | 0.0046
GEN-2026-PR14 | 04 SOUTHEAST | 516066 | FRNT2WD7 345.00 | 345 | 12.4209 | 12.425 | 0.0041
GEN-2026-PR14 | 04 SOUTHEAST | 509757 | WEKIWA-4 138.00 | 138 | 34.8439 | 34.8479 | 0.004
GEN-2026-PR14 | 04 SOUTHEAST | 560389 | GEN-2010-055138.00 | 138 | 34.8439 | 34.8479 | 0.004
GEN-2026-PR14 | 04 SOUTHEAST | 514825 | KAYWIND7 345.00 | 345 | 13.9123 | 13.9162 | 0.0039
GEN-2026-PR14 | 04 SOUTHEAST | 515621 | OPENSKY7 345.00 | 345 | 13.9534 | 13.9573 | 0.0039
GEN-2026-PR14 | 04 SOUTHEAST | 765470 | GEN-2021-018345.00 | 345 | 7.6582 | 7.662 | 0.0038
GEN-2026-PR14 | 04 SOUTHEAST | 514880 | NORTWST7 345.00 | 345 | 39.1872 | 39.1908 | 0.0036
GEN-2026-PR14 | 04 SOUTHEAST | 514881 | SPRNGCK7 345.00 | 345 | 27.8918 | 27.8952 | 0.0034
GEN-2026-PR14 | 04 SOUTHEAST | 515497 | MATHWSN7 345.00 | 345 | 42.9957 | 42.9991 | 0.0034
GEN-2026-PR14 | 04 SOUTHEAST | 514704 | MILLERT4 138.00 | 138 | 21.3216 | 21.3247 | 0.0031
GEN-2026-PR14 | 04 SOUTHEAST | 509870 | SAPLPRD7 345.00 | 345 | 23.6341 | 23.6371 | 0.003
GEN-2026-PR14 | 04 SOUTHEAST | 514798 | SNRPMPT4 138.00 | 138 | 21.3979 | 21.4009 | 0.003
GEN-2026-PR14 | 04 SOUTHEAST | 784620 | GEN-2024-255345.00 | 345 | 25.6311 | 25.634 | 0.0029
GEN-2026-PR14 | 04 SOUTHEAST | 784621 | GEN-2024-255345.00 | 345 | 25.992 | 25.9949 | 0.0029
GEN-2026-PR14 | 04 SOUTHEAST | 509782 | R.S.S.-7 345.00 | 345 | 33.4533 | 33.456 | 0.0027
GEN-2026-PR14 | 04 SOUTHEAST | 509842 | CDC-WT 4 138.00 | 138 | 27.6974 | 27.7001 | 0.0027
GEN-2026-PR14 | 04 SOUTHEAST | 511877 | G16133G16146345.00 | 345 | 33.4533 | 33.456 | 0.0027
GEN-2026-PR14 | 04 SOUTHEAST | 784591 | GEN-2024-254345.00 | 345 | 38.3777 | 38.3803 | 0.0026
GEN-2026-PR14 | 04 SOUTHEAST | 784590 | GEN-2024-254345.00 | 345 | 37.8548 | 37.8574 | 0.0026
GEN-2026-PR14 | 04 SOUTHEAST | 509839 | CDC-ET 4 138.00 | 138 | 26.2051 | 26.2075 | 0.0024
GEN-2026-PR14 | 04 SOUTHEAST | 514901 | CIMARON7 345.00 | 345 | 42.7074 | 42.7098 | 0.0024
GEN-2026-PR14 | 04 SOUTHEAST | 509834 | COGENT 7 345.00 | 345 | 30.9346 | 30.9369 | 0.0023
GEN-2026-PR14 | 04 SOUTHEAST | 784141 | GEN-2024-239345.00 | 345 | 42.0259 | 42.0282 | 0.0023
GEN-2026-PR14 | 04 SOUTHEAST | 509715 | CDC 4 138.00 | 138 | 25.514 | 25.5162 | 0.0022
GEN-2026-PR14 | 04 SOUTHEAST | 509806 | ONETA--4 138.00 | 138 | 52.4882 | 52.4904 | 0.0022
GEN-2026-PR14 | 04 SOUTHEAST | 515875 | REDNGTN7 345.00 | 345 | 18.9738 | 18.976 | 0.0022
GEN-2026-PR14 | 04 SOUTHEAST | 515877 | REDDIRT7 345.00 | 345 | 18.9689 | 18.9711 | 0.0022
GEN-2026-PR14 | 04 SOUTHEAST | 514737 | OTOE 4 138.00 | 138 | 17.016 | 17.018 | 0.002
GEN-2026-PR14 | 04 SOUTHEAST | 510406 | N.E.S.-7 345.00 | 345 | 17.1414 | 17.1434 | 0.002
GEN-2026-PR14 | 04 SOUTHEAST | 515978 | OTOETAP4 138.00 | 138 | 17.0635 | 17.0655 | 0.002
GEN-2026-PR14 | 04 SOUTHEAST | 784531 | GEN-2024-252345.00 | 345 | 38.1485 | 38.1504 | 0.0019
GEN-2026-PR14 | 04 SOUTHEAST | 301011 | 4REDRCK 138.00 | 138 | 16.6798 | 16.6817 | 0.0019
GEN-2026-PR14 | 04 SOUTHEAST | 505610 | KEYSTON4 138.00 | 138 | 24.1112 | 24.1131 | 0.0019
GEN-2026-PR14 | 04 SOUTHEAST | 784530 | GEN-2024-252345.00 | 345 | 37.6287 | 37.6305 | 0.0018
GEN-2026-PR14 | 04 SOUTHEAST | 762321 | GEN-2017-164345.00 | 345 | 11.9545 | 11.9563 | 0.0018
GEN-2026-PR14 | 04 SOUTHEAST | 562900 | G15052_1 345.00 | 345 | 13.2935 | 13.2952 | 0.0017
GEN-2026-PR14 | 04 SOUTHEAST | 509807 | ONETA--7 345.00 | 345 | 30.5348 | 30.5365 | 0.0017
GEN-2026-PR14 | 04 SOUTHEAST | 509836 | OEC 7 345.00 | 345 | 30.4298 | 30.4315 | 0.0017
GEN-2026-PR14 | 04 SOUTHEAST | 509871 | SAPLPRD4 138.00 | 138 | 34.3595 | 34.3612 | 0.0017
GEN-2026-PR14 | 04 SOUTHEAST | 532837 | G15052_T 345.00 | 345 | 13.3491 | 13.3508 | 0.0017
GEN-2026-PR14 | 04 SOUTHEAST | 514879 | NORTWST4 138.00 | 138 | 50.648 | 50.6497 | 0.0017
GEN-2026-PR14 | 04 SOUTHEAST | 509812 | SHEFFD-4 138.00 | 138 | 27.1185 | 27.12 | 0.0015
GEN-2026-PR14 | 04 SOUTHEAST | 509900 | 46ST-TP-4 138.00 | 138 | 20.4022 | 20.4037 | 0.0015
GEN-2026-PR14 | 04 SOUTHEAST | 515477 | CHSHLMV7 345.00 | 345 | 13.6246 | 13.6261 | 0.0015
GEN-2026-PR14 | 04 SOUTHEAST | 515476 | HUNTERS7 345.00 | 345 | 13.6478 | 13.6493 | 0.0015
GEN-2026-PR14 | 04 SOUTHEAST | 509915 | ANTHEM7 345.00 | 345 | 12.8868 | 12.8881 | 0.0013
GEN-2026-PR14 | 04 SOUTHEAST | 532794 | ROSEHIL7 345.00 | 345 | 19.3319 | 19.3332 | 0.0013
GEN-2026-PR14 | 04 SOUTHEAST | 514714 | WOODRNG4 138.00 | 138 | 20.8085 | 20.8097 | 0.0012
GEN-2026-PR14 | 04 SOUTHEAST | 514743 | OSAGE 4 138.00 | 138 | 18.3722 | 18.3734 | 0.0012
GEN-2026-PR14 | 04 SOUTHEAST | 514761 | WHEAGLE4 138.00 | 138 | 17.2292 | 17.2304 | 0.0012
GEN-2026-PR14 | 04 SOUTHEAST | 515412 | DMNCRKT4 138.00 | 138 | 14.5663 | 14.5675 | 0.0012
GEN-2026-PR14 | 04 SOUTHEAST | 514908 | ARCADIA7 345.00 | 345 | 33.201 | 33.2022 | 0.0012
GEN-2026-PR14 | 04 SOUTHEAST | 510396 | N.E.S.-4 138.00 | 138 | 37.1617 | 37.1628 | 0.0011
GEN-2026-PR14 | 04 SOUTHEAST | 300140 | 4SILVCTY 138.00 | 138 | 18.011 | 18.0121 | 0.0011
GEN-2026-PR14 | 04 SOUTHEAST | 512726 | SILVCTYGR4 138.00 | 138 | 17.8044 | 17.8055 | 0.0011
GEN-2026-PR14 | 04 SOUTHEAST | 770101 | GEN-2022-156138.00 | 138 | 17.2929 | 17.294 | 0.0011
GEN-2026-PR14 | 04 SOUTHEAST | 514709 | FRMNTAP4 138.00 | 138 | 19.3884 | 19.3894 | 0.001
GEN-2026-PR14 | 04 SOUTHEAST | 515447 | MORISNT4 138.00 | 138 | 14.598 | 14.599 | 0.001
GEN-2026-PR14 | 04 SOUTHEAST | 785790 | G24-294-TAP 345.00 | 345 | 12.6329 | 12.6339 | 0.001
GEN-2026-PR14 | 04 SOUTHEAST | 509851 | P&P WTP4 138.00 | 138 | 16.251 | 16.252 | 0.001
GEN-2026-PR14 | 04 SOUTHEAST | 300131 | 4FISHERTP 138.00 | 138 | 16.0227 | 16.0236 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 509823 | WED-TAP4 138.00 | 138 | 20.0898 | 20.0907 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 514758 | STDBEAR4 138.00 | 138 | 15.2138 | 15.2147 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 514799 | SNRPMP 4 138.00 | 138 | 11.8138 | 11.8147 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 515006 | MORRISN4 138.00 | 138 | 14.5701 | 14.571 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 515543 | RENFROW7 345.00 | 345 | 12.6609 | 12.6618 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 770501 | GEN-2022-176345.00 | 345 | 12.8982 | 12.8991 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 785791 | GEN-2024-294345.00 | 345 | 12.576 | 12.5769 | 0.0009
GEN-2026-PR14 | 04 SOUTHEAST | 770500 | G22-176-TAP 345.00 | 345 | 12.9314 | 12.9322 | 0.0008
GEN-2026-PR14 | 04 SOUTHEAST | 762342 | GEN-2017-178345.00 | 345 | 8.3311 | 8.3319 | 0.0008
GEN-2026-PR14 | 04 SOUTHEAST | 509862 | YARCHT 4 138.00 | 138 | 14.8923 | 14.893 | 0.0007
GEN-2026-PR14 | 04 SOUTHEAST | 514707 | PERRY 4 138.00 | 138 | 11.6785 | 11.6792 | 0.0007
GEN-2026-PR14 | 04 SOUTHEAST | 301640 | 4HOMNYTP 138.00 | 138 | 9.7348 | 9.7355 | 0.0007
GEN-2026-PR14 | 04 SOUTHEAST | 514706 | COWCRK 4 138.00 | 138 | 12.0007 | 12.0014 | 0.0007
GEN-2026-PR14 | 04 SOUTHEAST | 514711 | WAUKOTP4 138.00 | 138 | 16.7262 | 16.7269 | 0.0007
GEN-2026-PR14 | 04 SOUTHEAST | 509726 | OWASO1_4 138.00 | 138 | 14.8749 | 14.8755 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 509844 | OWASOTP4 138.00 | 138 | 15.949 | 15.9496 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 512749 | PAWNSW4 138.00 | 138 | 10.9413 | 10.9419 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 515011 | STILWTR4 138.00 | 138 | 14.693 | 14.6936 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 515646 | GRNTWD 7 345.00 | 345 | 11.0898 | 11.0904 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 765720 | GEN-2021-047345.00 | 345 | 15.2108 | 15.2114 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 773121 | GEN-2023-057138.00 | 138 | 10.8578 | 10.8584 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 778650 | G24-056-TAP 138.00 | 138 | 11.5965 | 11.5971 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 778651 | GEN-2024-056138.00 | 138 | 11.4576 | 11.4582 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 515009 | MCELROY4 138.00 | 138 | 14.3102 | 14.3108 | 0.0006
GEN-2026-PR14 | 04 SOUTHEAST | 509745 | CLARKSV7 345.00 | 345 | 22.1387 | 22.1392 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 300141 | 4STILWTR 138.00 | 138 | 12.4088 | 12.4093 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 509818 | PP----E4 138.00 | 138 | 12.3318 | 12.3323 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 510380 | DELWARE7 345.00 | 345 | 11.6787 | 11.6792 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 514770 | MARLNDT4 138.00 | 138 | 11.8467 | 11.8472 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 763417 | GEN-2018-128345.00 | 345 | 10.9409 | 10.9414 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 914715 | SKELETON__HV345.00 | 345 | 6.0166 | 6.0171 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 509746 | DENVTAP4 138.00 | 138 | 10.3215 | 10.322 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 509884 | SKIATOK4 138.00 | 138 | 12.342 | 12.3425 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 509908 | SKIATKTP4 138.00 | 138 | 12.3809 | 12.3814 | 0.0005
GEN-2026-PR14 | 04 SOUTHEAST | 511878 | G16133_765TN765.00 | 765 | 9.2558 | 9.2562 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 511879 | G16133_765R1765.00 | 765 | 9.2558 | 9.2562 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 761229 | GEN-2017-150345.00 | 345 | 24.6803 | 24.6807 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 761250 | GEN-2017-233345.00 | 345 | 24.7311 | 24.7315 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 300927 | 2CLEVLND 69.000 | 69 | 11.033 | 11.0334 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 509825 | YARCH-N4 138.00 | 138 | 9.9308 | 9.9312 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 513095 | GLENCO 4 138.00 | 138 | 9.9747 | 9.9751 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 514713 | WRVALLY4 138.00 | 138 | 9.3236 | 9.324 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 514742 | OSGE 2 69.000 | 69 | 20.2683 | 20.2687 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 515400 | DMANCRK4 138.00 | 138 | 8.5087 | 8.5091 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 515444 | MCNOWND7 345.00 | 345 | 25.5084 | 25.5088 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 515610 | FSHRTAP7 345.00 | 345 | 18.1557 | 18.1561 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 515694 | ARMFTWD4 138.00 | 138 | 10.5006 | 10.501 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 765350 | GEN-2021-006345.00 | 345 | 17.9024 | 17.9028 | 0.0004
GEN-2026-PR14 | 04 SOUTHEAST | 786601 | GEN-2024-321345.00 | 345 | 33.2272 | 33.2275 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 301546 | 4RAMSEYCP 138.00 | 138 | 10.4493 | 10.4496 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509727 | OAKS W4 138.00 | 138 | 15.1783 | 15.1786 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509743 | DENVR-E4 138.00 | 138 | 8.7244 | 8.7247 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509822 | W.ED.-E4 138.00 | 138 | 8.6319 | 8.6322 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 515574 | SPGVLLY4 138.00 | 138 | 11.3313 | 11.3316 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 516363 | ARMADILLO_HV138.00 | 138 | 10.3474 | 10.3477 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 515990 | SKELTON7 345.00 | 345 | 5.2049 | 5.2052 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 521007 | MARLAND_138 138.00 | 138 | 7.96 | 7.9603 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 300139 | 4FAIRFAX 138.00 | 138 | 8.2246 | 8.2249 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 301603 | 4RPLY 138.00 | 138 | 8.1496 | 8.1499 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509737 | BA101 S4 138.00 | 138 | 18.8812 | 18.8815 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509832 | W.ED.-W4 138.00 | 138 | 12.0757 | 12.076 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509865 | CARSONT4 138.00 | 138 | 12.5106 | 12.5109 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 514708 | OTTER 4 138.00 | 138 | 10.534 | 10.5343 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 515947 | CONTCBN2 69.000 | 69 | 16.9969 | 16.9972 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 914807 | MINCO_I_&_HV345.00 | 345 | 25.5052 | 25.5055 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509741 | CARSN-N4 138.00 | 138 | 9.7106 | 9.7109 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509805 | PP----W4 138.00 | 138 | 8.8356 | 8.8359 | 0.0003
GEN-2026-PR14 | 04 SOUTHEAST | 509721 | BA.NO-S4 138.00 | 138 | 12.8614 | 12.8616 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 509748 | DENVR-W4 138.00 | 138 | 10.0653 | 10.0655 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 510376 | WEBBTAP4 138.00 | 138 | 8.7033 | 8.7035 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 515605 | CANADN7 345.00 | 345 | 12.8234 | 12.8236 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 532801 | ELKRVR17 345.00 | 345 | 9.1993 | 9.1995 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 300996 | 4JAVINE 138.00 | 138 | 6.9593 | 6.9595 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 301379 | 4OSAGEWIND 138.00 | 138 | 7.6616 | 7.6618 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 512876 | OSAGEK2 69.000 | 69 | 7.6421 | 7.6423 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 521100 | WARREN 4 138.00 | 138 | 6.6243 | 6.6245 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 588190 | GEN-2016-128345.00 | 345 | 4.9499 | 4.9501 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 300943 | 2SILVCTY 69.000 | 69 | 10.9581 | 10.9583 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 505609 | KEYSTON5 161.00 | 161 | 7.4858 | 7.486 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 515448 | CRSRDSW7 345.00 | 345 | 12.9421 | 12.9423 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 515549 | MNCWND37 345.00 | 345 | 15.2441 | 15.2443 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 515585 | MAMTHPW7 345.00 | 345 | 14.573 | 14.5732 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 515600 | KNGFSHR7 345.00 | 345 | 11.4969 | 11.4971 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 529248 | OMPECANT 69.000 | 69 | 13.3742 | 13.3744 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 529249 | OMWW 69.000 | 69 | 15.2535 | 15.2537 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 762823 | GEN-2018-048345.00 | 345 | 18.052 | 18.0522 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 777361 | GEN-2024-013345.00 | 345 | 22.3978 | 22.398 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 777368 | GEN-2024-C1 345.00 | 345 | 20.2256 | 20.2258 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 777369 | GEN-2024-C2 345.00 | 345 | 20.2256 | 20.2258 | 0.0002
GEN-2026-PR14 | 04 SOUTHEAST | 529242 | OMHUFFYT 69.000 | 69 | 16.3608 | 16.3609 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 515582 | SLNGWND7 345.00 | 345 | 9.004 | 9.0041 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 515939 | MNCWND47 345.00 | 345 | 10.5596 | 10.5597 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 529244 | OMNEASTT 69.000 | 69 | 11.6254 | 11.6255 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 509821 | HWY20-T4 138.00 | 138 | 4.9082 | 4.9083 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 513098 | HALLETTAP 2 69.000 | 69 | 4.4107 | 4.4108 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 516087 | TRAV22Z7 345.00 | 345 | 5.6385 | 5.6386 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 516108 | TRAV11Z7 345.00 | 345 | 5.241 | 5.2411 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 300137 | 4BRISTOW 138.00 | 138 | 10.6585 | 10.6586 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 300922 | 2BURBANK 69.000 | 69 | 3.3039 | 3.304 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 300939 | 2PAWNEE 69.000 | 69 | 3.6095 | 3.6096 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 509754 | WHORSE-4 138.00 | 138 | 4.8884 | 4.8885 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 511880 | G16133_765R2765.00 | 765 | 4.5588 | 4.5589 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 511883 | G16133_345CS345.00 | 345 | 7.9338 | 7.9339 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 511911 | ZONE-4 SUB 345.00 | 345 | 6.5056 | 6.5057 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 511929 | ZONE-6 SUB 345.00 | 345 | 7.0521 | 7.0522 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 514733 | MARSHL 4 138.00 | 138 | 8.3768 | 8.3769 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 516054 | TRAV1WD7 345.00 | 345 | 5.5235 | 5.5236 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 516107 | TRAV21Z7 345.00 | 345 | 5.6388 | 5.6389 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 520441 | HARDY 4 138.00 | 138 | 4.1989 | 4.199 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 520461 | GARBER 4 138.00 | 138 | 4.7488 | 4.7489 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 521006 | MARSHAL4 138.00 | 138 | 8.3768 | 8.3769 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 529241 | OMMORANT 69.000 | 69 | 15.1944 | 15.1945 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 529246 | OMKAWS 69.000 | 69 | 12.5557 | 12.5558 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 520442 | SHIDWFC4 138.00 | 138 | 6.5401 | 6.5402 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 529245 | OMGONTER 69.000 | 69 | 11.9652 | 11.9653 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 914801 | MINCO_IV__HV345.00 | 345 | 14.7112 | 14.7113 | 0.0001
GEN-2026-PR14 | 04 SOUTHEAST | 300923 | 2CEDARPT 69.000 | 69 | 2.7819 | 2.7819 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 509798 | HWY20--4 138.00 | 138 | 3.8991 | 3.8991 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 509837 | 46ST--E4 138.00 | 138 | 3.5842 | 3.5842 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 509897 | WLDCT_HIL4 138.00 | 138 | 4.9 | 4.9 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 511726 | ZONE-5 SUB 345.00 | 345 | 7.0117 | 7.0117 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 511881 | G16133_765R3765.00 | 765 | 3.6467 | 3.6467 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 511882 | G16133_765CS765.00 | 765 | 3.6467 | 3.6467 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 511884 | ZONE-1 SUB 345.00 | 345 | 7.0445 | 7.0445 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 511893 | ZONE-2 SUB 345.00 | 345 | 7.0263 | 7.0263 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 511902 | ZONE-3 SUB 345.00 | 345 | 6.9661 | 6.9661 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 512641 | MANFORD2 69.000 | 69 | 4.1452 | 4.1452 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 514705 | COWCRK 2 69.000 | 69 | 4.7099 | 4.7099 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 514766 | ORLANDO2 69.000 | 69 | 1.8069 | 1.8069 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 514768 | WF KAY 2 69.000 | 69 | 3.3392 | 3.3392 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 514797 | BRONRD 2 69.000 | 69 | 1.6719 | 1.6719 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 514800 | BRRDTP 2 69.000 | 69 | 1.9584 | 1.9584 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 515980 | MNCWND57 345.00 | 345 | 7.6141 | 7.6141 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 516036 | TRAV3WD7 345.00 | 345 | 7.4771 | 7.4771 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 516045 | TRAV2WD7 345.00 | 345 | 5.9716 | 5.9716 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 516086 | TRAV3WZ7 345.00 | 345 | 6.9474 | 6.9474 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 516109 | TRAV12Z7 345.00 | 345 | 5.2409 | 5.2409 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 520443 | WEBBCTY4 138.00 | 138 | 4.6247 | 4.6247 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 521034 | PERRY 2 69.000 | 69 | 2.4059 | 2.4059 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 529243 | OMNWESTT 69.000 | 69 | 14.655 | 14.655 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 529247 | OMMCCORD 69.000 | 69 | 8.5134 | 8.5134 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 529306 | OMHOMNY4 138.00 | 138 | 3.2377 | 3.2377 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 760032 | GEN-2017-133345.00 | 345 | 5.3754 | 5.3754 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 760389 | GEN-2017-140345.00 | 345 | 1.9352 | 1.9352 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 760393 | G17-140-BUS 345.00 | 345 | 1.9219 | 1.9219 | 0
GEN-2026-PR14 | 04 SOUTHEAST | 914802 | MINCO IV HV2345.00 | 345 | 9.989 | 9.989 | 0

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
04 SOUTHEAST | GEN-2026-PR14 | 41.395 | PASS | 10.471 | PASS | N/A | N/A

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | BASE CASE | 50.1896 | PASS | 10.9094 | PASS | 10809.4212 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300131 [4FISHERTP 138.00] TO BUS 300140 [4SILVCTY 138.00] CKT 1 | 50.1897 | PASS | 10.9095 | PASS | 10809.5126 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300131 [4FISHERTP 138.00] TO BUS 300145 [4FISHER 138.00] CKT 1 | 50.1878 | PASS | 10.9094 | PASS | 10809.395 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300131 [4FISHERTP 138.00] TO BUS 505610 [KEYSTON4 138.00] CKT 1 | 50.1894 | PASS | 10.9094 | PASS | 10809.4462 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 300140 [4SILVCTY 138.00] CKT 1 | 50.0988 | PASS | 10.9095 | PASS | 10809.5049 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 300140 [4SILVCTY 138.00] CKT 1 | 50.1585 | PASS | 10.909 | PASS | 10809.0485 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 300927 [2CLEVLND 69.00] CKT 1 | 50.1885 | PASS | 10.9094 | PASS | 10809.4197 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 300927 [2CLEVLND 69.00] CKT 2 | 50.1883 | PASS | 10.9095 | PASS | 10809.4516 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 301640 [4HOMNYTP 138.00] CKT 1 | 50.1376 | PASS | 10.9083 | PASS | 10808.3419 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 512729 [CLEVLND 4 138.00] CKT 1 | 48.8568 | PASS | 10.9002 | PASS | 10800.1819 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 512749 [PAWNSW4 138.00] CKT 1 | 50.1841 | PASS | 10.9095 | PASS | 10809.4886 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 301369 [4REMNGTON 138.00] CKT 1 | 50.1863 | PASS | 10.9095 | PASS | 10809.4563 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 512749 [PAWNSW4 138.00] CKT 1 | 50.186 | PASS | 10.9094 | PASS | 10809.4439 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 300141 [4STILWTR 138.00] CKT 1 | 50.1897 | PASS | 10.9094 | PASS | 10809.3526 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 300943 [2SILVCTY 69.00] CKT 1 | 50.1894 | PASS | 10.9095 | PASS | 10809.5265 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 300943 [2SILVCTY 69.00] CKT 2 | 50.1894 | PASS | 10.9095 | PASS | 10809.5271 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 512726 [SILVCTYGR4 138.00] CKT 1 | 50.1883 | PASS | 10.9097 | PASS | 10809.6813 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 513095 [GLENCO 4 138.00] CKT 1 | 50.1852 | PASS | 10.9091 | PASS | 10809.0951 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300927 [2CLEVLND 69.00] TO BUS 512876 [OSAGEK2 69.00] CKT 1 | 50.1813 | PASS | 10.909 | PASS | 10809.0367 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300996 [4JAVINE 138.00] TO BUS 301640 [4HOMNYTP 138.00] CKT 1 | 50.1376 | PASS | 10.9083 | PASS | 10808.3117 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 301011 [4REDRCK 138.00] TO BUS 515978 [OTOETAP4 138.00] CKT 1 | 50.1888 | PASS | 10.9094 | PASS | 10809.4263 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 301369 [4REMNGTON 138.00] TO BUS 510403 [SHIDLER4 138.00] CKT 1 | 50.1832 | PASS | 10.9096 | PASS | 10809.5547 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 505610 [KEYSTON4 138.00] TO BUS 509757 [WEKIWA-4 138.00] CKT 1 | 50.18 | PASS | 10.9095 | PASS | 10809.542 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509727 [OAKS W4 138.00] TO BUS 509848 [OAKSWTP4 138.00] CKT 1 | 50.1873 | PASS | 10.9095 | PASS | 10809.487 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509739 [CARSN-T4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 50.1383 | PASS | 10.9099 | PASS | 10809.9459 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509741 [CARSN-N4 138.00] TO BUS 509865 [CARSONT4 138.00] CKT 1 | 50.189 | PASS | 10.9095 | PASS | 10809.5189 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 50.1118 | PASS | 10.9094 | PASS | 10809.3528 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 50.1014 | PASS | 10.9138 | PASS | 10813.7749 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509746 [DENVTAP4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 50.1884 | PASS | 10.9093 | PASS | 10809.33 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509748 [DENVR-W4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 50.1884 | PASS | 10.9096 | PASS | 10809.6313 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509753 [116JENK4 138.00] TO BUS 509759 [JENKS--4 138.00] CKT 1 | 50.1692 | PASS | 10.9095 | PASS | 10809.5312 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509753 [116JENK4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 50.1694 | PASS | 10.9096 | PASS | 10809.6461 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 50.1519 | PASS | 10.9154 | PASS | 10815.4097 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 48.6937 | PASS | 10.9089 | PASS | 10808.8773 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 44.9827 | PASS | 10.9189 | PASS | 10818.8564 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 509812 [SHEFFD-4 138.00] CKT 1 | 50.1258 | PASS | 10.9096 | PASS | 10809.6296 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 509823 [WED-TAP4 138.00] CKT 1 | 50.1568 | PASS | 10.9096 | PASS | 10809.5754 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 509851 [P&P WTP4 138.00] CKT 1 | 50.1859 | PASS | 10.9101 | PASS | 10810.0821 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 512726 [SILVCTYGR4 138.00] CKT 1 | 50.1884 | PASS | 10.9095 | PASS | 10809.5491 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 560389 [GEN-2010-055 138.00] CKT 1 | 50.1844 | PASS | 10.9095 | PASS | 10809.4574 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509758 [PRATTV-4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 50.1751 | PASS | 10.9092 | PASS | 10809.2247 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509759 [JENKS--4 138.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 50.1692 | PASS | 10.9095 | PASS | 10809.5056 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 50.1825 | PASS | 10.9091 | PASS | 10809.0763 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 50.1359 | PASS | 10.9116 | PASS | 10811.5505 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 50.1028 | PASS | 10.9083 | PASS | 10808.2536 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 49.1969 | PASS | 10.908 | PASS | 10807.9621 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146 345.00] CKT 1 | 50.1423 | PASS | 10.9067 | PASS | 10806.7118 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 50.1366 | PASS | 10.9148 | PASS | 10814.7779 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 50.0614 | PASS | 10.9097 | PASS | 10809.7388 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509875 [RSS T2 4 138.00] CKT 1 | 50.1826 | PASS | 10.909 | PASS | 10809.0475 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509888 [72ELWOD4 138.00] CKT 1 | 50.1809 | PASS | 10.9096 | PASS | 10809.585 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509904 [AVERYDR4 138.00] CKT 1 | 50.1839 | PASS | 10.9096 | PASS | 10809.5618 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509805 [PP----W4 138.00] TO BUS 509851 [P&P WTP4 138.00] CKT 1 | 50.188 | PASS | 10.9092 | PASS | 10809.2256 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 50.1892 | PASS | 10.9094 | PASS | 10809.4404 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 50.1892 | PASS | 10.9094 | PASS | 10809.4404 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 49.8656 | PASS | 10.9171 | PASS | 10817.0672 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509812 [SHEFFD-4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 50.1258 | PASS | 10.9096 | PASS | 10809.606 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509815 [S.S.---4 138.00] TO BUS 509821 [HWY20-T4 138.00] CKT 1 | 50.1886 | PASS | 10.9094 | PASS | 10809.4456 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509815 [S.S.---4 138.00] TO BUS 509823 [WED-TAP4 138.00] CKT 1 | 50.1573 | PASS | 10.9095 | PASS | 10809.5345 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509815 [S.S.---4 138.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 50.179 | PASS | 10.9095 | PASS | 10809.5178 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509839 [CDC-ET 4 138.00] CKT 1 | 50.172 | PASS | 10.9094 | PASS | 10809.3509 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509842 [CDC-WT 4 138.00] CKT 1 | 50.1707 | PASS | 10.9092 | PASS | 10809.2008 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509844 [OWASOTP4 138.00] CKT 1 | 50.1031 | PASS | 10.9096 | PASS | 10809.6359 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509851 [P&P WTP4 138.00] CKT 1 | 50.1869 | PASS | 10.9098 | PASS | 10809.8433 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509895 [T.NO.2-4 138.00] CKT 1 | 50.0811 | PASS | 10.9101 | PASS | 10810.142 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509900 [46ST-TP-4 138.00] CKT 1 | 50.1672 | PASS | 10.9093 | PASS | 10809.2656 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509908 [SKIATKTP4 138.00] CKT 1 | 50.1798 | PASS | 10.9087 | PASS | 10808.7228 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 510396 [N.E.S.-4 138.00] CKT 1 | 50.1141 | PASS | 10.9099 | PASS | 10809.9183 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 50.0887 | PASS | 10.9089 | PASS | 10808.9375 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509823 [WED-TAP4 138.00] TO BUS 509865 [CARSONT4 138.00] CKT 1 | 50.1878 | PASS | 10.9095 | PASS | 10809.5015 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509832 [W.ED.-W4 138.00] TO BUS 509865 [CARSONT4 138.00] CKT 1 | 50.1884 | PASS | 10.9094 | PASS | 10809.3953 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509848 [OAKSWTP4 138.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 50.1816 | PASS | 10.9095 | PASS | 10809.486 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509848 [OAKSWTP4 138.00] TO BUS 509904 [AVERYDR4 138.00] CKT 1 | 50.1813 | PASS | 10.9096 | PASS | 10809.5578 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 49.6757 | PASS | 10.9009 | PASS | 10800.9211 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 46.4073 | PASS | 10.8681 | PASS | 10768.0521 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 50.0886 | PASS | 10.9089 | PASS | 10808.9374 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 782100 [G24-171-TAP 345.00] CKT 1 | 49.611 | PASS | 10.9089 | PASS | 10808.8753 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509871 [SAPLPRD4 138.00] TO BUS 509888 [72ELWOD4 138.00] CKT 1 | 50.181 | PASS | 10.9095 | PASS | 10809.5269 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028 138.00] CKT 1 | 50.1895 | PASS | 10.91 | PASS | 10810.0251 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 782100 [G24-171-TAP 345.00] CKT 1 | 49.6161 | PASS | 10.9077 | PASS | 10807.6982 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 785790 [G24-294-TAP 345.00] CKT 1 | 49.6374 | PASS | 10.908 | PASS | 10808.0488 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510376 [WEBBTAP4 138.00] TO BUS 510403 [SHIDLER4 138.00] CKT 1 | 50.1452 | PASS | 10.9097 | PASS | 10809.7425 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510376 [WEBBTAP4 138.00] TO BUS 514743 [OSAGE 4 138.00] CKT 1 | 50.1416 | PASS | 10.91 | PASS | 10809.9752 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510376 [WEBBTAP4 138.00] TO BUS 520442 [SHIDWFC4 138.00] CKT 1 | 50.1854 | PASS | 10.9093 | PASS | 10809.3283 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 770500 [G22-176-TAP 345.00] CKT 1 | 50.0083 | PASS | 10.91 | PASS | 10810.0423 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510382 [WPAWHSK4 138.00] TO BUS 510403 [SHIDLER4 138.00] CKT 1 | 50.144 | PASS | 10.9102 | PASS | 10810.2082 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510406 [N.E.S.-7 345.00] TO BUS 770500 [G22-176-TAP 345.00] CKT 1 | 50.0271 | PASS | 10.9095 | PASS | 10809.4942 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 50.1882 | PASS | 10.9092 | PASS | 10809.1946 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 50.1773 | PASS | 10.9093 | PASS | 10809.331 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511877 [G16133G16146 345.00] TO BUS 511878 [G16133_765TN 765.00] CKT 1 | 50.1843 | PASS | 10.9096 | PASS | 10809.6069 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511877 [G16133G16146 345.00] TO BUS 511878 [G16133_765TN 765.00] CKT 2 | 50.1843 | PASS | 10.9096 | PASS | 10809.6069 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 42.8611 | PASS | 10.8383 | PASS | 10738.3007 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512726 [SILVCTYGR4 138.00] TO BUS 770101 [GEN-2022-156 138.00] CKT 1 | 50.1922 | PASS | 10.9094 | PASS | 10809.4092 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512749 [PAWNSW4 138.00] TO BUS 513095 [GLENCO 4 138.00] CKT 1 | 50.1856 | PASS | 10.9091 | PASS | 10809.0893 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512749 [PAWNSW4 138.00] TO BUS 773121 [GEN-2023-057 138.00] CKT 1 | 50.1876 | PASS | 10.9104 | PASS | 10810.4105 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514704 [MILLERT4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 50.083 | PASS | 10.91 | PASS | 10809.9685 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514704 [MILLERT4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 50.084 | PASS | 10.9099 | PASS | 10809.9407 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514704 [MILLERT4 138.00] TO BUS 515978 [OTOETAP4 138.00] CKT 1 | 50.1871 | PASS | 10.9094 | PASS | 10809.4275 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514768 [WF KAY 2 69.00] CKT 1 | 50.1873 | PASS | 10.9095 | PASS | 10809.4514 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514707 [PERRY 4 138.00] CKT 1 | 50.1485 | PASS | 10.9096 | PASS | 10809.5554 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 50.1795 | PASS | 10.9097 | PASS | 10809.7061 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 50.1722 | PASS | 10.9095 | PASS | 10809.4524 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514707 [PERRY 4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 50.1504 | PASS | 10.9096 | PASS | 10809.5589 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 50.1786 | PASS | 10.9098 | PASS | 10809.8088 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 50.1783 | PASS | 10.9097 | PASS | 10809.6958 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 515694 [ARMFTWD4 138.00] CKT 1 | 50.1978 | PASS | 10.9092 | PASS | 10809.2175 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514712 [FAIRMON4 138.00] CKT 1 | 50.1862 | PASS | 10.9092 | PASS | 10809.2451 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 50.1722 | PASS | 10.9093 | PASS | 10809.2529 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 50.184 | PASS | 10.9094 | PASS | 10809.4186 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514711 [WAUKOTP4 138.00] CKT 1 | 50.0679 | PASS | 10.9094 | PASS | 10809.4487 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514774 [HENESEY4 138.00] CKT 1 | 50.0686 | PASS | 10.9095 | PASS | 10809.4608 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 50.1629 | PASS | 10.9094 | PASS | 10809.3758 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 50.1903 | PASS | 10.9094 | PASS | 10809.4468 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514712 [FAIRMON4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 50.1859 | PASS | 10.9093 | PASS | 10809.2669 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 50.1862 | PASS | 10.9095 | PASS | 10809.4824 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514733 [MARSHL 4 138.00] CKT 1 | 50.1083 | PASS | 10.9095 | PASS | 10809.4829 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 49.2404 | PASS | 10.9247 | PASS | 10824.7194 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 47.5125 | PASS | 10.9119 | PASS | 10811.8596 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 50.2285 | PASS | 10.9082 | PASS | 10808.1887 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 43.4609 | PASS | 10.9153 | PASS | 10815.3372 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 50.2175 | PASS | 10.9084 | PASS | 10808.3519 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914715 [SKELETON__HV 345.00] CKT 1 | 50.2085 | PASS | 10.9099 | PASS | 10809.9344 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914720 [SKELETON__HV 345.00] CKT 1 | 50.1912 | PASS | 10.9093 | PASS | 10809.2874 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514790 [IMO 4 138.00] CKT 1 | 50.1781 | PASS | 10.9095 | PASS | 10809.4614 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 50.1895 | PASS | 10.9094 | PASS | 10809.4216 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 50.108 | PASS | 10.9095 | PASS | 10809.4855 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 521006 [MARSHAL4 138.00] CKT 1 | 50.1891 | PASS | 10.9094 | PASS | 10809.4441 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514737 [OTOE 4 138.00] TO BUS 515978 [OTOETAP4 138.00] CKT 1 | 50.1879 | PASS | 10.9094 | PASS | 10809.4158 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 515402 [CONBLKT2 69.00] CKT 1 | 50.1867 | PASS | 10.9094 | PASS | 10809.4171 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 515947 [CONTCBN2 69.00] CKT 1 | 50.1685 | PASS | 10.9093 | PASS | 10809.3466 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 529241 [OMMORANT 69.00] CKT 1 | 50.0951 | PASS | 10.9095 | PASS | 10809.5466 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 529249 [OMWW 69.00] CKT 1 | 50.143 | PASS | 10.9094 | PASS | 10809.42 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514758 [STDBEAR4 138.00] CKT 1 | 50.1898 | PASS | 10.9095 | PASS | 10809.4969 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 50.1841 | PASS | 10.9094 | PASS | 10809.4346 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514770 [MARLNDT4 138.00] CKT 1 | 50.1893 | PASS | 10.9095 | PASS | 10809.5325 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514798 [SNRPMPT4 138.00] CKT 1 | 50.057 | PASS | 10.91 | PASS | 10809.9649 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514745 [CHERPLT2 69.00] TO BUS 515402 [CONBLKT2 69.00] CKT 1 | 50.1867 | PASS | 10.9094 | PASS | 10809.4172 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514748 [CONTEMP4 138.00] TO BUS 514753 [CONORTH4 138.00] CKT 1 | 50.1885 | PASS | 10.9094 | PASS | 10809.4383 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514748 [CONTEMP4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 50.1877 | PASS | 10.9094 | PASS | 10809.416 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514753 [CONORTH4 138.00] TO BUS 514758 [STDBEAR4 138.00] CKT 1 | 50.1889 | PASS | 10.9095 | PASS | 10809.4573 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 514760 [KILDARE4 138.00] CKT 1 | 50.1874 | PASS | 10.9095 | PASS | 10809.4949 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 50.1627 | PASS | 10.9099 | PASS | 10809.8553 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514764 [NWKRKAT4 138.00] CKT 1 | 50.1368 | PASS | 10.9118 | PASS | 10811.7861 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 50.085 | PASS | 10.9099 | PASS | 10809.9141 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514768 [WF KAY 2 69.00] TO BUS 514800 [BRRDTP 2 69.00] CKT 1 | 50.1879 | PASS | 10.9094 | PASS | 10809.4285 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514768 [WF KAY 2 69.00] TO BUS 521034 [PERRY 2 69.00] CKT 1 | 50.189 | PASS | 10.9094 | PASS | 10809.4399 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514770 [MARLNDT4 138.00] TO BUS 515542 [CWBOYHT4 138.00] CKT 1 | 50.1886 | PASS | 10.9096 | PASS | 10809.5698 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514770 [MARLNDT4 138.00] TO BUS 521007 [MARLAND_138 138.00] CKT 1 | 50.1889 | PASS | 10.9094 | PASS | 10809.4339 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514798 [SNRPMPT4 138.00] TO BUS 514799 [SNRPMP 4 138.00] CKT 1 | 50.1883 | PASS | 10.9094 | PASS | 10809.4047 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514798 [SNRPMPT4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 50.0561 | PASS | 10.91 | PASS | 10809.9535 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 50.0658 | PASS | 10.9088 | PASS | 10808.8254 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515444 [MCNOWND7 345.00] CKT 1 | 50.2223 | PASS | 10.9066 | PASS | 10806.5798 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515549 [MNCWND37 345.00] CKT 1 | 50.2176 | PASS | 10.9073 | PASS | 10807.261 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 50.0678 | PASS | 10.9108 | PASS | 10810.8485 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 50.1731 | PASS | 10.9096 | PASS | 10809.6435 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 761250 [GEN-2017-233 345.00] CKT 1 | 50.2217 | PASS | 10.9068 | PASS | 10806.7987 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 914801 [MINCO_IV__HV 345.00] CKT 1 | 50.1925 | PASS | 10.9093 | PASS | 10809.2713 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 914807 [MINCO_I_&_HV 345.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.4212 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 50.0588 | PASS | 10.9095 | PASS | 10809.5326 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515576 [RANCHRD7 345.00] CKT 1 | 43.6124 | PASS | 10.9137 | PASS | 10813.7106 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515894 [THUNDER7 345.00] CKT 1 | 50.3576 | PASS | 10.915 | PASS | 10814.9737 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 43.0262 | PASS | 10.4714 | PASS | 10371.4159 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 43.5222 | PASS | 10.9192 | PASS | 10819.211 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 42.8973 | PASS | 10.9139 | PASS | 10813.9134 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 44.9934 | PASS | 10.9232 | PASS | 10823.1863 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 50.1851 | PASS | 10.9095 | PASS | 10809.4516 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514820 [JENSENT4 138.00] CKT 1 | 50.1895 | PASS | 10.9094 | PASS | 10809.4108 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 50.1895 | PASS | 10.9094 | PASS | 10809.3824 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.3626 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514825 [KAYWIND7 345.00] TO BUS 515621 [OPENSKY7 345.00] CKT 1 | 50.1655 | PASS | 10.911 | PASS | 10810.9745 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514829 [PINE ST4 138.00] CKT 1 | 50.1624 | PASS | 10.9104 | PASS | 10810.398 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 50.1552 | PASS | 10.9098 | PASS | 10809.8483 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515373 [LBRTYLK4 138.00] CKT 1 | 50.1754 | PASS | 10.9094 | PASS | 10809.3926 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515377 [CRESENT4 138.00] CKT 1 | 50.1929 | PASS | 10.9093 | PASS | 10809.286 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514834 [KETCH 4 138.00] CKT 1 | 50.1723 | PASS | 10.9094 | PASS | 10809.3955 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 50.1849 | PASS | 10.9095 | PASS | 10809.5064 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 515466 [MITCHSB4 138.00] CKT 1 | 50.1776 | PASS | 10.9097 | PASS | 10809.6629 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514851 [QUAILCK4 138.00] TO BUS 514852 [SLVRLAK4 138.00] CKT 1 | 50.1894 | PASS | 10.9094 | PASS | 10809.4405 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514851 [QUAILCK4 138.00] TO BUS 514873 [LNEOAK 4 138.00] CKT 1 | 50.1846 | PASS | 10.9094 | PASS | 10809.4318 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514852 [SLVRLAK4 138.00] TO BUS 514854 [BRADEN 4 138.00] CKT 1 | 50.1685 | PASS | 10.9094 | PASS | 10809.3996 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514854 [BRADEN 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 50.1682 | PASS | 10.9094 | PASS | 10809.415 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514862 [RICHRDS4 138.00] TO BUS 514864 [PIEDMNT4 138.00] CKT 1 | 50.1789 | PASS | 10.9094 | PASS | 10809.411 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514863 [HAYMAKR4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 50.1889 | PASS | 10.9094 | PASS | 10809.3975 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514864 [PIEDMNT4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 50.1783 | PASS | 10.9094 | PASS | 10809.4152 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 50.1712 | PASS | 10.9095 | PASS | 10809.5182 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 515374 [CHISHOM4 138.00] CKT 1 | 50.1853 | PASS | 10.9094 | PASS | 10809.4405 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 47.5055 | PASS | 10.9186 | PASS | 10818.5841 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 50.0754 | PASS | 10.9088 | PASS | 10808.7891 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 49.986 | PASS | 10.9096 | PASS | 10809.574 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 50.1672 | PASS | 10.9097 | PASS | 10809.6761 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 42.8303 | PASS | 10.9116 | PASS | 10811.5547 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784620 [GEN-2024-255 345.00] CKT 3 | 50.2042 | PASS | 10.9082 | PASS | 10808.152 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784621 [GEN-2024-255 345.00] CKT 1 | 49.8539 | PASS | 10.9052 | PASS | 10805.1504 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514894 [CZECHAL4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 50.1748 | PASS | 10.9095 | PASS | 10809.458 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 50.1703 | PASS | 10.9095 | PASS | 10809.4797 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 50.1329 | PASS | 10.9091 | PASS | 10809.0931 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 50.1331 | PASS | 10.9091 | PASS | 10809.0947 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 50.2378 | PASS | 10.9056 | PASS | 10805.584 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 50.012 | PASS | 10.909 | PASS | 10808.9757 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784141 [GEN-2024-239 345.00] CKT 1 | 50.2202 | PASS | 10.9068 | PASS | 10806.7638 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784530 [GEN-2024-252 345.00] CKT 3 | 50.2017 | PASS | 10.9084 | PASS | 10808.3654 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784531 [GEN-2024-252 345.00] CKT 1 | 50.0926 | PASS | 10.9054 | PASS | 10805.448 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 50.1804 | PASS | 10.9094 | PASS | 10809.4452 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 50.1911 | PASS | 10.9094 | PASS | 10809.4183 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 50.1839 | PASS | 10.9094 | PASS | 10809.3792 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 50.1876 | PASS | 10.9094 | PASS | 10809.4314 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 50.1875 | PASS | 10.9094 | PASS | 10809.4319 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 50.1872 | PASS | 10.9094 | PASS | 10809.4455 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 50.1283 | PASS | 10.9089 | PASS | 10808.9292 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 | 50.1886 | PASS | 10.9102 | PASS | 10810.2391 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 | 50.1886 | PASS | 10.9102 | PASS | 10810.2391 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 3 | 50.1886 | PASS | 10.9102 | PASS | 10810.2391 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 50.0965 | PASS | 10.9096 | PASS | 10809.611 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 50.1774 | PASS | 10.9092 | PASS | 10809.1653 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 2 | 50.1774 | PASS | 10.9092 | PASS | 10809.1653 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 3 | 50.1832 | PASS | 10.9093 | PASS | 10809.3417 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 50.1795 | PASS | 10.9095 | PASS | 10809.4698 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 2 | 50.1786 | PASS | 10.9095 | PASS | 10809.477 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 50.1643 | PASS | 10.9098 | PASS | 10809.7606 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 50.1642 | PASS | 10.9098 | PASS | 10809.7894 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515008 [KINZE 4 138.00] TO BUS 515181 [UNVRSTY4 138.00] CKT 1 | 50.1381 | PASS | 10.91 | PASS | 10809.9553 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515009 [MCELROY4 138.00] TO BUS 515011 [STILWTR4 138.00] CKT 1 | 50.1341 | PASS | 10.9101 | PASS | 10810.0509 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515009 [MCELROY4 138.00] TO BUS 515181 [UNVRSTY4 138.00] CKT 1 | 50.1374 | PASS | 10.91 | PASS | 10810.0228 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 49.8863 | PASS | 10.9098 | PASS | 10809.783 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 50.0664 | PASS | 10.9099 | PASS | 10809.8809 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515033 [CUSHING4 138.00] TO BUS 515039 [PAYNESB4 138.00] CKT 1 | 50.1671 | PASS | 10.9096 | PASS | 10809.5986 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515039 [PAYNESB4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 50.1668 | PASS | 10.9096 | PASS | 10809.5773 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 50.1607 | PASS | 10.9122 | PASS | 10812.1863 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 786601 [GEN-2024-321 345.00] CKT 1 | 50.2056 | PASS | 10.905 | PASS | 10804.9858 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 50.1779 | PASS | 10.9096 | PASS | 10809.6369 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 50.1674 | PASS | 10.9101 | PASS | 10810.1446 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 50.1761 | PASS | 10.9108 | PASS | 10810.7523 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 50.1653 | PASS | 10.9094 | PASS | 10809.3933 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 762823 [GEN-2018-048 345.00] CKT 1 | 50.2076 | PASS | 10.908 | PASS | 10808.0319 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 50.1532 | PASS | 10.9109 | PASS | 10810.9109 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 50.1524 | PASS | 10.9109 | PASS | 10810.9391 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515400 [DMANCRK4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 50.1873 | PASS | 10.9094 | PASS | 10809.416 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515403 [FNTANTP4 138.00] TO BUS 515542 [CWBOYHT4 138.00] CKT 1 | 50.1887 | PASS | 10.9096 | PASS | 10809.5633 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 50.1978 | PASS | 10.9087 | PASS | 10808.7387 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 50.1572 | PASS | 10.9109 | PASS | 10810.9308 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 50.1571 | PASS | 10.9109 | PASS | 10810.9336 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 50.2121 | PASS | 10.9071 | PASS | 10807.1209 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 50.1948 | PASS | 10.9085 | PASS | 10808.537 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515477 [CHSHLMV7 345.00] CKT 1 | 50.1914 | PASS | 10.9092 | PASS | 10809.2441 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515543 [RENFROW7 345.00] CKT 1 | 49.1949 | PASS | 10.9278 | PASS | 10827.8305 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 47.4886 | PASS | 10.9102 | PASS | 10810.214 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 50.2293 | PASS | 10.907 | PASS | 10807.0198 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 50.2014 | PASS | 10.9084 | PASS | 10808.3831 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 50.033 | PASS | 10.9062 | PASS | 10806.2098 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515514 [KNIPE 4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 50.146 | PASS | 10.9096 | PASS | 10809.6416 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515514 [KNIPE 4 138.00] TO BUS 515675 [TRYON 4 138.00] CKT 1 | 50.1461 | PASS | 10.9097 | PASS | 10809.6641 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 50.1832 | PASS | 10.9097 | PASS | 10809.6693 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 49.2543 | PASS | 10.8891 | PASS | 10789.0645 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515546 [GRANTCO4 138.00] CKT 1 | 50.1906 | PASS | 10.9095 | PASS | 10809.4627 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 50.1902 | PASS | 10.9095 | PASS | 10809.4902 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 520409 [WFEC_RNFRO4 138.00] CKT 1 | 50.1342 | PASS | 10.9095 | PASS | 10809.4784 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515621 [OPENSKY7 345.00] CKT 1 | 46.5354 | PASS | 10.9246 | PASS | 10824.6407 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515688 [FRNTWND7 345.00] CKT 1 | 50.1942 | PASS | 10.9103 | PASS | 10810.2608 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 529200 [OMCDLEC7 345.00] CKT 1 | 49.1428 | PASS | 10.9119 | PASS | 10811.9258 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 50.1619 | PASS | 10.9158 | PASS | 10815.8484 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 786991 [GEN-2024-334 345.00] CKT 1 | 49.2681 | PASS | 10.9109 | PASS | 10810.8823 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515600 [KNGFSHR7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 50.2245 | PASS | 10.9066 | PASS | 10806.5714 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515605 [CANADN7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 50.2027 | PASS | 10.9084 | PASS | 10808.3711 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515621 [OPENSKY7 345.00] TO BUS 532837 [G15052_T 345.00] CKT 1 | 46.462 | PASS | 10.9287 | PASS | 10828.7168 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 516363 [ARMADILLO_HV 138.00] CKT 1 | 50.1919 | PASS | 10.9092 | PASS | 10809.1693 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT 1 | 50.2062 | PASS | 10.9085 | PASS | 10808.4553 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765470 [GEN-2021-018 345.00] CKT 1 | 50.3064 | PASS | 10.9084 | PASS | 10808.3863 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765480 [GEN-2021-019 345.00] CKT 1 | 50.2183 | PASS | 10.9071 | PASS | 10807.1228 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515974 [GEN-2015-066 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 50.2941 | PASS | 10.897 | PASS | 10796.9874 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 588190 [GEN-2016-128 345.00] CKT 1 | 50.2065 | PASS | 10.9084 | PASS | 10808.3545 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516010 [PINTAIL7 345.00] TO BUS 516019 [KINGWD 7 345.00] CKT 1 | 50.2122 | PASS | 10.909 | PASS | 10808.97 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 50.2222 | PASS | 10.9071 | PASS | 10807.0795 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 50.1959 | PASS | 10.9089 | PASS | 10808.9198 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516066 [FRNT2WD7 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 50.1666 | PASS | 10.913 | PASS | 10813.0015 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 777361 [GEN-2024-013 345.00] CKT 1 | 50.1772 | PASS | 10.903 | PASS | 10803.0438 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516192 [WAGNWTIE7 345.00] TO BUS 516198 [WAGNWL7 345.00] CKT 1 | 50.2253 | PASS | 10.9064 | PASS | 10806.4338 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516192 [WAGNWTIE7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 50.2546 | PASS | 10.904 | PASS | 10803.9807 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520442 [SHIDWFC4 138.00] TO BUS 520443 [WEBBCTY4 138.00] CKT 1 | 50.1886 | PASS | 10.9094 | PASS | 10809.407 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520461 [GARBER 4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 50.1895 | PASS | 10.9094 | PASS | 10809.4406 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529241 [OMMORANT 69.00] TO BUS 529242 [OMHUFFYT 69.00] CKT 1 | 50.0963 | PASS | 10.9096 | PASS | 10809.583 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529248 [OMPECANT 69.00] TO BUS 529249 [OMWW 69.00] CKT 1 | 50.1431 | PASS | 10.9094 | PASS | 10809.4219 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532780 [CANEYRV7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 50.026 | PASS | 10.9097 | PASS | 10809.7422 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 49.8611 | PASS | 10.9066 | PASS | 10806.5542 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 50.1 | PASS | 10.9095 | PASS | 10809.5033 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 50.0249 | PASS | 10.9109 | PASS | 10810.8739 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 49.9074 | PASS | 10.9116 | PASS | 10811.559 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 50.0226 | PASS | 10.9104 | PASS | 10810.4005 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532837 [G15052_T 345.00] CKT 1 | 46.2831 | PASS | 10.8908 | PASS | 10790.7935 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 49.7491 | PASS | 10.9166 | PASS | 10816.62 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 50.1422 | PASS | 10.9109 | PASS | 10810.9328 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 50.1837 | PASS | 10.9101 | PASS | 10810.0881 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 50.1578 | PASS | 10.91 | PASS | 10810.0303 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 49.2515 | PASS | 10.8889 | PASS | 10788.8635 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532800 [LATHAMS7 345.00] TO BUS 532801 [ELKRVR17 345.00] CKT 1 | 50.1825 | PASS | 10.91 | PASS | 10810.0055 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532837 [G15052_T 345.00] TO BUS 562900 [G15052_1 345.00] CKT 1 | 50.1568 | PASS | 10.9126 | PASS | 10812.5866 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 50.1822 | PASS | 10.9092 | PASS | 10809.1833 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 50.1881 | PASS | 10.9091 | PASS | 10809.1361 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533068 [STEARMN4 138.00] CKT 1 | 50.1894 | PASS | 10.9094 | PASS | 10809.4133 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533062 [ROSEHIL4 138.00] TO BUS 533068 [STEARMN4 138.00] CKT 1 | 50.1871 | PASS | 10.9093 | PASS | 10809.2605 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762342 [GEN-2017-178 345.00] CKT 1 | 50.2032 | PASS | 10.9089 | PASS | 10808.9167 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763065 [GEN-2018-071 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 50.2097 | PASS | 10.9104 | PASS | 10810.4466 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763417 [GEN-2018-128 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 50.193 | PASS | 10.9097 | PASS | 10809.7024 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 770500 [G22-176-TAP 345.00] TO BUS 770501 [GEN-2022-176 345.00] CKT 1 | 50.1839 | PASS | 10.9107 | PASS | 10810.6994 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 778650 [G24-056-TAP 138.00] TO BUS 778651 [GEN-2024-056 138.00] CKT 0 | 50.2011 | PASS | 10.9092 | PASS | 10809.2146 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 782100 [G24-171-TAP 345.00] TO BUS 782101 [GEN-2024-171 345.00] CKT 1 | 50.1805 | PASS | 10.9111 | PASS | 10811.1031 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784020 [G24-235-TAP 345.00] TO BUS 784021 [GEN-2024-235 345.00] CKT 1 | 50.1493 | PASS | 10.9126 | PASS | 10812.6453 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786991 [GEN-2024-334 345.00] TO BUS 786998 [G24-334-C1 345.00] CKT 2 | 49.7413 | PASS | 10.9101 | PASS | 10810.0948 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786991 [GEN-2024-334 345.00] TO BUS 786999 [G24-334-C2 345.00] CKT 2 | 49.7413 | PASS | 10.9101 | PASS | 10810.0946 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 300686 [4WOODY 138.00] CKT 1 | 50.1815 | PASS | 10.9095 | PASS | 10809.5358 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 300889 [2BRIISTOW 69.00] CKT 2 | 50.1875 | PASS | 10.9095 | PASS | 10809.5192 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 910314 [GI103_GEN1 20.00] CKT 1 | 50.1295 | PASS | 10.909 | PASS | 10809.0315 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 910514 [GI105_GEN1 20.00] CKT 1 | 49.4174 | PASS | 10.9099 | PASS | 10809.8682 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 300929 [2FAIRFAX 69.00] CKT 1 | 50.1876 | PASS | 10.9095 | PASS | 10809.5238 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 300929 [2FAIRFAX 69.00] CKT 2 | 50.189 | PASS | 10.9095 | PASS | 10809.4528 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 300844 [4RAMSEY 138.00] CKT 1 | 50.1894 | PASS | 10.9095 | PASS | 10809.4764 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301413 [2STILWTRKAMO 69.00] CKT 1 | 50.1887 | PASS | 10.9094 | PASS | 10809.4405 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301413 [2STILWTRKAMO 69.00] CKT 2 | 50.1887 | PASS | 10.9094 | PASS | 10809.4405 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301603 [4RPLY 138.00] CKT 1 | 50.1897 | PASS | 10.9094 | PASS | 10809.4307 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 512731 [NORTHTP4 138.00] CKT 1 | 50.1892 | PASS | 10.9095 | PASS | 10809.5175 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300145 [4FISHER 138.00] TO BUS 300931 [2FISHER 69.00] CKT 2 | 50.1877 | PASS | 10.9094 | PASS | 10809.3913 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300943 [2SILVCTY 69.00] TO BUS 300936 [2MANFORD 69.00] CKT 1 | 50.1884 | PASS | 10.9094 | PASS | 10809.4454 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300943 [2SILVCTY 69.00] TO BUS 301630 [2SILVCTYLD 69.00] CKT 1 | 50.1898 | PASS | 10.9093 | PASS | 10809.2759 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300943 [2SILVCTY 69.00] TO BUS 301631 [2SILVCTYTP 69.00] CKT 1 | 50.1878 | PASS | 10.9097 | PASS | 10809.6609 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300996 [4JAVINE 138.00] TO BUS 301339 [4SFORKKTP 138.00] CKT 1 | 50.1385 | PASS | 10.9084 | PASS | 10808.3572 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 301369 [4REMNGTON 138.00] TO BUS 301379 [4OSAGEWIND 138.00] CKT 1 | 50.1854 | PASS | 10.91 | PASS | 10810.0122 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 505609 [KEYSTON5 161.00] TO BUS 505610 [KEYSTON4 138.00] CKT 1 | 50.1648 | PASS | 10.9094 | PASS | 10809.3734 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509739 [CARSN-T4 138.00] TO BUS 509724 [36&OLY-4 138.00] CKT 1 | 50.1384 | PASS | 10.9101 | PASS | 10810.0524 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509739 [CARSN-T4 138.00] TO BUS 509740 [UNIONAV4 138.00] CKT 1 | 50.1876 | PASS | 10.9095 | PASS | 10809.4974 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 50.0685 | PASS | 10.9201 | PASS | 10820.104 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140 345.00] CKT 1 | 50.1992 | PASS | 10.909 | PASS | 10809.034 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509746 [DENVTAP4 138.00] TO BUS 509743 [DENVR-E4 138.00] CKT 1 | 50.1891 | PASS | 10.9095 | PASS | 10809.5269 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509746 [DENVTAP4 138.00] TO BUS 509822 [W.ED.-E4 138.00] CKT 1 | 50.1889 | PASS | 10.9092 | PASS | 10809.1894 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] CKT 1 | 49.9766 | PASS | 10.9096 | PASS | 10809.5642 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509758 [PRATTV-4 138.00] TO BUS 515242 [BLUEBEL4 138.00] CKT 1 | 50.174 | PASS | 10.9094 | PASS | 10809.4294 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] CKT 1 | 50.1827 | PASS | 10.9091 | PASS | 10809.0762 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] CKT 1 | 50.1827 | PASS | 10.909 | PASS | 10809.0471 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509775 [136YALE4 138.00] CKT 1 | 50.1884 | PASS | 10.9097 | PASS | 10809.6637 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509814 [S HILLWT4 138.00] CKT 1 | 50.1869 | PASS | 10.9095 | PASS | 10809.4714 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509849 [ORU ETP4 138.00] CKT 1 | 50.1879 | PASS | 10.9099 | PASS | 10809.9183 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509850 [OAKSETP4 138.00] CKT 1 | 50.1866 | PASS | 10.9095 | PASS | 10809.4793 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509853 [ORU-WTP4 138.00] CKT 1 | 50.1874 | PASS | 10.9099 | PASS | 10809.8597 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 510898 [OKMULGE4 138.00] CKT 1 | 50.1863 | PASS | 10.9095 | PASS | 10809.5118 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 510904 [EXP_OKM4 138.00] CKT 1 | 50.1863 | PASS | 10.9095 | PASS | 10809.5093 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 511842 [RSS1-1 24.00] CKT 1 | 50.1259 | PASS | 10.9086 | PASS | 10808.5705 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 511843 [RSS2-1 22.00] CKT 1 | 50.112 | PASS | 10.9086 | PASS | 10808.5734 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 515473 [EXPGLNT4 138.00] CKT 1 | 50.1798 | PASS | 10.9101 | PASS | 10810.1106 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 511844 [RSS NG3 13.8.00] CKT 1 | 50.166 | PASS | 10.9089 | PASS | 10808.8728 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509724 [36&OLY-4 138.00] CKT 1 | 50.138 | PASS | 10.9104 | PASS | 10810.4414 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509756 [CARSN-S4 138.00] CKT 1 | 50.1862 | PASS | 10.9096 | PASS | 10809.6105 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509800 [36LEWIS4 138.00] CKT 1 | 50.1826 | PASS | 10.91 | PASS | 10809.9905 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509814 [S HILLWT4 138.00] CKT 1 | 50.1871 | PASS | 10.9094 | PASS | 10809.4467 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509850 [OAKSETP4 138.00] CKT 1 | 50.1865 | PASS | 10.9095 | PASS | 10809.4651 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 511854 [TPS2-1 14.4.00] CKT 1 | 50.1557 | PASS | 10.9092 | PASS | 10809.1583 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 511858 [TPS4-1 14.4.00] CKT 1 | 50.1558 | PASS | 10.9092 | PASS | 10809.1612 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 762625 [GEN-2018-027 138.00] CKT 1 | 50.1943 | PASS | 10.9091 | PASS | 10809.0775 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 999996 [ZSWSH_999996 138.00] CKT 1 | 50.1926 | PASS | 10.9094 | PASS | 10809.4196 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509789 [T.P.S.-2 69.00] CKT 1 | 50.1888 | PASS | 10.9095 | PASS | 10809.4553 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 50.19 | PASS | 10.9094 | PASS | 10809.3976 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 50.1904 | PASS | 10.9094 | PASS | 10809.4284 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 50.1704 | PASS | 10.9115 | PASS | 10811.4708 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 50.1906 | PASS | 10.9094 | PASS | 10809.4343 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 50.1904 | PASS | 10.9094 | PASS | 10809.431 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 50.1887 | PASS | 10.9095 | PASS | 10809.5424 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] CKT 2 | 50.1887 | PASS | 10.9095 | PASS | 10809.544 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] CKT 3 | 50.1886 | PASS | 10.9096 | PASS | 10809.5553 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509821 [HWY20-T4 138.00] TO BUS 509897 [WLDCT_HIL4 138.00] CKT 1 | 50.1886 | PASS | 10.9094 | PASS | 10809.4196 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.00] CKT 1 | 50.1612 | PASS | 10.9091 | PASS | 10809.1251 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.00] CKT 1 | 50.1612 | PASS | 10.9091 | PASS | 10809.1251 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.00] CKT 1 | 50.1649 | PASS | 10.9088 | PASS | 10808.8198 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.00] CKT 1 | 50.1572 | PASS | 10.909 | PASS | 10809.0243 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.00] CKT 1 | 50.166 | PASS | 10.9091 | PASS | 10809.1444 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.00] CKT 1 | 50.1654 | PASS | 10.9092 | PASS | 10809.1751 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.00] CKT 1 | 50.1572 | PASS | 10.909 | PASS | 10809.0243 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.00] CKT 1 | 50.166 | PASS | 10.9091 | PASS | 10809.1444 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.00] CKT 1 | 50.1654 | PASS | 10.9092 | PASS | 10809.1751 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509839 [CDC-ET 4 138.00] TO BUS 509714 [CIP 4 138.00] CKT 1 | 50.189 | PASS | 10.9095 | PASS | 10809.4583 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509839 [CDC-ET 4 138.00] TO BUS 509887 [OWAS88_4 138.00] CKT 1 | 50.1378 | PASS | 10.9095 | PASS | 10809.4566 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509842 [CDC-WT 4 138.00] TO BUS 509784 [A.A.---4 138.00] CKT 1 | 50.1674 | PASS | 10.9092 | PASS | 10809.2364 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509842 [CDC-WT 4 138.00] TO BUS 509840 [WHIRLPO4 138.00] CKT 1 | 50.189 | PASS | 10.9094 | PASS | 10809.402 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509844 [OWASOTP4 138.00] TO BUS 509726 [OWASO1_4 138.00] CKT 1 | 50.1889 | PASS | 10.9092 | PASS | 10809.1818 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509844 [OWASOTP4 138.00] TO BUS 509860 [OWAS1094 138.00] CKT 1 | 50.104 | PASS | 10.9099 | PASS | 10809.915 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] CKT 1 | 50.0887 | PASS | 10.9089 | PASS | 10808.9307 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 50.1419 | PASS | 10.91 | PASS | 10809.9666 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509900 [46ST-TP-4 138.00] TO BUS 509837 [46ST--E4 138.00] CKT 1 | 50.1884 | PASS | 10.9091 | PASS | 10809.0559 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509900 [46ST-TP-4 138.00] TO BUS 509863 [PPTAP 4 138.00] CKT 1 | 50.1676 | PASS | 10.9093 | PASS | 10809.302 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509904 [AVERYDR4 138.00] TO BUS 509903 [AVERYDR2 69.00] CKT 1 | 50.1842 | PASS | 10.9094 | PASS | 10809.3683 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509908 [SKIATKTP4 138.00] TO BUS 509884 [SKIATOK4 138.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.3825 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509908 [SKIATKTP4 138.00] TO BUS 510388 [BARNSAL4 138.00] CKT 1 | 50.1799 | PASS | 10.9087 | PASS | 10808.7269 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 50.0399 | PASS | 10.9101 | PASS | 10810.1412 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510379 [DELWARE4 138.00] CKT 1 | 50.1874 | PASS | 10.9092 | PASS | 10809.236 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510382 [WPAWHSK4 138.00] TO BUS 510412 [WESTERNWALL4 138.00] CKT 1 | 50.144 | PASS | 10.9102 | PASS | 10810.17 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 509843 [OWASO2_4 138.00] CKT 1 | 50.1856 | PASS | 10.9096 | PASS | 10809.6265 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 509854 [VERDIGS4 138.00] CKT 1 | 50.1855 | PASS | 10.9097 | PASS | 10809.6787 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 509860 [OWAS1094 138.00] CKT 1 | 50.1053 | PASS | 10.9104 | PASS | 10810.4207 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 510384 [WATOVA 4 138.00] CKT 1 | 50.1807 | PASS | 10.9101 | PASS | 10810.0759 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 510385 [RICE CK4 138.00] CKT 1 | 50.1737 | PASS | 10.9106 | PASS | 10810.6417 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 510413 [HAWTHRN4 138.00] CKT 1 | 50.1783 | PASS | 10.91 | PASS | 10809.9862 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511836 [NES1-1 14.4.00] CKT 1 | 50.164 | PASS | 10.9096 | PASS | 10809.5905 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511837 [NES1-1A 18.00] CKT 1 | 50.1605 | PASS | 10.9097 | PASS | 10809.6676 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511838 [NES1-1B 18.00] CKT 1 | 50.1608 | PASS | 10.9097 | PASS | 10809.6673 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511839 [NES2-1 22.00] CKT 1 | 50.0763 | PASS | 10.9113 | PASS | 10811.3418 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 513124 [OOLOGAH 4 138.00] CKT 1 | 50.187 | PASS | 10.9101 | PASS | 10810.089 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | 50.1866 | PASS | 10.9084 | PASS | 10808.3572 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 510925 [KIOWA 7 345.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.4216 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 514809 [JOHNCO 7 345.00] CKT 1 | 50.1918 | PASS | 10.9096 | PASS | 10809.5525 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 515422 [C-RIVER7 345.00] CKT 1 | 50.1641 | PASS | 10.9117 | PASS | 10811.6846 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 763131 [GEN-2018-082 345.00] CKT 1 | 50.199 | PASS | 10.9086 | PASS | 10808.6195 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511501 [TUTTLE4 138.00] CKT 1 | 50.1772 | PASS | 10.9093 | PASS | 10809.3215 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511576 [CEMRD_TP4 138.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.4233 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511878 [G16133_765TN 765.00] TO BUS 511879 [G16133_765R1 765.00] CKT 1 | 50.1423 | PASS | 10.9067 | PASS | 10806.7118 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] CKT 1 | 48.8566 | PASS | 10.9002 | PASS | 10800.1802 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512876 [OSAGEK2 69.00] TO BUS 512875 [PRUEK2 69.00] CKT 1 | 50.181 | PASS | 10.9094 | PASS | 10809.3618 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512876 [OSAGEK2 69.00] TO BUS 512877 [CLEVDSTK2 69.00] CKT 1 | 50.1896 | PASS | 10.9092 | PASS | 10809.2396 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 513098 [HALLETTAP 2 69.00] TO BUS 512675 [PAWNEGR2 69.00] CKT 1 | 50.1896 | PASS | 10.9095 | PASS | 10809.4637 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 513098 [HALLETTAP 2 69.00] TO BUS 512877 [CLEVDSTK2 69.00] CKT 1 | 50.1895 | PASS | 10.9095 | PASS | 10809.5219 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514706 [COWCRK 4 138.00] CKT 2 | 50.1872 | PASS | 10.9095 | PASS | 10809.451 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514715 [WOODRNG7 345.00] CKT 2 | 49.8761 | PASS | 10.9098 | PASS | 10809.8212 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514718 [VANCE 2 69.00] CKT 1 | 50.1877 | PASS | 10.9095 | PASS | 10809.4691 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514722 [CLEVETP2 69.00] CKT 1 | 50.1885 | PASS | 10.9094 | PASS | 10809.4176 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514727 [ENID 2 69.00] CKT 2 | 50.1896 | PASS | 10.9094 | PASS | 10809.4243 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 515456 [CHSTNTT2 69.00] CKT 1 | 50.1897 | PASS | 10.9094 | PASS | 10809.4237 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 50.1887 | PASS | 10.9095 | PASS | 10809.4561 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 514743 [OSAGE 4 138.00] CKT 3 | 50.1278 | PASS | 10.9095 | PASS | 10809.4965 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 514743 [OSAGE 4 138.00] CKT 4 | 50.1288 | PASS | 10.9095 | PASS | 10809.4952 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514745 [CHERPLT2 69.00] TO BUS 514744 [CHILOCO2 69.00] CKT 1 | 50.1859 | PASS | 10.9094 | PASS | 10809.415 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514745 [CHERPLT2 69.00] TO BUS 514746 [CHERKPL2 69.00] CKT 1 | 50.189 | PASS | 10.9094 | PASS | 10809.4225 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 515581 [COYOTE 4 138.00] CKT 1 | 50.187 | PASS | 10.9096 | PASS | 10809.6236 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 514756 [CHIKASI2 69.00] CKT 2 | 50.1859 | PASS | 10.9094 | PASS | 10809.3989 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514764 [NWKRKAT4 138.00] TO BUS 514759 [NEWKIRK4 138.00] CKT 1 | 50.1386 | PASS | 10.9117 | PASS | 10811.7112 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514764 [NWKRKAT4 138.00] TO BUS 521012 [NEWKIR-WFEC4 138.00] CKT 1 | 50.1878 | PASS | 10.9094 | PASS | 10809.4267 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514774 [HENESEY4 138.00] TO BUS 520535 [BULFTTP4 138.00] CKT 1 | 50.0708 | PASS | 10.9095 | PASS | 10809.492 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514790 [IMO 4 138.00] TO BUS 514734 [GLENWD 4 138.00] CKT 1 | 50.189 | PASS | 10.9094 | PASS | 10809.4168 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514790 [IMO 4 138.00] TO BUS 514789 [MENOTAP4 138.00] CKT 1 | 50.1206 | PASS | 10.9094 | PASS | 10809.3978 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514790 [IMO 4 138.00] TO BUS 514721 [IMO 2 69.00] CKT 1 | 50.1892 | PASS | 10.9095 | PASS | 10809.454 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514800 [BRRDTP 2 69.00] TO BUS 514766 [ORLANDO2 69.00] CKT 1 | 50.1891 | PASS | 10.9094 | PASS | 10809.4141 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514800 [BRRDTP 2 69.00] TO BUS 514797 [BRONRD 2 69.00] CKT 1 | 50.1883 | PASS | 10.9094 | PASS | 10809.4304 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514805 [SOONER1G 22.00] CKT 1 | 47.643 | PASS | 10.9182 | PASS | 10818.1964 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514803 [SOONER 7 345.00] CKT 5 | 44.889 | PASS | 10.9255 | PASS | 10825.5047 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 514806 [SOONER2G 20.00] CKT 1 | 43.2287 | PASS | 10.9054 | PASS | 10805.4104 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 514642 [BRCKWND4 138.00] CKT 1 | 50.2006 | PASS | 10.9083 | PASS | 10808.3379 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 514701 [BUNCHCK4 138.00] CKT 1 | 50.1863 | PASS | 10.9097 | PASS | 10809.7358 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 515383 [ENIDINT4 138.00] CKT 1 | 50.1858 | PASS | 10.9095 | PASS | 10809.4867 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 515962 [OMEGA 4 138.00] CKT 1 | 50.1897 | PASS | 10.9094 | PASS | 10809.3694 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514818 [ELRENO 2 69.00] CKT 5 | 50.1893 | PASS | 10.9094 | PASS | 10809.4158 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514821 [JENSEN 4 138.00] CKT 1 | 50.1896 | PASS | 10.9092 | PASS | 10809.2468 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514825 [KAYWIND7 345.00] TO BUS 515622 [KAYWND11 34.5.00] CKT 1 | 50.1777 | PASS | 10.9102 | PASS | 10810.1775 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514825 [KAYWIND7 345.00] TO BUS 515623 [KAYWND12 34.5.00] CKT 1 | 50.1777 | PASS | 10.9102 | PASS | 10810.1771 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514829 [PINE ST4 138.00] TO BUS 514830 [FITZGRD4 138.00] CKT 1 | 50.1615 | PASS | 10.9101 | PASS | 10810.1335 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514834 [KETCH 4 138.00] TO BUS 514833 [DANFRTH4 138.00] CKT 1 | 50.1804 | PASS | 10.9094 | PASS | 10809.4211 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514834 [KETCH 4 138.00] TO BUS 515468 [FAIRFLD4 138.00] CKT 1 | 50.1886 | PASS | 10.9094 | PASS | 10809.4117 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514851 [QUAILCK4 138.00] TO BUS 514850 [SKYLINE4 138.00] CKT 1 | 50.1832 | PASS | 10.9094 | PASS | 10809.4395 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514852 [SLVRLAK4 138.00] TO BUS 514853 [DVISION4 138.00] CKT 1 | 50.1717 | PASS | 10.9093 | PASS | 10809.3347 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514862 [RICHRDS4 138.00] TO BUS 514853 [DVISION4 138.00] CKT 1 | 50.1794 | PASS | 10.9094 | PASS | 10809.3987 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514863 [HAYMAKR4 138.00] TO BUS 514853 [DVISION4 138.00] CKT 1 | 50.1895 | PASS | 10.9093 | PASS | 10809.3433 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 2 | 50.1669 | PASS | 10.9097 | PASS | 10809.6754 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 3 | 50.1678 | PASS | 10.9097 | PASS | 10809.6674 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 4 | 50.1679 | PASS | 10.9097 | PASS | 10809.666 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514882 [SPGCK1&2 13.8.00] CKT 1 | 50.0373 | PASS | 10.9086 | PASS | 10808.6295 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514883 [SPGCK3&4 13.8.00] CKT 1 | 50.0404 | PASS | 10.9084 | PASS | 10808.4346 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514894 [CZECHAL4 138.00] TO BUS 514893 [XEROX 4 138.00] CKT 1 | 50.1755 | PASS | 10.9094 | PASS | 10809.4476 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 515481 [STHLAKE4 138.00] CKT 1 | 50.1736 | PASS | 10.9095 | PASS | 10809.4687 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 50.1718 | PASS | 10.9098 | PASS | 10809.7921 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 2 | 50.165 | PASS | 10.9094 | PASS | 10809.352 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 300136 [4MEMORALT 138.00] CKT 1 | 50.1727 | PASS | 10.91 | PASS | 10810.0461 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 50.1693 | PASS | 10.9093 | PASS | 10809.2827 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 2 | 50.1892 | PASS | 10.9095 | PASS | 10809.4743 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 3 | 50.1893 | PASS | 10.9096 | PASS | 10809.5578 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 4 | 50.1892 | PASS | 10.9096 | PASS | 10809.5907 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514899 [REDBUD1S 18.00] CKT 1 | 50.125 | PASS | 10.9071 | PASS | 10807.1385 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514900 [REDBUD2S 18.00] CKT 1 | 50.125 | PASS | 10.9071 | PASS | 10807.1417 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514905 [REDBUD3S 18.00] CKT 1 | 50.1246 | PASS | 10.9072 | PASS | 10807.1701 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514940 [REDBUD4S 18.00] CKT 1 | 50.125 | PASS | 10.9071 | PASS | 10807.1385 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 514933 [DRAPER 4 138.00] CKT 2 | 50.1899 | PASS | 10.9094 | PASS | 10809.4322 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 514933 [DRAPER 4 138.00] CKT 3 | 50.1899 | PASS | 10.9094 | PASS | 10809.4341 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 514933 [DRAPER 4 138.00] CKT 4 | 50.1899 | PASS | 10.9094 | PASS | 10809.4341 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515008 [KINZE 4 138.00] TO BUS 512710 [KINZEGR4 138.00] CKT 1 | 50.1674 | PASS | 10.9113 | PASS | 10811.3288 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515008 [KINZE 4 138.00] TO BUS 516212 [COYLE 4 138.00] CKT 1 | 50.1617 | PASS | 10.9101 | PASS | 10810.0582 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515033 [CUSHING4 138.00] TO BUS 515417 [GRNWOOD4 138.00] CKT 1 | 50.1782 | PASS | 10.9095 | PASS | 10809.4616 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515033 [CUSHING4 138.00] TO BUS 515032 [CUSHING2 69.00] CKT 3 | 50.1881 | PASS | 10.9095 | PASS | 10809.4839 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515040 [SEMINL1G 20.9.00] CKT 1 | 50.1872 | PASS | 10.9064 | PASS | 10806.4476 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 1 | 50.1885 | PASS | 10.9095 | PASS | 10809.4512 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 2 | 50.1888 | PASS | 10.9094 | PASS | 10809.4439 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515531 [VANOSTP4 138.00] CKT 1 | 50.1898 | PASS | 10.9094 | PASS | 10809.4321 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515977 [LKKONWA4 138.00] CKT 1 | 50.1896 | PASS | 10.9095 | PASS | 10809.4646 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 775520 [G23-177-TAP 138.00] CKT 1 | 50.19 | PASS | 10.9094 | PASS | 10809.414 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 50.1885 | PASS | 10.9094 | PASS | 10809.423 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 2 | 50.188 | PASS | 10.9094 | PASS | 10809.4238 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 3 | 50.1885 | PASS | 10.9094 | PASS | 10809.423 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515041 [SEMINL2G 17.1.00] CKT 1 | 50.1923 | PASS | 10.9065 | PASS | 10806.4691 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515042 [SEMINL3G 20.9.00] CKT 1 | 50.1834 | PASS | 10.9065 | PASS | 10806.5104 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515223 [MUSKOG4G 18.00] CKT 1 | 50.1732 | PASS | 10.9083 | PASS | 10808.3299 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515225 [MUSKOG5G 18.00] CKT 1 | 50.1745 | PASS | 10.9083 | PASS | 10808.2652 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515226 [MUSKOG6G 24.00] CKT 1 | 50.1669 | PASS | 10.9083 | PASS | 10808.2808 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | 50.1798 | PASS | 10.9094 | PASS | 10809.4431 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 2 | 50.1803 | PASS | 10.9096 | PASS | 10809.5639 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 516091 [OKTAHA 7 345.00] CKT 1 | 50.1803 | PASS | 10.9104 | PASS | 10810.3594 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515233 [PECANCK4 138.00] TO BUS 515249 [BEGGS 4 138.00] CKT 1 | 50.1784 | PASS | 10.9094 | PASS | 10809.4341 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515233 [PECANCK4 138.00] TO BUS 515235 [PECANCK7 345.00] CKT 4 | 50.1784 | PASS | 10.9094 | PASS | 10809.4122 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515228 [5TRIBES5 161.00] CKT 1 | 50.1864 | PASS | 10.9098 | PASS | 10809.7535 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515230 [AGENCY 5 161.00] CKT 1 | 50.1872 | PASS | 10.9097 | PASS | 10809.6968 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 50.1876 | PASS | 10.9096 | PASS | 10809.5997 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515235 [PECANCK7 345.00] CKT 2 | 50.1864 | PASS | 10.9098 | PASS | 10809.7551 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515373 [LBRTYLK4 138.00] TO BUS 514831 [WATRLOO4 138.00] CKT 1 | 50.1757 | PASS | 10.9094 | PASS | 10809.4304 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515374 [CHISHOM4 138.00] TO BUS 514850 [SKYLINE4 138.00] CKT 1 | 50.1816 | PASS | 10.9094 | PASS | 10809.4125 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515374 [CHISHOM4 138.00] TO BUS 515468 [FAIRFLD4 138.00] CKT 1 | 50.1886 | PASS | 10.9094 | PASS | 10809.421 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 50.1524 | PASS | 10.912 | PASS | 10812.0467 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 50.1524 | PASS | 10.912 | PASS | 10812.0468 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 50.2202 | PASS | 10.9067 | PASS | 10806.688 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 50.1533 | PASS | 10.9089 | PASS | 10808.9177 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 50.1827 | PASS | 10.9094 | PASS | 10809.3926 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 50.1827 | PASS | 10.9094 | PASS | 10809.393 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 50.2067 | PASS | 10.9073 | PASS | 10807.328 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 50.1942 | PASS | 10.9084 | PASS | 10808.4475 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 50.2117 | PASS | 10.9072 | PASS | 10807.1671 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 2 | 50.1876 | PASS | 10.9095 | PASS | 10809.5187 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 3 | 50.1875 | PASS | 10.9095 | PASS | 10809.5234 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515377 [CRESENT4 138.00] TO BUS 516100 [HORIZON4 138.00] CKT 1 | 50.1994 | PASS | 10.9083 | PASS | 10808.3436 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515377 [CRESENT4 138.00] TO BUS 521073 [TWNLKSW4 138.00] CKT 1 | 50.1906 | PASS | 10.9094 | PASS | 10809.3865 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515403 [FNTANTP4 138.00] TO BUS 515635 [BLLNGTP4 138.00] CKT 1 | 50.1872 | PASS | 10.9096 | PASS | 10809.642 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515444 [MCNOWND7 345.00] TO BUS 515443 [MNCOWND1 34.5.00] CKT 1 | 50.2223 | PASS | 10.9066 | PASS | 10806.5797 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515450 [CRSRDW21 34.5.00] CKT 2 | 50.1939 | PASS | 10.909 | PASS | 10809.018 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515449 [CRSRDW11 34.5.00] CKT 1 | 50.1932 | PASS | 10.9091 | PASS | 10809.0887 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515461 [RNDBARN4 138.00] TO BUS 514510 [BURGETT4 138.00] CKT 1 | 50.191 | PASS | 10.9094 | PASS | 10809.4199 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515465 [LGARBER4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 50.1839 | PASS | 10.9094 | PASS | 10809.3772 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515466 [MITCHSB4 138.00] TO BUS 515467 [WHITESB4 138.00] CKT 1 | 50.1771 | PASS | 10.9096 | PASS | 10809.6179 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515479 [CHSHMVE1 34.5.00] CKT 1 | 50.1905 | PASS | 10.9093 | PASS | 10809.2996 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515484 [CHSHMVW1 34.5.00] CKT 1 | 50.1915 | PASS | 10.9093 | PASS | 10809.2874 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] CKT 2 | 50.1607 | PASS | 10.9097 | PASS | 10809.6622 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515546 [GRANTCO4 138.00] TO BUS 515547 [GRANTCO2 69.00] CKT 4 | 50.1896 | PASS | 10.9095 | PASS | 10809.4618 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515549 [MNCWND37 345.00] TO BUS 515939 [MNCWND47 345.00] CKT 1 | 50.2135 | PASS | 10.9076 | PASS | 10807.584 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515549 [MNCWND37 345.00] TO BUS 515550 [MNCWND31 34.5.00] CKT 1 | 50.1942 | PASS | 10.909 | PASS | 10809.0292 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 515426 [RDRUNNR4 138.00] CKT 1 | 50.1906 | PASS | 10.9095 | PASS | 10809.4794 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 522397 [MEDFORD4 138.00] CKT 1 | 50.1894 | PASS | 10.9094 | PASS | 10809.444 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515583 [SLINGW11 34.5.00] CKT 1 | 50.1996 | PASS | 10.9086 | PASS | 10808.562 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515632 [SILNGW21 34.5.00] CKT 2 | 50.2077 | PASS | 10.9079 | PASS | 10807.8569 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 515586 [MMTHPW11 34.5.00] CKT 2 | 50.1975 | PASS | 10.9087 | PASS | 10808.6982 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 915586 [MMTHPW21 34.5.00] CKT 1 | 50.1868 | PASS | 10.9092 | PASS | 10809.2215 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515600 [KNGFSHR7 345.00] TO BUS 515855 [KNGFSR11 34.5.00] CKT 1 | 50.1975 | PASS | 10.9088 | PASS | 10808.7929 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515600 [KNGFSHR7 345.00] TO BUS 515856 [KNGFSR21 34.5.00] CKT 2 | 50.2162 | PASS | 10.9071 | PASS | 10807.1452 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515605 [CANADN7 345.00] TO BUS 515606 [CANDN11 34.5.00] CKT 1 | 50.1959 | PASS | 10.9089 | PASS | 10808.888 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515605 [CANADN7 345.00] TO BUS 515609 [CANDNT2 13.8.00] CKT 1 | 50.1959 | PASS | 10.9089 | PASS | 10808.8814 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515648 [GRNTWD12 34.5.00] CKT 1 | 50.1863 | PASS | 10.9095 | PASS | 10809.4971 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515647 [GRNTWD11 34.5.00] CKT 1 | 50.1863 | PASS | 10.9095 | PASS | 10809.4946 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515675 [TRYON 4 138.00] TO BUS 515047 [WARWICK4 138.00] CKT 1 | 50.1468 | PASS | 10.9094 | PASS | 10809.4146 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515675 [TRYON 4 138.00] TO BUS 515453 [LNWOODT4 138.00] CKT 1 | 50.1892 | PASS | 10.9095 | PASS | 10809.4978 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515675 [TRYON 4 138.00] TO BUS 516237 [ANVIL 4 138.00] CKT 1 | 50.1963 | PASS | 10.9088 | PASS | 10808.831 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515688 [FRNTWND7 345.00] TO BUS 515689 [FRNTWD11 34.5.00] CKT 1 | 50.1902 | PASS | 10.91 | PASS | 10810.0029 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 515695 [ARMFTL11 34.5.00] CKT 1 | 50.1966 | PASS | 10.9094 | PASS | 10809.3578 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 50.1688 | PASS | 10.9087 | PASS | 10808.6814 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 50.1476 | PASS | 10.9122 | PASS | 10812.2343 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] CKT 3 | 50.1693 | PASS | 10.9093 | PASS | 10809.294 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] CKT 1 | 50.1974 | PASS | 10.909 | PASS | 10808.9913 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] CKT 1 | 50.1985 | PASS | 10.9089 | PASS | 10808.8657 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515891 [THNDRL21 34.5.00] CKT 1 | 50.1971 | PASS | 10.9116 | PASS | 10811.6222 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515890 [THNDRL11 34.5.00] CKT 1 | 50.2093 | PASS | 10.9124 | PASS | 10812.4439 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515947 [CONTCBN2 69.00] TO BUS 515948 [CONTCBN1 12.5.00] CKT 1 | 50.1685 | PASS | 10.9093 | PASS | 10809.3464 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515974 [GEN-2015-066 345.00] TO BUS 515972 [G15-066XFMR1 34.5.00] CKT 1 | 50.2911 | PASS | 10.8962 | PASS | 10796.185 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 515991 [SKELTL11 34.5.00] CKT 1 | 50.2129 | PASS | 10.9086 | PASS | 10808.6121 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516017 [KNGWDL11 34.5.00] CKT 1 | 50.1995 | PASS | 10.9092 | PASS | 10809.1729 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516018 [KNGWDL21 34.5.00] CKT 1 | 50.2034 | PASS | 10.9091 | PASS | 10809.1226 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516054 [TRAV1WD7 345.00] CKT 1 | 50.203 | PASS | 10.9085 | PASS | 10808.4599 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516087 [TRAV22Z7 345.00] CKT 1 | 50.2026 | PASS | 10.9083 | PASS | 10808.3481 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516107 [TRAV21Z7 345.00] CKT 1 | 50.1961 | PASS | 10.9089 | PASS | 10808.8952 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516066 [FRNT2WD7 345.00] TO BUS 516064 [FRNT2L11 34.5.00] CKT 1 | 50.1826 | PASS | 10.9108 | PASS | 10810.7946 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516066 [FRNT2WD7 345.00] TO BUS 516065 [FRNT2L21 34.5.00] CKT 1 | 50.1741 | PASS | 10.9109 | PASS | 10810.9029 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516086 [TRAV3WZ7 345.00] TO BUS 516035 [TRAV3L11 34.5.00] CKT 1 | 50.1959 | PASS | 10.9089 | PASS | 10808.9198 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 50.1871 | PASS | 10.9095 | PASS | 10809.482 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] CKT 2 | 50.1871 | PASS | 10.9095 | PASS | 10809.4824 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514902 [MCCLAIN4 138.00] CKT 1 | 50.1868 | PASS | 10.9094 | PASS | 10809.431 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514929 [PLVALLY4 138.00] CKT 1 | 50.1893 | PASS | 10.9095 | PASS | 10809.4983 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514957 [CHERYCK4 138.00] CKT 1 | 50.1893 | PASS | 10.9094 | PASS | 10809.441 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514992 [TURNER 4 138.00] CKT 1 | 50.1901 | PASS | 10.9094 | PASS | 10809.3907 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516192 [WAGNWTIE7 345.00] TO BUS 516193 [WAGNWL11 34.5.00] CKT 1 | 50.2212 | PASS | 10.9068 | PASS | 10806.7804 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516198 [WAGNWL7 345.00] TO BUS 516194 [WAGNWL21 34.5.00] CKT 1 | 50.2253 | PASS | 10.9064 | PASS | 10806.4338 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516210 [RAVEN 7 345.00] TO BUS 515422 [C-RIVER7 345.00] CKT 1 | 50.1739 | PASS | 10.9111 | PASS | 10811.1437 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516210 [RAVEN 7 345.00] TO BUS 516091 [OKTAHA 7 345.00] CKT 1 | 50.1761 | PASS | 10.9107 | PASS | 10810.727 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516210 [RAVEN 7 345.00] TO BUS 588838 [G17-092-SWYD 345.00] CKT 1 | 50.2099 | PASS | 10.9078 | PASS | 10807.7535 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516363 [ARMADILLO_HV 138.00] TO BUS 516364 [ARMADILLO_T1 34.5.00] CKT 1 | 50.1919 | PASS | 10.9092 | PASS | 10809.1693 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520409 [WFEC_RNFRO4 138.00] TO BUS 520434 [WAKTASW4 138.00] CKT 1 | 50.1341 | PASS | 10.9095 | PASS | 10809.4791 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520443 [WEBBCTY4 138.00] TO BUS 520441 [HARDY 4 138.00] CKT 1 | 50.1892 | PASS | 10.9094 | PASS | 10809.4039 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529200 [OMCDLEC7 345.00] TO BUS 529201 [OMCDLEC1 13.8.00] CKT 1 | 49.1428 | PASS | 10.9119 | PASS | 10811.9258 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529242 [OMHUFFYT 69.00] TO BUS 529251 [OMRIGGS 69.00] CKT 1 | 50.0974 | PASS | 10.9096 | PASS | 10809.6238 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529248 [OMPECANT 69.00] TO BUS 529246 [OMKAWS 69.00] CKT 1 | 50.1437 | PASS | 10.9094 | PASS | 10809.4479 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532780 [CANEYRV7 345.00] TO BUS 532777 [NRSS7 345.00] CKT 1 | 50.0321 | PASS | 10.9099 | PASS | 10809.8733 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532780 [CANEYRV7 345.00] TO BUS 532781 [CANEYWF7 345.00] CKT 1 | 50.1766 | PASS | 10.9105 | PASS | 10810.5227 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] CKT 1 | 50.1909 | PASS | 10.9095 | PASS | 10809.4553 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] CKT 1 | 50.1905 | PASS | 10.9094 | PASS | 10809.446 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 50.187 | PASS | 10.9093 | PASS | 10809.2726 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 50.1872 | PASS | 10.9093 | PASS | 10809.2837 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 50.1859 | PASS | 10.9088 | PASS | 10808.8085 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 50.0054 | PASS | 10.9122 | PASS | 10812.1755 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 50.1792 | PASS | 10.9099 | PASS | 10809.9371 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 2 | 50.1792 | PASS | 10.9099 | PASS | 10809.9371 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 50.0605 | PASS | 10.9119 | PASS | 10811.8913 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] CKT 1 | 50.1865 | PASS | 10.9095 | PASS | 10809.5355 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] CKT 1 | 50.1858 | PASS | 10.9096 | PASS | 10809.5599 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532751 [WCGS U1 25.00] CKT 1 | 49.8793 | PASS | 10.9233 | PASS | 10823.2703 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533900 [WCGS_TX1_1 13.8.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.4211 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.00] CKT 1 | 50.1898 | PASS | 10.9094 | PASS | 10809.41 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.00] CKT 1 | 50.1897 | PASS | 10.9094 | PASS | 10809.4271 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 532814 [FR4345KV-TAP 345.00] CKT 1 | 50.1805 | PASS | 10.9119 | PASS | 10811.8878 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] CKT 2 | 50.1757 | PASS | 10.9098 | PASS | 10809.7626 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 50.1803 | PASS | 10.9102 | PASS | 10810.2329 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 50.185 | PASS | 10.9098 | PASS | 10809.8158 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 50.1317 | PASS | 10.9114 | PASS | 10811.3645 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532801 [ELKRVR17 345.00] TO BUS 534016 [ER1 TX1 34.5.00] CKT 1 | 50.1858 | PASS | 10.9097 | PASS | 10809.7161 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 532988 [BELAIRE4 138.00] CKT 1 | 50.1901 | PASS | 10.9095 | PASS | 10809.4766 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 532990 [MIDIAN 4 138.00] CKT 1 | 50.1869 | PASS | 10.9097 | PASS | 10809.6755 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 533024 [29TH 4 138.00] CKT 1 | 50.1898 | PASS | 10.9095 | PASS | 10809.469 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 533052 [PARKCTY4 138.00] CKT 1 | 50.187 | PASS | 10.9093 | PASS | 10809.2975 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 532993 [TALLGRS4 138.00] CKT 1 | 50.1828 | PASS | 10.9095 | PASS | 10809.4661 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533026 [ANDOVER4 138.00] CKT 1 | 50.1863 | PASS | 10.9094 | PASS | 10809.3919 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533032 [BU11PON4 138.00] CKT 1 | 50.1894 | PASS | 10.9094 | PASS | 10809.4357 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533067 [SPRNGDL4 138.00] CKT 1 | 50.1899 | PASS | 10.9094 | PASS | 10809.3804 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533604 [WEAVER 2 69.00] CKT 2 | 50.1887 | PASS | 10.9094 | PASS | 10809.4375 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533029 [59TH ST4 138.00] CKT 1 | 50.1867 | PASS | 10.9096 | PASS | 10809.5818 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533059 [ELPASOE4 138.00] CKT 1 | 50.1932 | PASS | 10.9095 | PASS | 10809.481 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533068 [STEARMN4 138.00] TO BUS 533030 [BOEINGE4 138.00] CKT 1 | 50.1815 | PASS | 10.9093 | PASS | 10809.274 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.00] TO BUS 533626 [BURLJCT2 69.00] CKT 1 | 50.1893 | PASS | 10.9097 | PASS | 10809.7205 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.00] TO BUS 533629 [CC2SHAR2 69.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.4204 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 560389 [GEN-2010-055 138.00] TO BUS 560390 [G10-055-GSU1 13.8.00] CKT 1 | 50.1843 | PASS | 10.9095 | PASS | 10809.4575 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 562901 [G15052_2 34.5.00] CKT 1 | 50.1895 | PASS | 10.9094 | PASS | 10809.4152 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 562901 [G15052_2 34.5.00] CKT 2 | 50.1895 | PASS | 10.9094 | PASS | 10809.4152 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 765514 [G21-023-XFM1 34.5.00] CKT 1 | 50.1705 | PASS | 10.9106 | PASS | 10810.6357 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 765517 [G21-023-XFM2 34.5.00] CKT 1 | 50.1705 | PASS | 10.9106 | PASS | 10810.6357 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 588190 [GEN-2016-128 345.00] TO BUS 588191 [G16-128XFMR1 34.5.00] CKT 1 | 50.2048 | PASS | 10.9083 | PASS | 10808.2711 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 760032 [GEN-2017-133 345.00] TO BUS 760053 [G17-133-XFM1 34.5.00] CKT 1 | 50.2058 | PASS | 10.9081 | PASS | 10808.0591 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 760032 [GEN-2017-133 345.00] TO BUS 760074 [G17-134-XFM1 34.5.00] CKT 1 | 50.2098 | PASS | 10.9077 | PASS | 10807.7232 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 760032 [GEN-2017-133 345.00] TO BUS 760095 [G17-137-XFM1 34.5.00] CKT 1 | 50.2133 | PASS | 10.9074 | PASS | 10807.4281 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 761250 [GEN-2017-233 345.00] TO BUS 761229 [GEN-2017-150 345.00] CKT 1 | 50.2069 | PASS | 10.908 | PASS | 10807.9952 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 761250 [GEN-2017-233 345.00] TO BUS 761251 [G17-233-XFMR 34.5.00] CKT 1 | 50.2039 | PASS | 10.9082 | PASS | 10808.1934 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762322 [G17-164XFM1 34.5.00] CKT 1 | 50.2021 | PASS | 10.9083 | PASS | 10808.3289 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762342 [GEN-2017-178 345.00] TO BUS 762343 [G17-178XFM1 34.5.00] CKT 1 | 50.1986 | PASS | 10.9086 | PASS | 10808.5864 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762636 [GEN-2018-028 138.00] TO BUS 762637 [G18-028XFM1 34.5.00] CKT 1 | 50.1895 | PASS | 10.91 | PASS | 10810.0225 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 762824 [G18-048-XFM1 34.5.00] CKT 1 | 50.1932 | PASS | 10.9091 | PASS | 10809.14 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 762827 [G18-048-XFM2 34.5.00] CKT 1 | 50.1932 | PASS | 10.9091 | PASS | 10809.14 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 765774 [G21-052-XFM1 34.5.00] CKT 1 | 50.1942 | PASS | 10.909 | PASS | 10809.0494 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 765784 [G21-053-XFM1 34.5.00] CKT 1 | 50.1931 | PASS | 10.9091 | PASS | 10809.1472 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 765787 [G21-053-XFM2 34.5.00] CKT 1 | 50.1931 | PASS | 10.9091 | PASS | 10809.1472 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763065 [GEN-2018-071 345.00] TO BUS 763066 [G18-071-XFM1 34.5.00] CKT 1 | 50.2031 | PASS | 10.9097 | PASS | 10809.681 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763065 [GEN-2018-071 345.00] TO BUS 763077 [G18-072-XFM1 34.5.00] CKT 1 | 50.2031 | PASS | 10.9097 | PASS | 10809.6713 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763417 [GEN-2018-128 345.00] TO BUS 763418 [G18-128-XFM1 34.5.00] CKT 1 | 50.1926 | PASS | 10.9097 | PASS | 10809.6719 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765200 [G20-090-TAP 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 50.1783 | PASS | 10.9106 | PASS | 10810.6041 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765200 [G20-090-TAP 345.00] TO BUS 765190 [GEN-2020-090 345.00] CKT 1 | 50.1897 | PASS | 10.9095 | PASS | 10809.4897 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765200 [G20-090-TAP 345.00] TO BUS 768061 [GEN-2022-054 345.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.437 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765470 [GEN-2021-018 345.00] TO BUS 765474 [G21-018-XFM1 34.5.00] CKT 1 | 50.2908 | PASS | 10.9072 | PASS | 10807.1612 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765480 [GEN-2021-019 345.00] TO BUS 765484 [G21-019-XFM1 34.5.00] CKT 1 | 50.2181 | PASS | 10.9071 | PASS | 10807.1074 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 766141 [G21-096-TAP 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 50.1301 | PASS | 10.9092 | PASS | 10809.211 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 766141 [G21-096-TAP 345.00] TO BUS 766140 [GEN-2021-096 345.00] CKT 1 | 50.1901 | PASS | 10.9097 | PASS | 10809.7071 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 770101 [GEN-2022-156 138.00] TO BUS 770102 [G22-156XFMR1 34.5.00] CKT 1 | 50.1922 | PASS | 10.9094 | PASS | 10809.4086 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 770501 [GEN-2022-176 345.00] TO BUS 770502 [G22-176XFMR1 34.5.00] CKT 1 | 50.1839 | PASS | 10.9107 | PASS | 10810.6966 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 773121 [GEN-2023-057 138.00] TO BUS 773122 [G23-057XFMR1 34.5.00] CKT 1 | 50.1876 | PASS | 10.9104 | PASS | 10810.4102 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 777361 [GEN-2024-013 345.00] TO BUS 777368 [GEN-2024-C1 345.00] CKT 1 | 50.1869 | PASS | 10.9062 | PASS | 10806.1834 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 777361 [GEN-2024-013 345.00] TO BUS 777369 [GEN-2024-C2 345.00] CKT 1 | 50.1884 | PASS | 10.9061 | PASS | 10806.0604 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 778651 [GEN-2024-056 138.00] TO BUS 778652 [G24-056XFMR1 34.5.00] CKT 0 | 50.2011 | PASS | 10.9092 | PASS | 10809.2144 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 782101 [GEN-2024-171 345.00] TO BUS 782102 [G24-171XFMR1 34.5.00] CKT 1 | 50.1888 | PASS | 10.9097 | PASS | 10809.7185 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 782101 [GEN-2024-171 345.00] TO BUS 782105 [G24-171XFMR2 34.5.00] CKT 1 | 50.1822 | PASS | 10.9107 | PASS | 10810.7226 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784021 [GEN-2024-235 345.00] TO BUS 784022 [G24-235XFMR1 34.5.00] CKT 1 | 50.1714 | PASS | 10.9109 | PASS | 10810.8583 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784021 [GEN-2024-235 345.00] TO BUS 784025 [G24-235XFMR2 34.5.00] CKT 1 | 50.1716 | PASS | 10.9109 | PASS | 10810.8518 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784141 [GEN-2024-239 345.00] TO BUS 784142 [G24-239XFMR1 34.5.00] CKT 1 | 50.2202 | PASS | 10.9068 | PASS | 10806.7633 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784530 [GEN-2024-252 345.00] TO BUS 784535 [G24-252XFMR2 34.5.00] CKT 2 | 50.2017 | PASS | 10.9084 | PASS | 10808.3604 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 784534 [G24-252GEN1 13.8.00] CKT 1 | 50.0926 | PASS | 10.9054 | PASS | 10805.4437 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 784595 [G24-254XFMR2 34.5.00] CKT 2 | 50.2014 | PASS | 10.9084 | PASS | 10808.376 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 784594 [G24-254GEN1 13.8.00] CKT 1 | 50.0329 | PASS | 10.9062 | PASS | 10806.2032 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784620 [GEN-2024-255 345.00] TO BUS 784625 [G24-255XFMR2 34.5.00] CKT 2 | 50.2042 | PASS | 10.9081 | PASS | 10808.1385 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784621 [GEN-2024-255 345.00] TO BUS 784624 [G24-255GEN1 13.8.00] CKT 1 | 49.8539 | PASS | 10.9051 | PASS | 10805.1346 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 785790 [G24-294-TAP 345.00] TO BUS 765721 [G21-047-TAP 345.00] CKT 1 | 49.6092 | PASS | 10.9095 | PASS | 10809.5279 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 785790 [G24-294-TAP 345.00] TO BUS 785791 [GEN-2024-294 345.00] CKT 1 | 50.1842 | PASS | 10.9114 | PASS | 10811.4461 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786604 [G24-321GEN1 18.00] CKT 1 | 50.1989 | PASS | 10.9071 | PASS | 10807.0687 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786607 [G24-321GEN2 18.00] CKT 1 | 50.1989 | PASS | 10.9071 | PASS | 10807.0687 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786998 [G24-334-C1 345.00] TO BUS 786994 [G24-334GEN1 13.8.00] CKT 1 | 49.7413 | PASS | 10.9101 | PASS | 10810.0929 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786999 [G24-334-C2 345.00] TO BUS 786997 [G24-334GEN2 13.8.00] CKT 1 | 49.7412 | PASS | 10.9101 | PASS | 10810.093 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914715 [SKELETON__HV 345.00] TO BUS 914717 [SKELETON__T1 34.5.00] CKT 1 | 50.1956 | PASS | 10.9088 | PASS | 10808.7875 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914720 [SKELETON__HV 345.00] TO BUS 914722 [SKELETON__T1 34.5.00] CKT 1 | 50.1909 | PASS | 10.9093 | PASS | 10809.2598 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914801 [MINCO_IV__HV 345.00] TO BUS 914802 [MINCO IV HV2 345.00] CKT 1 | 50.192 | PASS | 10.9093 | PASS | 10809.2741 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914807 [MINCO_I_&_HV 345.00] TO BUS 914809 [MINCO_I_&_T1 34.5.00] CKT 1 | 50.1896 | PASS | 10.9094 | PASS | 10809.4212 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 300929 [2FAIRFAX 69.00] CKT 1 | 50.1821 | PASS | 10.9098 | PASS | 10809.8264 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301413 [2STILWTRKAMO 69.00] CKT 1 | 50.1856 | PASS | 10.9088 | PASS | 10808.7664 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 1 | 50.1853 | PASS | 10.9095 | PASS | 10809.5408 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | 50.1609 | PASS | 10.9095 | PASS | 10809.4608 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 49.9702 | PASS | 10.9252 | PASS | 10825.1743 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 50.0497 | PASS | 10.9127 | PASS | 10812.7134 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 50.0484 | PASS | 10.9176 | PASS | 10817.6087 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29SP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 562901 [G15052_2 34.5.00] CKT 1 | 50.1953 | PASS | 10.9101 | PASS | 10810.1231 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | BASE CASE | 48.5586 | PASS | 10.9376 | PASS | 10837.6274 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300131 [4FISHERTP 138.00] TO BUS 300140 [4SILVCTY 138.00] CKT 1 | 48.5583 | PASS | 10.9377 | PASS | 10837.6625 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300131 [4FISHERTP 138.00] TO BUS 300145 [4FISHER 138.00] CKT 1 | 48.555 | PASS | 10.9376 | PASS | 10837.6263 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300131 [4FISHERTP 138.00] TO BUS 505610 [KEYSTON4 138.00] CKT 1 | 48.5564 | PASS | 10.9377 | PASS | 10837.6795 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 300140 [4SILVCTY 138.00] CKT 1 | 48.4631 | PASS | 10.9376 | PASS | 10837.558 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 300140 [4SILVCTY 138.00] CKT 1 | 48.5353 | PASS | 10.9373 | PASS | 10837.3152 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 300927 [2CLEVLND 69.00] CKT 1 | 48.5578 | PASS | 10.9376 | PASS | 10837.5877 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 300927 [2CLEVLND 69.00] CKT 2 | 48.5576 | PASS | 10.9376 | PASS | 10837.583 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 301640 [4HOMNYTP 138.00] CKT 1 | 48.5111 | PASS | 10.9367 | PASS | 10836.6517 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 512729 [CLEVLND 4 138.00] CKT 1 | 47.2408 | PASS | 10.9283 | PASS | 10828.324 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 512749 [PAWNSW4 138.00] CKT 1 | 48.5544 | PASS | 10.9379 | PASS | 10837.9465 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 301369 [4REMNGTON 138.00] CKT 1 | 48.5579 | PASS | 10.9376 | PASS | 10837.5857 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 512749 [PAWNSW4 138.00] CKT 1 | 48.5583 | PASS | 10.9375 | PASS | 10837.4829 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 300141 [4STILWTR 138.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.6214 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 300943 [2SILVCTY 69.00] CKT 1 | 48.5586 | PASS | 10.9377 | PASS | 10837.6589 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 300943 [2SILVCTY 69.00] CKT 2 | 48.5586 | PASS | 10.9377 | PASS | 10837.6593 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300140 [4SILVCTY 138.00] TO BUS 512726 [SILVCTYGR4 138.00] CKT 1 | 48.5554 | PASS | 10.9379 | PASS | 10837.8663 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 513095 [GLENCO 4 138.00] CKT 1 | 48.5569 | PASS | 10.9372 | PASS | 10837.2268 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300927 [2CLEVLND 69.00] TO BUS 512876 [OSAGEK2 69.00] CKT 1 | 48.552 | PASS | 10.9372 | PASS | 10837.2305 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300996 [4JAVINE 138.00] TO BUS 301640 [4HOMNYTP 138.00] CKT 1 | 48.511 | PASS | 10.9366 | PASS | 10836.62 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 301011 [4REDRCK 138.00] TO BUS 515978 [OTOETAP4 138.00] CKT 1 | 48.5578 | PASS | 10.9376 | PASS | 10837.6375 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 301369 [4REMNGTON 138.00] TO BUS 510403 [SHIDLER4 138.00] CKT 1 | 48.5539 | PASS | 10.9376 | PASS | 10837.6337 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 505610 [KEYSTON4 138.00] TO BUS 509757 [WEKIWA-4 138.00] CKT 1 | 48.5465 | PASS | 10.9375 | PASS | 10837.4999 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509727 [OAKS W4 138.00] TO BUS 509848 [OAKSWTP4 138.00] CKT 1 | 48.5571 | PASS | 10.9376 | PASS | 10837.6153 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509739 [CARSN-T4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 48.5214 | PASS | 10.9376 | PASS | 10837.5558 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509741 [CARSN-N4 138.00] TO BUS 509865 [CARSONT4 138.00] CKT 1 | 48.5584 | PASS | 10.9377 | PASS | 10837.6888 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 48.4676 | PASS | 10.9372 | PASS | 10837.239 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 515224 [MUSKOGE7 345.00] CKT 1 | 48.4811 | PASS | 10.9402 | PASS | 10840.2017 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509746 [DENVTAP4 138.00] TO BUS 509817 [T.NO.--4 138.00] CKT 1 | 48.5577 | PASS | 10.9376 | PASS | 10837.6248 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509748 [DENVR-W4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 48.5594 | PASS | 10.9377 | PASS | 10837.7317 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509753 [116JENK4 138.00] TO BUS 509759 [JENKS--4 138.00] CKT 1 | 48.5441 | PASS | 10.9378 | PASS | 10837.7804 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509753 [116JENK4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 48.5449 | PASS | 10.9378 | PASS | 10837.8305 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509852 [T.NO.--7 345.00] CKT 1 | 48.5045 | PASS | 10.906 | PASS | 10806.0444 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 47.2472 | PASS | 10.9371 | PASS | 10837.1487 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 43.4973 | PASS | 10.9146 | PASS | 10814.6162 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 509812 [SHEFFD-4 138.00] CKT 1 | 48.5101 | PASS | 10.9374 | PASS | 10837.4435 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 509823 [WED-TAP4 138.00] CKT 1 | 48.5335 | PASS | 10.9376 | PASS | 10837.555 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 509851 [P&P WTP4 138.00] CKT 1 | 48.5542 | PASS | 10.9382 | PASS | 10838.1785 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 512726 [SILVCTYGR4 138.00] CKT 1 | 48.5568 | PASS | 10.9377 | PASS | 10837.6866 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509757 [WEKIWA-4 138.00] TO BUS 560389 [GEN-2010-055 138.00] CKT 1 | 48.5529 | PASS | 10.9376 | PASS | 10837.6426 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509758 [PRATTV-4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 48.5451 | PASS | 10.9374 | PASS | 10837.4461 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509759 [JENKS--4 138.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 48.544 | PASS | 10.9378 | PASS | 10837.7731 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509783 [R.S.S.-4 138.00] CKT 1 | 48.5557 | PASS | 10.9376 | PASS | 10837.569 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 48.4788 | PASS | 10.939 | PASS | 10839.0245 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509834 [COGENT 7 345.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6304 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509870 [SAPLPRD7 345.00] CKT 1 | 47.658 | PASS | 10.9369 | PASS | 10836.8507 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 511877 [G16133G16146 345.00] CKT 1 | 48.4564 | PASS | 10.9363 | PASS | 10836.3344 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 48.5223 | PASS | 10.9062 | PASS | 10806.2368 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 48.3676 | PASS | 10.9378 | PASS | 10837.7529 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509875 [RSS T2 4 138.00] CKT 1 | 48.5557 | PASS | 10.9376 | PASS | 10837.5572 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509888 [72ELWOD4 138.00] CKT 1 | 48.553 | PASS | 10.9376 | PASS | 10837.6367 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509904 [AVERYDR4 138.00] CKT 1 | 48.5556 | PASS | 10.9376 | PASS | 10837.6341 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509805 [PP----W4 138.00] TO BUS 509851 [P&P WTP4 138.00] CKT 1 | 48.5569 | PASS | 10.9375 | PASS | 10837.519 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 1 | 48.5583 | PASS | 10.9376 | PASS | 10837.6322 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 509836 [OEC 7 345.00] CKT 2 | 48.5583 | PASS | 10.9376 | PASS | 10837.6322 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509807 [ONETA--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 48.3243 | PASS | 10.9405 | PASS | 10840.5316 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509812 [SHEFFD-4 138.00] TO BUS 509815 [S.S.---4 138.00] CKT 1 | 48.5099 | PASS | 10.9374 | PASS | 10837.43 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509815 [S.S.---4 138.00] TO BUS 509821 [HWY20-T4 138.00] CKT 1 | 48.5579 | PASS | 10.9376 | PASS | 10837.6384 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509815 [S.S.---4 138.00] TO BUS 509823 [WED-TAP4 138.00] CKT 1 | 48.5331 | PASS | 10.9375 | PASS | 10837.5109 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509815 [S.S.---4 138.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 48.5504 | PASS | 10.9376 | PASS | 10837.6079 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509839 [CDC-ET 4 138.00] CKT 1 | 48.5422 | PASS | 10.9375 | PASS | 10837.5336 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509842 [CDC-WT 4 138.00] CKT 1 | 48.5406 | PASS | 10.9374 | PASS | 10837.4339 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509844 [OWASOTP4 138.00] CKT 1 | 48.468 | PASS | 10.9376 | PASS | 10837.5884 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509851 [P&P WTP4 138.00] CKT 1 | 48.5551 | PASS | 10.938 | PASS | 10838.0438 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509895 [T.NO.2-4 138.00] CKT 1 | 48.4592 | PASS | 10.9379 | PASS | 10837.8528 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509900 [46ST-TP-4 138.00] CKT 1 | 48.5366 | PASS | 10.9375 | PASS | 10837.4596 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 509908 [SKIATKTP4 138.00] CKT 1 | 48.5463 | PASS | 10.9372 | PASS | 10837.2281 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 510396 [N.E.S.-4 138.00] CKT 1 | 48.4792 | PASS | 10.9378 | PASS | 10837.7768 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509817 [T.NO.--4 138.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 48.4626 | PASS | 10.9371 | PASS | 10837.129 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509823 [WED-TAP4 138.00] TO BUS 509865 [CARSONT4 138.00] CKT 1 | 48.5573 | PASS | 10.9377 | PASS | 10837.669 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509832 [W.ED.-W4 138.00] TO BUS 509865 [CARSONT4 138.00] CKT 1 | 48.5576 | PASS | 10.9376 | PASS | 10837.6026 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509848 [OAKSWTP4 138.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 48.5526 | PASS | 10.9376 | PASS | 10837.6258 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509848 [OAKSWTP4 138.00] TO BUS 509904 [AVERYDR4 138.00] CKT 1 | 48.553 | PASS | 10.9376 | PASS | 10837.6319 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 510406 [N.E.S.-7 345.00] CKT 1 | 48.0325 | PASS | 10.9322 | PASS | 10832.1956 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 512694 [CLEVLND7 345.00] CKT 1 | 44.9523 | PASS | 10.8907 | PASS | 10790.7137 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 760152 [TNOXF2 138.00] CKT 2 | 48.4626 | PASS | 10.9371 | PASS | 10837.1289 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 782100 [G24-171-TAP 345.00] CKT 1 | 47.9607 | PASS | 10.9362 | PASS | 10836.2359 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509871 [SAPLPRD4 138.00] TO BUS 509888 [72ELWOD4 138.00] CKT 1 | 48.5526 | PASS | 10.9376 | PASS | 10837.6309 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509895 [T.NO.2-4 138.00] TO BUS 762636 [GEN-2018-028 138.00] CKT 1 | 48.5569 | PASS | 10.9383 | PASS | 10838.3479 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 782100 [G24-171-TAP 345.00] CKT 1 | 47.9712 | PASS | 10.934 | PASS | 10833.9764 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509915 [ANTHEM7 345.00] TO BUS 785790 [G24-294-TAP 345.00] CKT 1 | 48.0038 | PASS | 10.9376 | PASS | 10837.5689 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510376 [WEBBTAP4 138.00] TO BUS 510403 [SHIDLER4 138.00] CKT 1 | 48.5135 | PASS | 10.938 | PASS | 10837.9942 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510376 [WEBBTAP4 138.00] TO BUS 514743 [OSAGE 4 138.00] CKT 1 | 48.51 | PASS | 10.9382 | PASS | 10838.2267 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510376 [WEBBTAP4 138.00] TO BUS 520442 [SHIDWFC4 138.00] CKT 1 | 48.5536 | PASS | 10.9375 | PASS | 10837.5481 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 770500 [G22-176-TAP 345.00] CKT 1 | 48.396 | PASS | 10.9355 | PASS | 10835.5123 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510382 [WPAWHSK4 138.00] TO BUS 510403 [SHIDLER4 138.00] CKT 1 | 48.5139 | PASS | 10.9383 | PASS | 10838.3147 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510406 [N.E.S.-7 345.00] TO BUS 770500 [G22-176-TAP 345.00] CKT 1 | 48.4062 | PASS | 10.9357 | PASS | 10835.6776 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 48.5482 | PASS | 10.9382 | PASS | 10838.2444 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 48.5472 | PASS | 10.9376 | PASS | 10837.6213 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511877 [G16133G16146 345.00] TO BUS 511878 [G16133_765TN 765.00] CKT 1 | 48.553 | PASS | 10.9378 | PASS | 10837.7532 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511877 [G16133G16146 345.00] TO BUS 511878 [G16133_765TN 765.00] CKT 2 | 48.553 | PASS | 10.9378 | PASS | 10837.7532 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 41.4795 | PASS | 10.8422 | PASS | 10742.1573 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512726 [SILVCTYGR4 138.00] TO BUS 770101 [GEN-2022-156 138.00] CKT 1 | 48.5599 | PASS | 10.9377 | PASS | 10837.7087 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512749 [PAWNSW4 138.00] TO BUS 513095 [GLENCO 4 138.00] CKT 1 | 48.5572 | PASS | 10.9372 | PASS | 10837.2242 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512749 [PAWNSW4 138.00] TO BUS 773121 [GEN-2023-057 138.00] CKT 1 | 48.5559 | PASS | 10.9385 | PASS | 10838.4918 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514704 [MILLERT4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 48.4704 | PASS | 10.938 | PASS | 10837.9706 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514704 [MILLERT4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 48.4709 | PASS | 10.938 | PASS | 10837.9514 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514704 [MILLERT4 138.00] TO BUS 515978 [OTOETAP4 138.00] CKT 1 | 48.5564 | PASS | 10.9376 | PASS | 10837.649 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514768 [WF KAY 2 69.00] CKT 1 | 48.5565 | PASS | 10.9376 | PASS | 10837.6419 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514707 [PERRY 4 138.00] CKT 1 | 48.5249 | PASS | 10.9378 | PASS | 10837.7509 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 48.5529 | PASS | 10.9378 | PASS | 10837.7506 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514706 [COWCRK 4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 48.5423 | PASS | 10.9377 | PASS | 10837.703 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514707 [PERRY 4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 48.5263 | PASS | 10.9378 | PASS | 10837.8096 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514713 [WRVALLY4 138.00] CKT 1 | 48.5528 | PASS | 10.9378 | PASS | 10837.7734 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 48.5524 | PASS | 10.9376 | PASS | 10837.6201 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514708 [OTTER 4 138.00] TO BUS 515694 [ARMFTWD4 138.00] CKT 1 | 48.5687 | PASS | 10.9375 | PASS | 10837.4927 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514712 [FAIRMON4 138.00] CKT 1 | 48.5558 | PASS | 10.9374 | PASS | 10837.4251 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 48.5427 | PASS | 10.9374 | PASS | 10837.3856 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514709 [FRMNTAP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 48.5533 | PASS | 10.9376 | PASS | 10837.609 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514711 [WAUKOTP4 138.00] CKT 1 | 48.445 | PASS | 10.9376 | PASS | 10837.6276 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514710 [WAUKOMI4 138.00] TO BUS 514774 [HENESEY4 138.00] CKT 1 | 48.4457 | PASS | 10.9376 | PASS | 10837.6328 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514714 [WOODRNG4 138.00] CKT 1 | 48.5334 | PASS | 10.9376 | PASS | 10837.5629 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514711 [WAUKOTP4 138.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 48.5597 | PASS | 10.9376 | PASS | 10837.6147 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514712 [FAIRMON4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 48.5553 | PASS | 10.9375 | PASS | 10837.4595 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514713 [WRVALLY4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 48.5573 | PASS | 10.9376 | PASS | 10837.6479 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514733 [MARSHL 4 138.00] CKT 1 | 48.4815 | PASS | 10.9377 | PASS | 10837.6831 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515476 [HUNTERS7 345.00] CKT 1 | 47.8141 | PASS | 10.9081 | PASS | 10808.0654 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 45.9112 | PASS | 10.9374 | PASS | 10837.3816 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 515990 [SKELTON7 345.00] CKT 1 | 48.594 | PASS | 10.9366 | PASS | 10836.5713 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 42.0994 | PASS | 10.9447 | PASS | 10844.7151 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 762321 [GEN-2017-164 345.00] CKT 1 | 48.5777 | PASS | 10.9376 | PASS | 10837.5607 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914715 [SKELETON__HV 345.00] CKT 1 | 48.5842 | PASS | 10.9378 | PASS | 10837.8079 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514715 [WOODRNG7 345.00] TO BUS 914720 [SKELETON__HV 345.00] CKT 1 | 48.562 | PASS | 10.9374 | PASS | 10837.4267 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514790 [IMO 4 138.00] CKT 1 | 48.5472 | PASS | 10.9376 | PASS | 10837.6491 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514731 [SO4TH 4 138.00] TO BUS 514815 [BRECKNR4 138.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6256 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 514827 [CTNWOOD4 138.00] CKT 1 | 48.4812 | PASS | 10.9377 | PASS | 10837.6793 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514733 [MARSHL 4 138.00] TO BUS 521006 [MARSHAL4 138.00] CKT 1 | 48.558 | PASS | 10.9376 | PASS | 10837.6438 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514737 [OTOE 4 138.00] TO BUS 515978 [OTOETAP4 138.00] CKT 1 | 48.5572 | PASS | 10.9376 | PASS | 10837.6352 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 515402 [CONBLKT2 69.00] CKT 1 | 48.5554 | PASS | 10.9376 | PASS | 10837.6321 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 515947 [CONTCBN2 69.00] CKT 1 | 48.5343 | PASS | 10.9375 | PASS | 10837.5452 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 529241 [OMMORANT 69.00] CKT 1 | 48.478 | PASS | 10.9377 | PASS | 10837.7455 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 529249 [OMWW 69.00] CKT 1 | 48.5178 | PASS | 10.9377 | PASS | 10837.6545 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514758 [STDBEAR4 138.00] CKT 1 | 48.5592 | PASS | 10.9377 | PASS | 10837.6751 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 48.5535 | PASS | 10.9376 | PASS | 10837.6344 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514770 [MARLNDT4 138.00] CKT 1 | 48.56 | PASS | 10.9377 | PASS | 10837.6623 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514743 [OSAGE 4 138.00] TO BUS 514798 [SNRPMPT4 138.00] CKT 1 | 48.4467 | PASS | 10.938 | PASS | 10837.9922 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514745 [CHERPLT2 69.00] TO BUS 515402 [CONBLKT2 69.00] CKT 1 | 48.5554 | PASS | 10.9376 | PASS | 10837.6321 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514748 [CONTEMP4 138.00] TO BUS 514753 [CONORTH4 138.00] CKT 1 | 48.5576 | PASS | 10.9376 | PASS | 10837.6367 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514748 [CONTEMP4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 48.5567 | PASS | 10.9376 | PASS | 10837.6305 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514753 [CONORTH4 138.00] TO BUS 514758 [STDBEAR4 138.00] CKT 1 | 48.5582 | PASS | 10.9376 | PASS | 10837.6484 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 514760 [KILDARE4 138.00] CKT 1 | 48.5588 | PASS | 10.9376 | PASS | 10837.5782 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514761 [WHEAGLE4 138.00] CKT 1 | 48.5432 | PASS | 10.9377 | PASS | 10837.7071 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514760 [KILDARE4 138.00] TO BUS 514764 [NWKRKAT4 138.00] CKT 1 | 48.5315 | PASS | 10.9386 | PASS | 10838.6451 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514761 [WHEAGLE4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 48.4715 | PASS | 10.9379 | PASS | 10837.9417 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514768 [WF KAY 2 69.00] TO BUS 514800 [BRRDTP 2 69.00] CKT 1 | 48.5569 | PASS | 10.9376 | PASS | 10837.6206 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514768 [WF KAY 2 69.00] TO BUS 521034 [PERRY 2 69.00] CKT 1 | 48.5582 | PASS | 10.9376 | PASS | 10837.6449 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514770 [MARLNDT4 138.00] TO BUS 515542 [CWBOYHT4 138.00] CKT 1 | 48.5598 | PASS | 10.9377 | PASS | 10837.6691 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514770 [MARLNDT4 138.00] TO BUS 521007 [MARLAND_138 138.00] CKT 1 | 48.5583 | PASS | 10.9376 | PASS | 10837.6488 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514798 [SNRPMPT4 138.00] TO BUS 514799 [SNRPMP 4 138.00] CKT 1 | 48.5573 | PASS | 10.9376 | PASS | 10837.6161 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514798 [SNRPMPT4 138.00] TO BUS 514802 [SOONER 4 138.00] CKT 1 | 48.446 | PASS | 10.938 | PASS | 10837.9767 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 48.4287 | PASS | 10.9376 | PASS | 10837.6404 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515444 [MCNOWND7 345.00] CKT 1 | 48.5769 | PASS | 10.9359 | PASS | 10835.8975 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515549 [MNCWND37 345.00] CKT 1 | 48.581 | PASS | 10.9359 | PASS | 10835.8507 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 515800 [GRACMNT7 345.00] CKT 1 | 48.4418 | PASS | 10.9388 | PASS | 10838.8332 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 48.5431 | PASS | 10.9378 | PASS | 10837.7702 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 761250 [GEN-2017-233 345.00] CKT 1 | 48.5727 | PASS | 10.9365 | PASS | 10836.5003 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 914801 [MINCO_IV__HV 345.00] CKT 1 | 48.561 | PASS | 10.9375 | PASS | 10837.5461 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514801 [MINCO 7 345.00] TO BUS 914807 [MINCO_I_&_HV 345.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6276 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 48.4444 | PASS | 10.9379 | PASS | 10837.9117 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515576 [RANCHRD7 345.00] CKT 1 | 43.0902 | PASS | 10.943 | PASS | 10842.9733 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515894 [THUNDER7 345.00] CKT 1 | 48.7599 | PASS | 10.9415 | PASS | 10841.5283 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 41.6014 | PASS | 10.471 | PASS | 10370.9882 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516010 [PINTAIL7 345.00] CKT 1 | 42.176 | PASS | 10.9472 | PASS | 10847.158 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 41.4911 | PASS | 10.9371 | PASS | 10837.0601 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 784020 [G24-235-TAP 345.00] CKT 1 | 43.7189 | PASS | 10.9414 | PASS | 10841.3985 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 515641 [PLNSMEN4 138.00] CKT 1 | 48.5543 | PASS | 10.9376 | PASS | 10837.6359 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514820 [JENSENT4 138.00] CKT 1 | 48.5584 | PASS | 10.9376 | PASS | 10837.6303 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.5899 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.5859 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514825 [KAYWIND7 345.00] TO BUS 515621 [OPENSKY7 345.00] CKT 1 | 48.5446 | PASS | 10.9386 | PASS | 10838.6202 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514829 [PINE ST4 138.00] CKT 1 | 48.5354 | PASS | 10.9382 | PASS | 10838.1956 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 48.5264 | PASS | 10.9378 | PASS | 10837.8396 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515373 [LBRTYLK4 138.00] CKT 1 | 48.5452 | PASS | 10.9376 | PASS | 10837.5963 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514827 [CTNWOOD4 138.00] TO BUS 515377 [CRESENT4 138.00] CKT 1 | 48.561 | PASS | 10.9376 | PASS | 10837.5697 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514834 [KETCH 4 138.00] CKT 1 | 48.5446 | PASS | 10.9376 | PASS | 10837.6351 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 48.5554 | PASS | 10.9377 | PASS | 10837.7138 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514828 [KETCHTP4 138.00] TO BUS 515466 [MITCHSB4 138.00] CKT 1 | 48.5476 | PASS | 10.9377 | PASS | 10837.7029 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514851 [QUAILCK4 138.00] TO BUS 514852 [SLVRLAK4 138.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6428 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514851 [QUAILCK4 138.00] TO BUS 514873 [LNEOAK 4 138.00] CKT 1 | 48.5549 | PASS | 10.9377 | PASS | 10837.6603 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514852 [SLVRLAK4 138.00] TO BUS 514854 [BRADEN 4 138.00] CKT 1 | 48.5423 | PASS | 10.9377 | PASS | 10837.7102 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514854 [BRADEN 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 48.5422 | PASS | 10.9377 | PASS | 10837.7246 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514862 [RICHRDS4 138.00] TO BUS 514864 [PIEDMNT4 138.00] CKT 1 | 48.5498 | PASS | 10.9377 | PASS | 10837.6706 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514863 [HAYMAKR4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 48.5573 | PASS | 10.9376 | PASS | 10837.6272 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514864 [PIEDMNT4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 48.5497 | PASS | 10.9377 | PASS | 10837.6813 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 514879 [NORTWST4 138.00] CKT 1 | 48.546 | PASS | 10.9378 | PASS | 10837.8037 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514873 [LNEOAK 4 138.00] TO BUS 515374 [CHISHOM4 138.00] CKT 1 | 48.5556 | PASS | 10.9377 | PASS | 10837.6637 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514881 [SPRNGCK7 345.00] CKT 1 | 45.9885 | PASS | 10.911 | PASS | 10810.9808 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 48.4407 | PASS | 10.9375 | PASS | 10837.5244 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 514908 [ARCADIA7 345.00] CKT 1 | 48.3641 | PASS | 10.9375 | PASS | 10837.5229 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514880 [NORTWST7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 48.5465 | PASS | 10.9372 | PASS | 10837.1784 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 41.395 | PASS | 10.9376 | PASS | 10837.613 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784620 [GEN-2024-255 345.00] CKT 3 | 48.5699 | PASS | 10.9366 | PASS | 10836.5819 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 784621 [GEN-2024-255 345.00] CKT 1 | 48.1875 | PASS | 10.9339 | PASS | 10833.9307 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514894 [CZECHAL4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 48.5507 | PASS | 10.9377 | PASS | 10837.7274 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 514898 [CIMARON4 138.00] CKT 1 | 48.5369 | PASS | 10.9377 | PASS | 10837.6535 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 48.4997 | PASS | 10.9376 | PASS | 10837.604 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 48.4999 | PASS | 10.9376 | PASS | 10837.6052 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 48.5785 | PASS | 10.9362 | PASS | 10836.1586 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 48.3742 | PASS | 10.9376 | PASS | 10837.6122 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784141 [GEN-2024-239 345.00] CKT 1 | 48.5788 | PASS | 10.9358 | PASS | 10835.7809 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784530 [GEN-2024-252 345.00] CKT 3 | 48.5664 | PASS | 10.9369 | PASS | 10836.8825 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514901 [CIMARON7 345.00] TO BUS 784531 [GEN-2024-252 345.00] CKT 1 | 48.4218 | PASS | 10.9348 | PASS | 10834.8172 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514907 [ARCADIA4 138.00] CKT 1 | 48.5563 | PASS | 10.9378 | PASS | 10837.7872 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515461 [RNDBARN4 138.00] CKT 1 | 48.5607 | PASS | 10.9376 | PASS | 10837.5748 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 515465 [LGARBER4 138.00] CKT 1 | 48.5572 | PASS | 10.9377 | PASS | 10837.656 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 1 | 48.5562 | PASS | 10.9377 | PASS | 10837.6544 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 2 | 48.5559 | PASS | 10.9377 | PASS | 10837.6564 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 514909 [REDBUD 7 345.00] CKT 3 | 48.5557 | PASS | 10.9377 | PASS | 10837.6715 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 48.4856 | PASS | 10.9376 | PASS | 10837.5548 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 1 | 48.5669 | PASS | 10.9379 | PASS | 10837.8893 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 2 | 48.5669 | PASS | 10.9379 | PASS | 10837.8893 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514908 [ARCADIA7 345.00] TO BUS 760032 [GEN-2017-133 345.00] CKT 3 | 48.5669 | PASS | 10.9379 | PASS | 10837.8893 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 48.4672 | PASS | 10.9379 | PASS | 10837.8639 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 48.5412 | PASS | 10.9376 | PASS | 10837.5532 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 2 | 48.5412 | PASS | 10.9376 | PASS | 10837.5532 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 515045 [SEMINOL7 345.00] CKT 3 | 48.5499 | PASS | 10.9376 | PASS | 10837.6396 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 1 | 48.5479 | PASS | 10.9377 | PASS | 10837.7272 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 516096 [NORMHLL7 345.00] CKT 2 | 48.5469 | PASS | 10.9377 | PASS | 10837.7371 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 48.5363 | PASS | 10.9378 | PASS | 10837.7724 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515006 [MORRISN4 138.00] TO BUS 778650 [G24-056-TAP 138.00] CKT 1 | 48.5364 | PASS | 10.9378 | PASS | 10837.7946 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515008 [KINZE 4 138.00] TO BUS 515181 [UNVRSTY4 138.00] CKT 1 | 48.5112 | PASS | 10.938 | PASS | 10837.974 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515009 [MCELROY4 138.00] TO BUS 515011 [STILWTR4 138.00] CKT 1 | 48.5085 | PASS | 10.9382 | PASS | 10838.1747 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515009 [MCELROY4 138.00] TO BUS 515181 [UNVRSTY4 138.00] CKT 1 | 48.5108 | PASS | 10.938 | PASS | 10838.028 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515447 [MORISNT4 138.00] CKT 1 | 48.2876 | PASS | 10.9382 | PASS | 10838.1771 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515011 [STILWTR4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 48.4528 | PASS | 10.9378 | PASS | 10837.824 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515033 [CUSHING4 138.00] TO BUS 515039 [PAYNESB4 138.00] CKT 1 | 48.5392 | PASS | 10.9377 | PASS | 10837.6935 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515039 [PAYNESB4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 48.5389 | PASS | 10.9377 | PASS | 10837.6753 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 48.5373 | PASS | 10.9401 | PASS | 10840.1162 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 786601 [GEN-2024-321 345.00] CKT 1 | 48.5496 | PASS | 10.9339 | PASS | 10833.9049 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 48.5436 | PASS | 10.9378 | PASS | 10837.7589 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 48.5325 | PASS | 10.9381 | PASS | 10838.0922 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 516210 [RAVEN 7 345.00] CKT 1 | 48.5512 | PASS | 10.9385 | PASS | 10838.507 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 515778 [GRIFFIN7 345.00] CKT 1 | 48.5224 | PASS | 10.9376 | PASS | 10837.5519 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515235 [PECANCK7 345.00] TO BUS 762823 [GEN-2018-048 345.00] CKT 1 | 48.5624 | PASS | 10.9375 | PASS | 10837.4542 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 1 | 48.5305 | PASS | 10.9384 | PASS | 10838.3813 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515407 [TATONGA7 345.00] CKT 2 | 48.5299 | PASS | 10.9384 | PASS | 10838.3965 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515400 [DMANCRK4 138.00] TO BUS 515412 [DMNCRKT4 138.00] CKT 1 | 48.5564 | PASS | 10.9376 | PASS | 10837.6268 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515403 [FNTANTP4 138.00] TO BUS 515542 [CWBOYHT4 138.00] CKT 1 | 48.5595 | PASS | 10.9377 | PASS | 10837.6641 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515448 [CRSRDSW7 345.00] CKT 1 | 48.5657 | PASS | 10.937 | PASS | 10837.0467 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 1 | 48.5386 | PASS | 10.9379 | PASS | 10837.924 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515497 [MATHWSN7 345.00] CKT 2 | 48.5385 | PASS | 10.9379 | PASS | 10837.9237 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515582 [SLNGWND7 345.00] CKT 1 | 48.583 | PASS | 10.9356 | PASS | 10835.6061 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515407 [TATONGA7 345.00] TO BUS 515585 [MAMTHPW7 345.00] CKT 1 | 48.5648 | PASS | 10.9365 | PASS | 10836.537 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515477 [CHSHLMV7 345.00] CKT 1 | 48.5655 | PASS | 10.9372 | PASS | 10837.1999 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515476 [HUNTERS7 345.00] TO BUS 515543 [RENFROW7 345.00] CKT 1 | 47.7778 | PASS | 10.9085 | PASS | 10808.5299 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 515875 [REDNGTN7 345.00] CKT 1 | 45.8736 | PASS | 10.9366 | PASS | 10836.6456 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 516036 [TRAV3WD7 345.00] CKT 1 | 48.5855 | PASS | 10.9366 | PASS | 10836.6107 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784590 [GEN-2024-254 345.00] CKT 3 | 48.5667 | PASS | 10.9369 | PASS | 10836.8564 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515497 [MATHWSN7 345.00] TO BUS 784591 [GEN-2024-254 345.00] CKT 1 | 48.3706 | PASS | 10.9347 | PASS | 10834.7461 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515514 [KNIPE 4 138.00] TO BUS 515574 [SPGVLLY4 138.00] CKT 1 | 48.5225 | PASS | 10.9377 | PASS | 10837.7239 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515514 [KNIPE 4 138.00] TO BUS 515675 [TRYON 4 138.00] CKT 1 | 48.5227 | PASS | 10.9377 | PASS | 10837.7344 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515646 [GRNTWD 7 345.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.6003 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 47.8963 | PASS | 10.909 | PASS | 10809.0015 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515546 [GRANTCO4 138.00] CKT 1 | 48.5597 | PASS | 10.9377 | PASS | 10837.667 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 515569 [MDFRDTP4 138.00] CKT 1 | 48.5614 | PASS | 10.9375 | PASS | 10837.5059 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515544 [RENFROW4 138.00] TO BUS 520409 [WFEC_RNFRO4 138.00] CKT 1 | 48.5004 | PASS | 10.9376 | PASS | 10837.6375 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515621 [OPENSKY7 345.00] CKT 1 | 44.5862 | PASS | 10.9106 | PASS | 10810.5588 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 515688 [FRNTWND7 345.00] CKT 1 | 48.5706 | PASS | 10.9383 | PASS | 10838.3433 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 529200 [OMCDLEC7 345.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.61 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 48.5332 | PASS | 10.9401 | PASS | 10840.077 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515576 [RANCHRD7 345.00] TO BUS 786991 [GEN-2024-334 345.00] CKT 1 | 47.4925 | PASS | 10.9379 | PASS | 10837.9432 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515600 [KNGFSHR7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 48.5684 | PASS | 10.9369 | PASS | 10836.8961 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515605 [CANADN7 345.00] TO BUS 515610 [FSHRTAP7 345.00] CKT 1 | 48.5683 | PASS | 10.9368 | PASS | 10836.8138 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515621 [OPENSKY7 345.00] TO BUS 532837 [G15052_T 345.00] CKT 1 | 44.5294 | PASS | 10.9108 | PASS | 10810.7921 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 516363 [ARMADILLO_HV 138.00] CKT 1 | 48.5608 | PASS | 10.9375 | PASS | 10837.4527 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515875 [REDNGTN7 345.00] TO BUS 515877 [REDDIRT7 345.00] CKT 1 | 48.5696 | PASS | 10.9372 | PASS | 10837.1621 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765470 [GEN-2021-018 345.00] CKT 1 | 48.6367 | PASS | 10.9398 | PASS | 10839.7741 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 765480 [GEN-2021-019 345.00] CKT 1 | 48.5727 | PASS | 10.9363 | PASS | 10836.3096 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515974 [GEN-2015-066 345.00] TO BUS 515975 [G15-066T 345.00] CKT 1 | 48.6313 | PASS | 10.9286 | PASS | 10828.6175 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 588190 [GEN-2016-128 345.00] CKT 1 | 48.5724 | PASS | 10.9368 | PASS | 10836.764 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516010 [PINTAIL7 345.00] TO BUS 516019 [KINGWD 7 345.00] CKT 1 | 48.589 | PASS | 10.9366 | PASS | 10836.5726 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516045 [TRAV2WD7 345.00] CKT 1 | 48.5782 | PASS | 10.9366 | PASS | 10836.5698 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516036 [TRAV3WD7 345.00] TO BUS 516086 [TRAV3WZ7 345.00] CKT 1 | 48.5605 | PASS | 10.9376 | PASS | 10837.5599 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516066 [FRNT2WD7 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 48.5583 | PASS | 10.9399 | PASS | 10839.9018 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516359 [MCCLAIN7 345.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6443 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 777361 [GEN-2024-013 345.00] CKT 1 | 48.497 | PASS | 10.9332 | PASS | 10833.2108 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516192 [WAGNWTIE7 345.00] TO BUS 516198 [WAGNWL7 345.00] CKT 1 | 48.5847 | PASS | 10.9352 | PASS | 10835.1695 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516192 [WAGNWTIE7 345.00] TO BUS 516207 [GADWALL7 345.00] CKT 1 | 48.6045 | PASS | 10.9333 | PASS | 10833.2639 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520442 [SHIDWFC4 138.00] TO BUS 520443 [WEBBCTY4 138.00] CKT 1 | 48.5577 | PASS | 10.9376 | PASS | 10837.6207 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520461 [GARBER 4 138.00] TO BUS 521100 [WARREN 4 138.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6463 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529241 [OMMORANT 69.00] TO BUS 529242 [OMHUFFYT 69.00] CKT 1 | 48.4783 | PASS | 10.9378 | PASS | 10837.7548 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529248 [OMPECANT 69.00] TO BUS 529249 [OMWW 69.00] CKT 1 | 48.5178 | PASS | 10.9377 | PASS | 10837.6558 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532780 [CANEYRV7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 48.3488 | PASS | 10.9382 | PASS | 10838.2199 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 48.2212 | PASS | 10.9368 | PASS | 10836.7999 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 48.4663 | PASS | 10.9384 | PASS | 10838.4319 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 48.3732 | PASS | 10.9384 | PASS | 10838.3866 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 48.2411 | PASS | 10.9386 | PASS | 10838.6082 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 48.3521 | PASS | 10.9386 | PASS | 10838.6439 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532837 [G15052_T 345.00] CKT 1 | 44.3992 | PASS | 10.9103 | PASS | 10810.3346 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 48.2086 | PASS | 10.9062 | PASS | 10806.1961 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 48.4964 | PASS | 10.9385 | PASS | 10838.4885 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 48.5626 | PASS | 10.9381 | PASS | 10838.0628 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 48.5242 | PASS | 10.9375 | PASS | 10837.5106 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 47.8857 | PASS | 10.9089 | PASS | 10808.9005 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532800 [LATHAMS7 345.00] TO BUS 532801 [ELKRVR17 345.00] CKT 1 | 48.5591 | PASS | 10.9377 | PASS | 10837.6783 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532837 [G15052_T 345.00] TO BUS 562900 [G15052_1 345.00] CKT 1 | 48.5604 | PASS | 10.9388 | PASS | 10838.8315 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 48.5513 | PASS | 10.9374 | PASS | 10837.4437 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 48.557 | PASS | 10.9374 | PASS | 10837.387 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533068 [STEARMN4 138.00] CKT 1 | 48.5584 | PASS | 10.9376 | PASS | 10837.616 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533062 [ROSEHIL4 138.00] TO BUS 533068 [STEARMN4 138.00] CKT 1 | 48.5561 | PASS | 10.9375 | PASS | 10837.5026 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762342 [GEN-2017-178 345.00] CKT 1 | 48.5713 | PASS | 10.9372 | PASS | 10837.2314 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763065 [GEN-2018-071 345.00] TO BUS 763069 [G18-071-TAP 345.00] CKT 1 | 48.5466 | PASS | 10.9367 | PASS | 10836.6615 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763417 [GEN-2018-128 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 48.5607 | PASS | 10.9377 | PASS | 10837.7114 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 770500 [G22-176-TAP 345.00] TO BUS 770501 [GEN-2022-176 345.00] CKT 1 | 48.5577 | PASS | 10.9383 | PASS | 10838.314 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 778650 [G24-056-TAP 138.00] TO BUS 778651 [GEN-2024-056 138.00] CKT 0 | 48.5676 | PASS | 10.9378 | PASS | 10837.7987 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 782100 [G24-171-TAP 345.00] TO BUS 782101 [GEN-2024-171 345.00] CKT 1 | 48.5443 | PASS | 10.9405 | PASS | 10840.4816 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784020 [G24-235-TAP 345.00] TO BUS 784021 [GEN-2024-235 345.00] CKT 1 | 48.6389 | PASS | 10.9317 | PASS | 10831.7134 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786991 [GEN-2024-334 345.00] TO BUS 786998 [G24-334-C1 345.00] CKT 2 | 48.0412 | PASS | 10.9377 | PASS | 10837.7414 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786991 [GEN-2024-334 345.00] TO BUS 786999 [G24-334-C2 345.00] CKT 2 | 48.0412 | PASS | 10.9377 | PASS | 10837.7413 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 300686 [4WOODY 138.00] CKT 1 | 48.5535 | PASS | 10.9376 | PASS | 10837.6435 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 300889 [2BRIISTOW 69.00] CKT 2 | 48.5568 | PASS | 10.9376 | PASS | 10837.638 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300137 [4BRISTOW 138.00] TO BUS 910314 [GI103_GEN1 20.00] CKT 1 | 48.4803 | PASS | 10.9374 | PASS | 10837.4051 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300138 [4CLEVLND 138.00] TO BUS 910514 [GI105_GEN1 20.00] CKT 1 | 47.7396 | PASS | 10.9364 | PASS | 10836.4452 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 300929 [2FAIRFAX 69.00] CKT 1 | 48.5579 | PASS | 10.9377 | PASS | 10837.6929 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 300929 [2FAIRFAX 69.00] CKT 2 | 48.5579 | PASS | 10.9377 | PASS | 10837.6929 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 300844 [4RAMSEY 138.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.6451 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301413 [2STILWTRKAMO 69.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.6295 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301413 [2STILWTRKAMO 69.00] CKT 2 | 48.5581 | PASS | 10.9376 | PASS | 10837.6295 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301603 [4RPLY 138.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.6354 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 512731 [NORTHTP4 138.00] CKT 1 | 48.5584 | PASS | 10.9376 | PASS | 10837.6497 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300145 [4FISHER 138.00] TO BUS 300931 [2FISHER 69.00] CKT 2 | 48.5551 | PASS | 10.9376 | PASS | 10837.6069 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300943 [2SILVCTY 69.00] TO BUS 300936 [2MANFORD 69.00] CKT 1 | 48.558 | PASS | 10.9376 | PASS | 10837.6162 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300943 [2SILVCTY 69.00] TO BUS 301630 [2SILVCTYLD 69.00] CKT 1 | 48.5585 | PASS | 10.9375 | PASS | 10837.5265 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300943 [2SILVCTY 69.00] TO BUS 301631 [2SILVCTYTP 69.00] CKT 1 | 48.5573 | PASS | 10.9378 | PASS | 10837.7908 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300996 [4JAVINE 138.00] TO BUS 301339 [4SFORKKTP 138.00] CKT 1 | 48.5115 | PASS | 10.9367 | PASS | 10836.6683 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 301369 [4REMNGTON 138.00] TO BUS 301379 [4OSAGEWIND 138.00] CKT 1 | 48.5567 | PASS | 10.9379 | PASS | 10837.948 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 505609 [KEYSTON5 161.00] TO BUS 505610 [KEYSTON4 138.00] CKT 1 | 48.5297 | PASS | 10.9373 | PASS | 10837.2763 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509739 [CARSN-T4 138.00] TO BUS 509724 [36&OLY-4 138.00] CKT 1 | 48.5225 | PASS | 10.9376 | PASS | 10837.5851 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509739 [CARSN-T4 138.00] TO BUS 509740 [UNIONAV4 138.00] CKT 1 | 48.557 | PASS | 10.9376 | PASS | 10837.6214 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 506945 [CHAMSPR7 345.00] CKT 1 | 48.5006 | PASS | 10.9067 | PASS | 10806.6613 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509745 [CLARKSV7 345.00] TO BUS 760389 [GEN-2017-140 345.00] CKT 1 | 48.5639 | PASS | 10.9377 | PASS | 10837.6597 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509746 [DENVTAP4 138.00] TO BUS 509743 [DENVR-E4 138.00] CKT 1 | 48.5585 | PASS | 10.9377 | PASS | 10837.7329 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509746 [DENVTAP4 138.00] TO BUS 509822 [W.ED.-E4 138.00] CKT 1 | 48.5578 | PASS | 10.9375 | PASS | 10837.4955 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509755 [WEKIWA-7 345.00] TO BUS 509757 [WEKIWA-4 138.00] CKT 1 | 48.3461 | PASS | 10.9373 | PASS | 10837.3024 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509758 [PRATTV-4 138.00] TO BUS 515242 [BLUEBEL4 138.00] CKT 1 | 48.5448 | PASS | 10.9375 | PASS | 10837.5347 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509773 [RSS T1 4 138.00] TO BUS 509782 [R.S.S.-7 345.00] CKT 1 | 48.5561 | PASS | 10.9376 | PASS | 10837.569 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509782 [R.S.S.-7 345.00] TO BUS 509875 [RSS T2 4 138.00] CKT 1 | 48.5561 | PASS | 10.9376 | PASS | 10837.5574 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509775 [136YALE4 138.00] CKT 1 | 48.556 | PASS | 10.9378 | PASS | 10837.7634 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509814 [S HILLWT4 138.00] CKT 1 | 48.5574 | PASS | 10.9377 | PASS | 10837.7181 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509849 [ORU ETP4 138.00] CKT 1 | 48.558 | PASS | 10.938 | PASS | 10837.9565 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509850 [OAKSETP4 138.00] CKT 1 | 48.5566 | PASS | 10.9378 | PASS | 10837.767 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 509853 [ORU-WTP4 138.00] CKT 1 | 48.5578 | PASS | 10.9379 | PASS | 10837.8913 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 510898 [OKMULGE4 138.00] CKT 1 | 48.5538 | PASS | 10.9377 | PASS | 10837.6529 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 510904 [EXP_OKM4 138.00] CKT 1 | 48.5538 | PASS | 10.9377 | PASS | 10837.6531 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 511842 [RSS1-1 24.00] CKT 1 | 48.4303 | PASS | 10.9379 | PASS | 10837.8757 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 511843 [RSS2-1 22.00] CKT 1 | 48.556 | PASS | 10.9376 | PASS | 10837.6438 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 515473 [EXPGLNT4 138.00] CKT 1 | 48.5572 | PASS | 10.938 | PASS | 10838.0262 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509783 [R.S.S.-4 138.00] TO BUS 511844 [RSS NG3 13.8.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6277 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509724 [36&OLY-4 138.00] CKT 1 | 48.5245 | PASS | 10.9378 | PASS | 10837.7538 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509756 [CARSN-S4 138.00] CKT 1 | 48.5579 | PASS | 10.9377 | PASS | 10837.6962 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509800 [36LEWIS4 138.00] CKT 1 | 48.5459 | PASS | 10.9379 | PASS | 10837.9041 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509814 [S HILLWT4 138.00] CKT 1 | 48.557 | PASS | 10.9377 | PASS | 10837.7037 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509850 [OAKSETP4 138.00] CKT 1 | 48.5562 | PASS | 10.9377 | PASS | 10837.7416 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 511854 [TPS2-1 14.4.00] CKT 1 | 48.501 | PASS | 10.9373 | PASS | 10837.3376 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 511858 [TPS4-1 14.4.00] CKT 1 | 48.5573 | PASS | 10.9376 | PASS | 10837.6062 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 762625 [GEN-2018-027 138.00] CKT 1 | 48.5608 | PASS | 10.9375 | PASS | 10837.5347 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 999996 [ZSWSH_999996 138.00] CKT 1 | 48.5628 | PASS | 10.9378 | PASS | 10837.8016 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509788 [T.P.S.-4 138.00] TO BUS 509789 [T.P.S.-2 69.00] CKT 1 | 48.5582 | PASS | 10.9376 | PASS | 10837.6258 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509768 [BA101ST4 138.00] CKT 1 | 48.558 | PASS | 10.9376 | PASS | 10837.6096 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509769 [BA101-N4 138.00] CKT 1 | 48.5582 | PASS | 10.9377 | PASS | 10837.6641 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509786 [BA.N-ST4 138.00] CKT 1 | 48.5498 | PASS | 10.9387 | PASS | 10838.709 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509869 [121LYNN4 138.00] CKT 1 | 48.5587 | PASS | 10.9377 | PASS | 10837.665 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509891 [BA_71ST4 138.00] CKT 1 | 48.5582 | PASS | 10.9377 | PASS | 10837.6663 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] CKT 1 | 48.5574 | PASS | 10.9377 | PASS | 10837.7059 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] CKT 2 | 48.5574 | PASS | 10.9377 | PASS | 10837.7074 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509806 [ONETA--4 138.00] TO BUS 509807 [ONETA--7 345.00] CKT 3 | 48.5573 | PASS | 10.9377 | PASS | 10837.7157 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509821 [HWY20-T4 138.00] TO BUS 509897 [WLDCT_HIL4 138.00] CKT 1 | 48.5579 | PASS | 10.9376 | PASS | 10837.6199 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511953 [COGEN G1 18.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6274 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511955 [COGEN G2 18.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6274 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509834 [COGENT 7 345.00] TO BUS 511957 [COGEN G3 18.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6274 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511938 [OECSTM 1 18.00] CKT 1 | 48.509 | PASS | 10.9376 | PASS | 10837.5886 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511939 [OECGT1-1 18.00] CKT 1 | 48.5226 | PASS | 10.9376 | PASS | 10837.5977 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511940 [OECGT1-2 18.00] CKT 1 | 48.5222 | PASS | 10.9376 | PASS | 10837.5997 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511941 [OECSTM 2 18.00] CKT 1 | 48.509 | PASS | 10.9376 | PASS | 10837.5886 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511942 [OECGT2-1 18.00] CKT 1 | 48.5226 | PASS | 10.9376 | PASS | 10837.5977 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509836 [OEC 7 345.00] TO BUS 511943 [OECGT2-2 18.00] CKT 1 | 48.5222 | PASS | 10.9376 | PASS | 10837.5997 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509839 [CDC-ET 4 138.00] TO BUS 509714 [CIP 4 138.00] CKT 1 | 48.5582 | PASS | 10.9376 | PASS | 10837.6499 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509839 [CDC-ET 4 138.00] TO BUS 509887 [OWAS88_4 138.00] CKT 1 | 48.5108 | PASS | 10.9375 | PASS | 10837.5108 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509842 [CDC-WT 4 138.00] TO BUS 509784 [A.A.---4 138.00] CKT 1 | 48.5377 | PASS | 10.9375 | PASS | 10837.4682 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509842 [CDC-WT 4 138.00] TO BUS 509840 [WHIRLPO4 138.00] CKT 1 | 48.558 | PASS | 10.9376 | PASS | 10837.6108 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509844 [OWASOTP4 138.00] TO BUS 509726 [OWASO1_4 138.00] CKT 1 | 48.558 | PASS | 10.9375 | PASS | 10837.4817 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509844 [OWASOTP4 138.00] TO BUS 509860 [OWAS1094 138.00] CKT 1 | 48.469 | PASS | 10.9377 | PASS | 10837.7333 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509852 [T.NO.--7 345.00] TO BUS 509895 [T.NO.2-4 138.00] CKT 1 | 48.4626 | PASS | 10.9371 | PASS | 10837.125 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509870 [SAPLPRD7 345.00] TO BUS 509871 [SAPLPRD4 138.00] CKT 1 | 48.5278 | PASS | 10.9378 | PASS | 10837.8408 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509900 [46ST-TP-4 138.00] TO BUS 509837 [46ST--E4 138.00] CKT 1 | 48.5574 | PASS | 10.9374 | PASS | 10837.4215 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509900 [46ST-TP-4 138.00] TO BUS 509863 [PPTAP 4 138.00] CKT 1 | 48.5383 | PASS | 10.9375 | PASS | 10837.5032 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509904 [AVERYDR4 138.00] TO BUS 509903 [AVERYDR2 69.00] CKT 1 | 48.5495 | PASS | 10.9376 | PASS | 10837.5916 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509908 [SKIATKTP4 138.00] TO BUS 509884 [SKIATOK4 138.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.5943 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 509908 [SKIATKTP4 138.00] TO BUS 510388 [BARNSAL4 138.00] CKT 1 | 48.5463 | PASS | 10.9372 | PASS | 10837.2354 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 48.5582 | PASS | 10.9388 | PASS | 10838.789 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 48.4964 | PASS | 10.9371 | PASS | 10837.0544 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 580555 [MONETT345 345.00] CKT 1 | 48.4805 | PASS | 10.9372 | PASS | 10837.1797 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510379 [DELWARE4 138.00] CKT 1 | 48.5582 | PASS | 10.9375 | PASS | 10837.4884 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510382 [WPAWHSK4 138.00] TO BUS 510412 [WESTERNWALL4 138.00] CKT 1 | 48.5138 | PASS | 10.9383 | PASS | 10838.2803 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 509843 [OWASO2_4 138.00] CKT 1 | 48.5527 | PASS | 10.9377 | PASS | 10837.7243 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 509854 [VERDIGS4 138.00] CKT 1 | 48.5527 | PASS | 10.9378 | PASS | 10837.7585 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 509860 [OWAS1094 138.00] CKT 1 | 48.471 | PASS | 10.938 | PASS | 10837.9925 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 510384 [WATOVA 4 138.00] CKT 1 | 48.5516 | PASS | 10.9378 | PASS | 10837.8493 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 510385 [RICE CK4 138.00] CKT 1 | 48.5464 | PASS | 10.9381 | PASS | 10838.0831 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 510413 [HAWTHRN4 138.00] CKT 1 | 48.5522 | PASS | 10.9378 | PASS | 10837.7854 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511836 [NES1-1 14.4.00] CKT 1 | 48.5279 | PASS | 10.9378 | PASS | 10837.8043 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511837 [NES1-1A 18.00] CKT 1 | 48.5236 | PASS | 10.9379 | PASS | 10837.8957 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511838 [NES1-1B 18.00] CKT 1 | 48.524 | PASS | 10.9379 | PASS | 10837.8962 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 511839 [NES2-1 22.00] CKT 1 | 48.4238 | PASS | 10.9383 | PASS | 10838.2564 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510396 [N.E.S.-4 138.00] TO BUS 513124 [OOLOGAH 4 138.00] CKT 1 | 48.558 | PASS | 10.9381 | PASS | 10838.0665 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 510911 [VALIANT7 345.00] CKT 1 | 48.5388 | PASS | 10.9376 | PASS | 10837.5641 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 510925 [KIOWA 7 345.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6278 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 514809 [JOHNCO 7 345.00] CKT 1 | 48.5584 | PASS | 10.9378 | PASS | 10837.8426 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 515422 [C-RIVER7 345.00] CKT 1 | 48.5428 | PASS | 10.9393 | PASS | 10839.2685 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 510907 [PITTSB-7 345.00] TO BUS 763131 [GEN-2018-082 345.00] CKT 1 | 48.5651 | PASS | 10.9371 | PASS | 10837.0567 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511501 [TUTTLE4 138.00] CKT 1 | 48.5472 | PASS | 10.9376 | PASS | 10837.6103 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511425 [TUTCONT4 138.00] TO BUS 511576 [CEMRD_TP4 138.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6292 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 511878 [G16133_765TN 765.00] TO BUS 511879 [G16133_765R1 765.00] CKT 1 | 48.4564 | PASS | 10.9363 | PASS | 10836.3344 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512694 [CLEVLND7 345.00] TO BUS 512729 [CLEVLND 4 138.00] CKT 1 | 47.2408 | PASS | 10.9283 | PASS | 10828.324 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512876 [OSAGEK2 69.00] TO BUS 512875 [PRUEK2 69.00] CKT 1 | 48.5509 | PASS | 10.9376 | PASS | 10837.5749 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 512876 [OSAGEK2 69.00] TO BUS 512877 [CLEVDSTK2 69.00] CKT 1 | 48.5592 | PASS | 10.9374 | PASS | 10837.4158 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 513098 [HALLETTAP 2 69.00] TO BUS 512675 [PAWNEGR2 69.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.6235 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 513098 [HALLETTAP 2 69.00] TO BUS 512877 [CLEVDSTK2 69.00] CKT 1 | 48.5588 | PASS | 10.9377 | PASS | 10837.6726 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514705 [COWCRK 2 69.00] TO BUS 514706 [COWCRK 4 138.00] CKT 2 | 48.5565 | PASS | 10.9376 | PASS | 10837.6413 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514714 [WOODRNG4 138.00] TO BUS 514715 [WOODRNG7 345.00] CKT 2 | 48.2602 | PASS | 10.9378 | PASS | 10837.7727 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514718 [VANCE 2 69.00] CKT 1 | 48.5569 | PASS | 10.9377 | PASS | 10837.655 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514722 [CLEVETP2 69.00] CKT 1 | 48.5574 | PASS | 10.9376 | PASS | 10837.6234 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514727 [ENID 2 69.00] CKT 2 | 48.5587 | PASS | 10.9376 | PASS | 10837.6278 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 515456 [CHSTNTT2 69.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.6268 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514730 [SO4TH 2 69.00] TO BUS 514731 [SO4TH 4 138.00] CKT 1 | 48.5584 | PASS | 10.9376 | PASS | 10837.6299 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 514743 [OSAGE 4 138.00] CKT 3 | 48.5056 | PASS | 10.9377 | PASS | 10837.6576 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514742 [OSGE 2 69.00] TO BUS 514743 [OSAGE 4 138.00] CKT 4 | 48.5065 | PASS | 10.9377 | PASS | 10837.6571 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514745 [CHERPLT2 69.00] TO BUS 514744 [CHILOCO2 69.00] CKT 1 | 48.5545 | PASS | 10.9376 | PASS | 10837.6369 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514745 [CHERPLT2 69.00] TO BUS 514746 [CHERKPL2 69.00] CKT 1 | 48.5577 | PASS | 10.9376 | PASS | 10837.6349 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 515581 [COYOTE 4 138.00] CKT 1 | 48.5584 | PASS | 10.9376 | PASS | 10837.6361 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514757 [CHIKASI4 138.00] TO BUS 514756 [CHIKASI2 69.00] CKT 2 | 48.5555 | PASS | 10.9376 | PASS | 10837.5987 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514764 [NWKRKAT4 138.00] TO BUS 514759 [NEWKIRK4 138.00] CKT 1 | 48.5322 | PASS | 10.9386 | PASS | 10838.5774 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514764 [NWKRKAT4 138.00] TO BUS 521012 [NEWKIR-WFEC4 138.00] CKT 1 | 48.5567 | PASS | 10.9377 | PASS | 10837.6592 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514774 [HENESEY4 138.00] TO BUS 520535 [BULFTTP4 138.00] CKT 1 | 48.4481 | PASS | 10.9376 | PASS | 10837.6444 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514790 [IMO 4 138.00] TO BUS 514734 [GLENWD 4 138.00] CKT 1 | 48.5579 | PASS | 10.9376 | PASS | 10837.6204 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514790 [IMO 4 138.00] TO BUS 514789 [MENOTAP4 138.00] CKT 1 | 48.4885 | PASS | 10.9376 | PASS | 10837.6474 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514790 [IMO 4 138.00] TO BUS 514721 [IMO 2 69.00] CKT 1 | 48.5583 | PASS | 10.9376 | PASS | 10837.6499 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514800 [BRRDTP 2 69.00] TO BUS 514766 [ORLANDO2 69.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.6176 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514800 [BRRDTP 2 69.00] TO BUS 514797 [BRONRD 2 69.00] CKT 1 | 48.5573 | PASS | 10.9376 | PASS | 10837.6246 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514805 [SOONER1G 22.00] CKT 1 | 45.9763 | PASS | 10.9079 | PASS | 10807.9203 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514802 [SOONER 4 138.00] TO BUS 514803 [SOONER 7 345.00] CKT 5 | 43.3991 | PASS | 10.9111 | PASS | 10811.1377 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514803 [SOONER 7 345.00] TO BUS 514806 [SOONER2G 20.00] CKT 1 | 41.4245 | PASS | 10.9092 | PASS | 10809.1681 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 514642 [BRCKWND4 138.00] CKT 1 | 48.5654 | PASS | 10.9369 | PASS | 10836.853 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 514701 [BUNCHCK4 138.00] CKT 1 | 48.5582 | PASS | 10.9378 | PASS | 10837.761 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514815 [BRECKNR4 138.00] TO BUS 515383 [ENIDINT4 138.00] CKT 1 | 48.5548 | PASS | 10.9377 | PASS | 10837.6938 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 515962 [OMEGA 4 138.00] CKT 1 | 48.5584 | PASS | 10.9376 | PASS | 10837.5641 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514819 [EL-RENO4 138.00] TO BUS 514818 [ELRENO 2 69.00] CKT 5 | 48.5584 | PASS | 10.9376 | PASS | 10837.6341 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514820 [JENSENT4 138.00] TO BUS 514821 [JENSEN 4 138.00] CKT 1 | 48.5579 | PASS | 10.9375 | PASS | 10837.5346 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514825 [KAYWIND7 345.00] TO BUS 515622 [KAYWND11 34.5.00] CKT 1 | 48.5517 | PASS | 10.9381 | PASS | 10838.114 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514825 [KAYWIND7 345.00] TO BUS 515623 [KAYWND12 34.5.00] CKT 1 | 48.5517 | PASS | 10.9381 | PASS | 10838.1146 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514829 [PINE ST4 138.00] TO BUS 514830 [FITZGRD4 138.00] CKT 1 | 48.535 | PASS | 10.938 | PASS | 10838.0329 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514834 [KETCH 4 138.00] TO BUS 514833 [DANFRTH4 138.00] CKT 1 | 48.5512 | PASS | 10.9377 | PASS | 10837.6537 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514834 [KETCH 4 138.00] TO BUS 515468 [FAIRFLD4 138.00] CKT 1 | 48.5577 | PASS | 10.9376 | PASS | 10837.6207 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514851 [QUAILCK4 138.00] TO BUS 514850 [SKYLINE4 138.00] CKT 1 | 48.5544 | PASS | 10.9377 | PASS | 10837.6757 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514852 [SLVRLAK4 138.00] TO BUS 514853 [DVISION4 138.00] CKT 1 | 48.5431 | PASS | 10.9376 | PASS | 10837.6276 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514862 [RICHRDS4 138.00] TO BUS 514853 [DVISION4 138.00] CKT 1 | 48.5503 | PASS | 10.9377 | PASS | 10837.6555 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514863 [HAYMAKR4 138.00] TO BUS 514853 [DVISION4 138.00] CKT 1 | 48.5573 | PASS | 10.9376 | PASS | 10837.5952 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 2 | 48.5412 | PASS | 10.9376 | PASS | 10837.607 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 3 | 48.542 | PASS | 10.9376 | PASS | 10837.6255 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514879 [NORTWST4 138.00] TO BUS 514880 [NORTWST7 345.00] CKT 4 | 48.5428 | PASS | 10.9378 | PASS | 10837.8107 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514882 [SPGCK1&2 13.8.00] CKT 1 | 48.4054 | PASS | 10.9359 | PASS | 10835.9243 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514881 [SPRNGCK7 345.00] TO BUS 514883 [SPGCK3&4 13.8.00] CKT 1 | 48.4058 | PASS | 10.9359 | PASS | 10835.924 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514894 [CZECHAL4 138.00] TO BUS 514893 [XEROX 4 138.00] CKT 1 | 48.5511 | PASS | 10.9377 | PASS | 10837.6999 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514895 [SARA 4 138.00] TO BUS 515481 [STHLAKE4 138.00] CKT 1 | 48.54 | PASS | 10.9377 | PASS | 10837.6654 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 1 | 48.5478 | PASS | 10.9379 | PASS | 10837.9102 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514898 [CIMARON4 138.00] TO BUS 514901 [CIMARON7 345.00] CKT 2 | 48.5415 | PASS | 10.9375 | PASS | 10837.4998 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 300136 [4MEMORALT 138.00] CKT 1 | 48.548 | PASS | 10.9381 | PASS | 10838.1137 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514906 [JNSKAMO4 138.00] TO BUS 514941 [HSL 4 138.00] CKT 1 | 48.5508 | PASS | 10.9376 | PASS | 10837.5754 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 2 | 48.5581 | PASS | 10.9377 | PASS | 10837.6859 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 3 | 48.5577 | PASS | 10.9376 | PASS | 10837.6458 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514907 [ARCADIA4 138.00] TO BUS 514908 [ARCADIA7 345.00] CKT 4 | 48.5575 | PASS | 10.9377 | PASS | 10837.67 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514899 [REDBUD1S 18.00] CKT 1 | 48.4636 | PASS | 10.9363 | PASS | 10836.2903 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514900 [REDBUD2S 18.00] CKT 1 | 48.4636 | PASS | 10.9363 | PASS | 10836.2923 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514905 [REDBUD3S 18.00] CKT 1 | 48.4634 | PASS | 10.9363 | PASS | 10836.3102 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514909 [REDBUD 7 345.00] TO BUS 514940 [REDBUD4S 18.00] CKT 1 | 48.4636 | PASS | 10.9363 | PASS | 10836.2903 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 514933 [DRAPER 4 138.00] CKT 2 | 48.5593 | PASS | 10.9377 | PASS | 10837.6524 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 514933 [DRAPER 4 138.00] CKT 3 | 48.5583 | PASS | 10.9375 | PASS | 10837.5197 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 514934 [DRAPER 7 345.00] TO BUS 514933 [DRAPER 4 138.00] CKT 4 | 48.5583 | PASS | 10.9375 | PASS | 10837.5197 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515008 [KINZE 4 138.00] TO BUS 512710 [KINZEGR4 138.00] CKT 1 | 48.5427 | PASS | 10.9389 | PASS | 10838.9439 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515008 [KINZE 4 138.00] TO BUS 516212 [COYLE 4 138.00] CKT 1 | 48.5349 | PASS | 10.938 | PASS | 10837.9848 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515033 [CUSHING4 138.00] TO BUS 515417 [GRNWOOD4 138.00] CKT 1 | 48.5491 | PASS | 10.9377 | PASS | 10837.7045 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515033 [CUSHING4 138.00] TO BUS 515032 [CUSHING2 69.00] CKT 3 | 48.5574 | PASS | 10.9377 | PASS | 10837.652 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515040 [SEMINL1G 20.9.00] CKT 1 | 48.523 | PASS | 10.9363 | PASS | 10836.3019 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 1 | 48.5555 | PASS | 10.9377 | PASS | 10837.6726 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 2 | 48.5567 | PASS | 10.9376 | PASS | 10837.6492 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515531 [VANOSTP4 138.00] CKT 1 | 48.5588 | PASS | 10.9376 | PASS | 10837.6474 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515977 [LKKONWA4 138.00] CKT 1 | 48.5586 | PASS | 10.9377 | PASS | 10837.6809 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 775520 [G23-177-TAP 138.00] CKT 1 | 48.5577 | PASS | 10.9376 | PASS | 10837.6244 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 1 | 48.5575 | PASS | 10.9376 | PASS | 10837.6219 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 2 | 48.5576 | PASS | 10.9376 | PASS | 10837.6243 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515045 [SEMINOL7 345.00] CKT 3 | 48.5575 | PASS | 10.9376 | PASS | 10837.6219 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515041 [SEMINL2G 17.1.00] CKT 1 | 48.5401 | PASS | 10.9356 | PASS | 10835.5721 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515045 [SEMINOL7 345.00] TO BUS 515042 [SEMINL3G 20.9.00] CKT 1 | 48.5276 | PASS | 10.9357 | PASS | 10835.7017 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515223 [MUSKOG4G 18.00] CKT 1 | 48.5236 | PASS | 10.9372 | PASS | 10837.1582 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515225 [MUSKOG5G 18.00] CKT 1 | 48.5231 | PASS | 10.9372 | PASS | 10837.1958 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515226 [MUSKOG6G 24.00] CKT 1 | 48.5128 | PASS | 10.9371 | PASS | 10837.1457 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | 48.5442 | PASS | 10.9377 | PASS | 10837.7009 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 2 | 48.5462 | PASS | 10.9378 | PASS | 10837.7582 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 516091 [OKTAHA 7 345.00] CKT 1 | 48.5536 | PASS | 10.9382 | PASS | 10838.2334 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515233 [PECANCK4 138.00] TO BUS 515249 [BEGGS 4 138.00] CKT 1 | 48.545 | PASS | 10.9377 | PASS | 10837.679 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515233 [PECANCK4 138.00] TO BUS 515235 [PECANCK7 345.00] CKT 4 | 48.5444 | PASS | 10.9377 | PASS | 10837.6601 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515228 [5TRIBES5 161.00] CKT 1 | 48.5567 | PASS | 10.9378 | PASS | 10837.7692 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515230 [AGENCY 5 161.00] CKT 1 | 48.5573 | PASS | 10.9377 | PASS | 10837.7426 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515235 [PECANCK7 345.00] CKT 1 | 48.5574 | PASS | 10.9377 | PASS | 10837.721 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515234 [PECANCK5 161.00] TO BUS 515235 [PECANCK7 345.00] CKT 2 | 48.5567 | PASS | 10.9378 | PASS | 10837.7796 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515373 [LBRTYLK4 138.00] TO BUS 514831 [WATRLOO4 138.00] CKT 1 | 48.5457 | PASS | 10.9376 | PASS | 10837.613 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515374 [CHISHOM4 138.00] TO BUS 514850 [SKYLINE4 138.00] CKT 1 | 48.5527 | PASS | 10.9376 | PASS | 10837.6441 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515374 [CHISHOM4 138.00] TO BUS 515468 [FAIRFLD4 138.00] CKT 1 | 48.5578 | PASS | 10.9376 | PASS | 10837.6219 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 48.5347 | PASS | 10.939 | PASS | 10839.0081 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 2 | 48.5347 | PASS | 10.939 | PASS | 10839.0075 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515961 [GUTHRIE7 345.00] CKT 1 | 48.586 | PASS | 10.9352 | PASS | 10835.218 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 48.5064 | PASS | 10.9373 | PASS | 10837.2669 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 48.5479 | PASS | 10.9377 | PASS | 10837.7108 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 2 | 48.5478 | PASS | 10.9377 | PASS | 10837.7109 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 763527 [GEN-2019-012 345.00] CKT 1 | 48.5727 | PASS | 10.9362 | PASS | 10836.1898 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767221 [GEN-2022-012 345.00] CKT 1 | 48.5656 | PASS | 10.9369 | PASS | 10836.9096 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 767301 [GEN-2022-016 345.00] CKT 1 | 48.5712 | PASS | 10.9364 | PASS | 10836.3607 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 2 | 48.5554 | PASS | 10.9377 | PASS | 10837.6779 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515376 [WWRDEHV4 138.00] CKT 3 | 48.5539 | PASS | 10.9377 | PASS | 10837.6776 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515377 [CRESENT4 138.00] TO BUS 516100 [HORIZON4 138.00] CKT 1 | 48.5647 | PASS | 10.9368 | PASS | 10836.7669 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515377 [CRESENT4 138.00] TO BUS 521073 [TWNLKSW4 138.00] CKT 1 | 48.5589 | PASS | 10.9376 | PASS | 10837.6254 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515403 [FNTANTP4 138.00] TO BUS 515635 [BLLNGTP4 138.00] CKT 1 | 48.5587 | PASS | 10.9377 | PASS | 10837.709 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515444 [MCNOWND7 345.00] TO BUS 515443 [MNCOWND1 34.5.00] CKT 1 | 48.5769 | PASS | 10.9359 | PASS | 10835.8974 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515450 [CRSRDW21 34.5.00] CKT 2 | 48.5631 | PASS | 10.9373 | PASS | 10837.3041 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515448 [CRSRDSW7 345.00] TO BUS 515449 [CRSRDW11 34.5.00] CKT 1 | 48.5623 | PASS | 10.9374 | PASS | 10837.3599 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515461 [RNDBARN4 138.00] TO BUS 514510 [BURGETT4 138.00] CKT 1 | 48.5605 | PASS | 10.9376 | PASS | 10837.5804 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515465 [LGARBER4 138.00] TO BUS 514842 [CHTWOOD4 138.00] CKT 1 | 48.5572 | PASS | 10.9377 | PASS | 10837.6505 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515466 [MITCHSB4 138.00] TO BUS 515467 [WHITESB4 138.00] CKT 1 | 48.5471 | PASS | 10.9377 | PASS | 10837.6769 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515479 [CHSHMVE1 34.5.00] CKT 1 | 48.5626 | PASS | 10.9374 | PASS | 10837.4059 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515477 [CHSHLMV7 345.00] TO BUS 515484 [CHSHMVW1 34.5.00] CKT 1 | 48.5636 | PASS | 10.9374 | PASS | 10837.3986 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] CKT 2 | 48.5317 | PASS | 10.9375 | PASS | 10837.5383 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515546 [GRANTCO4 138.00] TO BUS 515547 [GRANTCO2 69.00] CKT 4 | 48.5587 | PASS | 10.9377 | PASS | 10837.6671 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515549 [MNCWND37 345.00] TO BUS 515939 [MNCWND47 345.00] CKT 1 | 48.5762 | PASS | 10.9362 | PASS | 10836.2397 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515549 [MNCWND37 345.00] TO BUS 515550 [MNCWND31 34.5.00] CKT 1 | 48.565 | PASS | 10.9372 | PASS | 10837.1989 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 515426 [RDRUNNR4 138.00] CKT 1 | 48.5619 | PASS | 10.9375 | PASS | 10837.4948 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515569 [MDFRDTP4 138.00] TO BUS 522397 [MEDFORD4 138.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6479 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515583 [SLINGW11 34.5.00] CKT 1 | 48.5682 | PASS | 10.9368 | PASS | 10836.7644 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515582 [SLNGWND7 345.00] TO BUS 515632 [SILNGW21 34.5.00] CKT 2 | 48.5712 | PASS | 10.9364 | PASS | 10836.4464 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 515586 [MMTHPW11 34.5.00] CKT 2 | 48.5683 | PASS | 10.9367 | PASS | 10836.6816 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515585 [MAMTHPW7 345.00] TO BUS 915586 [MMTHPW21 34.5.00] CKT 1 | 48.5547 | PASS | 10.9375 | PASS | 10837.4579 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515600 [KNGFSHR7 345.00] TO BUS 515855 [KNGFSR11 34.5.00] CKT 1 | 48.5643 | PASS | 10.9373 | PASS | 10837.2736 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515600 [KNGFSHR7 345.00] TO BUS 515856 [KNGFSR21 34.5.00] CKT 2 | 48.5651 | PASS | 10.9372 | PASS | 10837.1821 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515605 [CANADN7 345.00] TO BUS 515606 [CANDN11 34.5.00] CKT 1 | 48.5648 | PASS | 10.9372 | PASS | 10837.1961 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515605 [CANADN7 345.00] TO BUS 515609 [CANDNT2 13.8.00] CKT 1 | 48.5648 | PASS | 10.9372 | PASS | 10837.1945 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515648 [GRNTWD12 34.5.00] CKT 1 | 48.5591 | PASS | 10.9376 | PASS | 10837.5621 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515646 [GRNTWD 7 345.00] TO BUS 515647 [GRNTWD11 34.5.00] CKT 1 | 48.5591 | PASS | 10.9376 | PASS | 10837.5678 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515675 [TRYON 4 138.00] TO BUS 515047 [WARWICK4 138.00] CKT 1 | 48.523 | PASS | 10.9376 | PASS | 10837.552 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515675 [TRYON 4 138.00] TO BUS 515453 [LNWOODT4 138.00] CKT 1 | 48.5586 | PASS | 10.9377 | PASS | 10837.6684 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515675 [TRYON 4 138.00] TO BUS 516237 [ANVIL 4 138.00] CKT 1 | 48.562 | PASS | 10.9373 | PASS | 10837.3064 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515688 [FRNTWND7 345.00] TO BUS 515689 [FRNTWD11 34.5.00] CKT 1 | 48.5653 | PASS | 10.9381 | PASS | 10838.0953 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515694 [ARMFTWD4 138.00] TO BUS 515695 [ARMFTL11 34.5.00] CKT 1 | 48.5669 | PASS | 10.9376 | PASS | 10837.642 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 48.5225 | PASS | 10.9376 | PASS | 10837.5766 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 511587 [MATO 7 345.00] CKT 1 | 48.5351 | PASS | 10.9385 | PASS | 10838.4821 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515800 [GRACMNT7 345.00] TO BUS 515802 [GRACMNT4 138.00] CKT 3 | 48.5498 | PASS | 10.9376 | PASS | 10837.609 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515878 [RDDIRT11 34.5.00] CKT 1 | 48.5648 | PASS | 10.9374 | PASS | 10837.4107 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515877 [REDDIRT7 345.00] TO BUS 515879 [RDDIRT21 34.5.00] CKT 1 | 48.5651 | PASS | 10.9374 | PASS | 10837.3665 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515891 [THNDRL21 34.5.00] CKT 1 | 48.596 | PASS | 10.9379 | PASS | 10837.8981 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515894 [THUNDER7 345.00] TO BUS 515890 [THNDRL11 34.5.00] CKT 1 | 48.6147 | PASS | 10.9383 | PASS | 10838.3035 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515947 [CONTCBN2 69.00] TO BUS 515948 [CONTCBN1 12.5.00] CKT 1 | 48.5343 | PASS | 10.9375 | PASS | 10837.545 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515974 [GEN-2015-066 345.00] TO BUS 515972 [G15-066XFMR1 34.5.00] CKT 1 | 48.6275 | PASS | 10.9278 | PASS | 10827.8493 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515990 [SKELTON7 345.00] TO BUS 515991 [SKELTL11 34.5.00] CKT 1 | 48.5811 | PASS | 10.9368 | PASS | 10836.7901 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516017 [KNGWDL11 34.5.00] CKT 1 | 48.5722 | PASS | 10.9371 | PASS | 10837.0915 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516019 [KINGWD 7 345.00] TO BUS 516018 [KNGWDL21 34.5.00] CKT 1 | 48.576 | PASS | 10.9371 | PASS | 10837.0511 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516054 [TRAV1WD7 345.00] CKT 1 | 48.5635 | PASS | 10.9375 | PASS | 10837.4831 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516087 [TRAV22Z7 345.00] CKT 1 | 48.5665 | PASS | 10.9368 | PASS | 10836.8161 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516045 [TRAV2WD7 345.00] TO BUS 516107 [TRAV21Z7 345.00] CKT 1 | 48.5605 | PASS | 10.9375 | PASS | 10837.5473 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516066 [FRNT2WD7 345.00] TO BUS 516064 [FRNT2L11 34.5.00] CKT 1 | 48.5622 | PASS | 10.9384 | PASS | 10838.3905 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516066 [FRNT2WD7 345.00] TO BUS 516065 [FRNT2L21 34.5.00] CKT 1 | 48.5529 | PASS | 10.9385 | PASS | 10838.4861 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516086 [TRAV3WZ7 345.00] TO BUS 516035 [TRAV3L11 34.5.00] CKT 1 | 48.5605 | PASS | 10.9376 | PASS | 10837.5599 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] CKT 1 | 48.5559 | PASS | 10.9377 | PASS | 10837.6841 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516096 [NORMHLL7 345.00] TO BUS 516097 [NORMHLL4 138.00] CKT 2 | 48.5559 | PASS | 10.9377 | PASS | 10837.6844 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514902 [MCCLAIN4 138.00] CKT 1 | 48.5552 | PASS | 10.9376 | PASS | 10837.6364 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514929 [PLVALLY4 138.00] CKT 1 | 48.5592 | PASS | 10.9377 | PASS | 10837.7054 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514957 [CHERYCK4 138.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6476 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516097 [NORMHLL4 138.00] TO BUS 514992 [TURNER 4 138.00] CKT 1 | 48.5592 | PASS | 10.9376 | PASS | 10837.6248 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516192 [WAGNWTIE7 345.00] TO BUS 516193 [WAGNWL11 34.5.00] CKT 1 | 48.5815 | PASS | 10.9355 | PASS | 10835.4652 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516198 [WAGNWL7 345.00] TO BUS 516194 [WAGNWL21 34.5.00] CKT 1 | 48.5847 | PASS | 10.9352 | PASS | 10835.1695 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516210 [RAVEN 7 345.00] TO BUS 515422 [C-RIVER7 345.00] CKT 1 | 48.547 | PASS | 10.9389 | PASS | 10838.8949 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516210 [RAVEN 7 345.00] TO BUS 516091 [OKTAHA 7 345.00] CKT 1 | 48.5508 | PASS | 10.9385 | PASS | 10838.5088 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516210 [RAVEN 7 345.00] TO BUS 588838 [G17-092-SWYD 345.00] CKT 1 | 48.5646 | PASS | 10.9372 | PASS | 10837.1817 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516359 [MCCLAIN7 345.00] TO BUS 516360 [MCLN 4G 17.8.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6287 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516359 [MCCLAIN7 345.00] TO BUS 516361 [MCLN 5G` 17.8.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6287 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 516363 [ARMADILLO_HV 138.00] TO BUS 516364 [ARMADILLO_T1 34.5.00] CKT 1 | 48.5608 | PASS | 10.9375 | PASS | 10837.452 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520409 [WFEC_RNFRO4 138.00] TO BUS 520434 [WAKTASW4 138.00] CKT 1 | 48.5003 | PASS | 10.9376 | PASS | 10837.6356 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 520443 [WEBBCTY4 138.00] TO BUS 520441 [HARDY 4 138.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.6141 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529200 [OMCDLEC7 345.00] TO BUS 529201 [OMCDLEC1 13.8.00] CKT 1 | 48.5581 | PASS | 10.9376 | PASS | 10837.61 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529242 [OMHUFFYT 69.00] TO BUS 529251 [OMRIGGS 69.00] CKT 1 | 48.4785 | PASS | 10.9378 | PASS | 10837.7623 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 529248 [OMPECANT 69.00] TO BUS 529246 [OMKAWS 69.00] CKT 1 | 48.518 | PASS | 10.9377 | PASS | 10837.6625 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532780 [CANEYRV7 345.00] TO BUS 532777 [NRSS7 345.00] CKT 1 | 48.3483 | PASS | 10.9382 | PASS | 10838.2303 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532780 [CANEYRV7 345.00] TO BUS 532781 [CANEYWF7 345.00] CKT 1 | 48.5573 | PASS | 10.9379 | PASS | 10837.8939 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] CKT 1 | 48.5578 | PASS | 10.9376 | PASS | 10837.5946 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] CKT 1 | 48.5579 | PASS | 10.9376 | PASS | 10837.6005 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 48.5541 | PASS | 10.9375 | PASS | 10837.4747 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 48.5544 | PASS | 10.9375 | PASS | 10837.4862 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] CKT 1 | 48.554 | PASS | 10.9375 | PASS | 10837.4741 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532771 [RENO 7 345.00] CKT 1 | 48.3772 | PASS | 10.9382 | PASS | 10838.1666 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 48.5468 | PASS | 10.9379 | PASS | 10837.8915 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 2 | 48.5468 | PASS | 10.9379 | PASS | 10837.8915 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 48.4284 | PASS | 10.939 | PASS | 10838.9607 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532994 [WICHTA11_4 138.00] CKT 1 | 48.5568 | PASS | 10.9377 | PASS | 10837.6569 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532997 [WICHTA12_4 138.00] CKT 1 | 48.5563 | PASS | 10.9377 | PASS | 10837.6611 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532751 [WCGS U1 25.00] CKT 1 | 48.312 | PASS | 10.9063 | PASS | 10806.3162 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533900 [WCGS_TX1_1 13.8.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6268 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.00] CKT 1 | 48.5588 | PASS | 10.9376 | PASS | 10837.6177 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.6308 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 532814 [FR4345KV-TAP 345.00] CKT 1 | 48.5869 | PASS | 10.9375 | PASS | 10837.474 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] CKT 2 | 48.5527 | PASS | 10.9379 | PASS | 10837.9315 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 48.5527 | PASS | 10.9379 | PASS | 10837.9315 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 48.556 | PASS | 10.938 | PASS | 10837.9517 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 48.4971 | PASS | 10.9378 | PASS | 10837.7939 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532801 [ELKRVR17 345.00] TO BUS 534016 [ER1 TX1 34.5.00] CKT 1 | 48.5586 | PASS | 10.9377 | PASS | 10837.6718 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 532988 [BELAIRE4 138.00] CKT 1 | 48.5588 | PASS | 10.9377 | PASS | 10837.65 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 532990 [MIDIAN 4 138.00] CKT 1 | 48.5559 | PASS | 10.9377 | PASS | 10837.7183 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 533024 [29TH 4 138.00] CKT 1 | 48.5587 | PASS | 10.9376 | PASS | 10837.6466 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532986 [BENTON 4 138.00] TO BUS 533052 [PARKCTY4 138.00] CKT 1 | 48.5588 | PASS | 10.9376 | PASS | 10837.55 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 532993 [TALLGRS4 138.00] CKT 1 | 48.5502 | PASS | 10.9376 | PASS | 10837.6284 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533026 [ANDOVER4 138.00] CKT 1 | 48.5555 | PASS | 10.9376 | PASS | 10837.6206 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533032 [BU11PON4 138.00] CKT 1 | 48.5583 | PASS | 10.9376 | PASS | 10837.633 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533067 [SPRNGDL4 138.00] CKT 1 | 48.559 | PASS | 10.9376 | PASS | 10837.6046 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532991 [WEAVER 4 138.00] TO BUS 533604 [WEAVER 2 69.00] CKT 2 | 48.5585 | PASS | 10.9376 | PASS | 10837.6189 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533029 [59TH ST4 138.00] CKT 1 | 48.5542 | PASS | 10.9374 | PASS | 10837.4246 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533039 [ELPASO 4 138.00] TO BUS 533059 [ELPASOE4 138.00] CKT 1 | 48.5608 | PASS | 10.9376 | PASS | 10837.6327 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533068 [STEARMN4 138.00] TO BUS 533030 [BOEINGE4 138.00] CKT 1 | 48.5525 | PASS | 10.9375 | PASS | 10837.5298 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.00] TO BUS 533626 [BURLJCT2 69.00] CKT 1 | 48.5592 | PASS | 10.9378 | PASS | 10837.7515 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.00] TO BUS 533629 [CC2SHAR2 69.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6269 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 560389 [GEN-2010-055 138.00] TO BUS 560390 [G10-055-GSU1 13.8.00] CKT 1 | 48.5529 | PASS | 10.9376 | PASS | 10837.6426 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 562901 [G15052_2 34.5.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6207 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 562901 [G15052_2 34.5.00] CKT 2 | 48.5585 | PASS | 10.9376 | PASS | 10837.6207 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 765514 [G21-023-XFM1 34.5.00] CKT 1 | 48.5552 | PASS | 10.9379 | PASS | 10837.916 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 765517 [G21-023-XFM2 34.5.00] CKT 1 | 48.5552 | PASS | 10.9379 | PASS | 10837.916 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 588190 [GEN-2016-128 345.00] TO BUS 588191 [G16-128XFMR1 34.5.00] CKT 1 | 48.5704 | PASS | 10.9367 | PASS | 10836.6893 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 760032 [GEN-2017-133 345.00] TO BUS 760053 [G17-133-XFM1 34.5.00] CKT 1 | 48.5712 | PASS | 10.9365 | PASS | 10836.4986 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 760032 [GEN-2017-133 345.00] TO BUS 760074 [G17-134-XFM1 34.5.00] CKT 1 | 48.5742 | PASS | 10.9362 | PASS | 10836.2247 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 760032 [GEN-2017-133 345.00] TO BUS 760095 [G17-137-XFM1 34.5.00] CKT 1 | 48.577 | PASS | 10.936 | PASS | 10835.9813 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 761250 [GEN-2017-233 345.00] TO BUS 761229 [GEN-2017-150 345.00] CKT 1 | 48.5626 | PASS | 10.9374 | PASS | 10837.4181 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 761250 [GEN-2017-233 345.00] TO BUS 761251 [G17-233-XFMR 34.5.00] CKT 1 | 48.5691 | PASS | 10.9367 | PASS | 10836.6529 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762321 [GEN-2017-164 345.00] TO BUS 762322 [G17-164XFM1 34.5.00] CKT 1 | 48.5615 | PASS | 10.9376 | PASS | 10837.5555 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762342 [GEN-2017-178 345.00] TO BUS 762343 [G17-178XFM1 34.5.00] CKT 1 | 48.5655 | PASS | 10.9369 | PASS | 10836.9446 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762636 [GEN-2018-028 138.00] TO BUS 762637 [G18-028XFM1 34.5.00] CKT 1 | 48.5569 | PASS | 10.9383 | PASS | 10838.3448 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 762824 [G18-048-XFM1 34.5.00] CKT 1 | 48.559 | PASS | 10.9376 | PASS | 10837.6116 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 762827 [G18-048-XFM2 34.5.00] CKT 1 | 48.559 | PASS | 10.9376 | PASS | 10837.6116 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 765774 [G21-052-XFM1 34.5.00] CKT 1 | 48.5608 | PASS | 10.9375 | PASS | 10837.4879 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 765784 [G21-053-XFM1 34.5.00] CKT 1 | 48.5589 | PASS | 10.9376 | PASS | 10837.6133 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 762823 [GEN-2018-048 345.00] TO BUS 765787 [G21-053-XFM2 34.5.00] CKT 1 | 48.5589 | PASS | 10.9376 | PASS | 10837.6133 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763065 [GEN-2018-071 345.00] TO BUS 763066 [G18-071-XFM1 34.5.00] CKT 1 | 48.5538 | PASS | 10.937 | PASS | 10837.0387 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763065 [GEN-2018-071 345.00] TO BUS 763077 [G18-072-XFM1 34.5.00] CKT 1 | 48.5554 | PASS | 10.9369 | PASS | 10836.9186 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 763417 [GEN-2018-128 345.00] TO BUS 763418 [G18-128-XFM1 34.5.00] CKT 1 | 48.5601 | PASS | 10.9377 | PASS | 10837.6875 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765200 [G20-090-TAP 345.00] TO BUS 300739 [7BLACKBERRY 345.00] CKT 1 | 48.5643 | PASS | 10.938 | PASS | 10837.9546 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765200 [G20-090-TAP 345.00] TO BUS 765190 [GEN-2020-090 345.00] CKT 1 | 48.5586 | PASS | 10.9377 | PASS | 10837.6934 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765200 [G20-090-TAP 345.00] TO BUS 768061 [GEN-2022-054 345.00] CKT 1 | 48.5585 | PASS | 10.9376 | PASS | 10837.6427 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765470 [GEN-2021-018 345.00] TO BUS 765474 [G21-018-XFM1 34.5.00] CKT 1 | 48.6169 | PASS | 10.9388 | PASS | 10838.8116 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 765480 [GEN-2021-019 345.00] TO BUS 765484 [G21-019-XFM1 34.5.00] CKT 1 | 48.5724 | PASS | 10.9363 | PASS | 10836.2959 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 766141 [G21-096-TAP 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 48.527 | PASS | 10.9366 | PASS | 10836.6078 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 766141 [G21-096-TAP 345.00] TO BUS 766140 [GEN-2021-096 345.00] CKT 1 | 48.5608 | PASS | 10.9379 | PASS | 10837.9471 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 770101 [GEN-2022-156 138.00] TO BUS 770102 [G22-156XFMR1 34.5.00] CKT 1 | 48.5599 | PASS | 10.9377 | PASS | 10837.7082 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 770501 [GEN-2022-176 345.00] TO BUS 770502 [G22-176XFMR1 34.5.00] CKT 1 | 48.5576 | PASS | 10.9383 | PASS | 10838.3121 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 773121 [GEN-2023-057 138.00] TO BUS 773122 [G23-057XFMR1 34.5.00] CKT 1 | 48.5559 | PASS | 10.9385 | PASS | 10838.4915 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 777361 [GEN-2024-013 345.00] TO BUS 777368 [GEN-2024-C1 345.00] CKT 1 | 48.5322 | PASS | 10.9354 | PASS | 10835.4112 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 777361 [GEN-2024-013 345.00] TO BUS 777369 [GEN-2024-C2 345.00] CKT 1 | 48.5333 | PASS | 10.9353 | PASS | 10835.3248 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 778651 [GEN-2024-056 138.00] TO BUS 778652 [G24-056XFMR1 34.5.00] CKT 0 | 48.5676 | PASS | 10.9378 | PASS | 10837.7985 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 782101 [GEN-2024-171 345.00] TO BUS 782102 [G24-171XFMR1 34.5.00] CKT 1 | 48.552 | PASS | 10.939 | PASS | 10838.9644 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 782101 [GEN-2024-171 345.00] TO BUS 782105 [G24-171XFMR2 34.5.00] CKT 1 | 48.5519 | PASS | 10.939 | PASS | 10838.9782 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784021 [GEN-2024-235 345.00] TO BUS 784022 [G24-235XFMR1 34.5.00] CKT 1 | 48.5655 | PASS | 10.9372 | PASS | 10837.1682 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784021 [GEN-2024-235 345.00] TO BUS 784025 [G24-235XFMR2 34.5.00] CKT 1 | 48.5657 | PASS | 10.9372 | PASS | 10837.1685 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784141 [GEN-2024-239 345.00] TO BUS 784142 [G24-239XFMR1 34.5.00] CKT 1 | 48.5788 | PASS | 10.9358 | PASS | 10835.7807 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784530 [GEN-2024-252 345.00] TO BUS 784535 [G24-252XFMR2 34.5.00] CKT 2 | 48.5664 | PASS | 10.9369 | PASS | 10836.8775 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784531 [GEN-2024-252 345.00] TO BUS 784534 [G24-252GEN1 13.8.00] CKT 1 | 48.4217 | PASS | 10.9348 | PASS | 10834.8118 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784590 [GEN-2024-254 345.00] TO BUS 784595 [G24-254XFMR2 34.5.00] CKT 2 | 48.5666 | PASS | 10.9368 | PASS | 10836.8495 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784591 [GEN-2024-254 345.00] TO BUS 784594 [G24-254GEN1 13.8.00] CKT 1 | 48.3706 | PASS | 10.9347 | PASS | 10834.7396 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784620 [GEN-2024-255 345.00] TO BUS 784625 [G24-255XFMR2 34.5.00] CKT 2 | 48.5698 | PASS | 10.9366 | PASS | 10836.5689 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 784621 [GEN-2024-255 345.00] TO BUS 784624 [G24-255GEN1 13.8.00] CKT 1 | 48.1874 | PASS | 10.9339 | PASS | 10833.9151 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 785790 [G24-294-TAP 345.00] TO BUS 765721 [G21-047-TAP 345.00] CKT 1 | 47.995 | PASS | 10.9367 | PASS | 10836.6574 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 785790 [G24-294-TAP 345.00] TO BUS 785791 [GEN-2024-294 345.00] CKT 1 | 48.5538 | PASS | 10.9394 | PASS | 10839.4493 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786604 [G24-321GEN1 18.00] CKT 1 | 48.5558 | PASS | 10.9357 | PASS | 10835.7205 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786601 [GEN-2024-321 345.00] TO BUS 786607 [G24-321GEN2 18.00] CKT 1 | 48.5558 | PASS | 10.9357 | PASS | 10835.7205 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786998 [G24-334-C1 345.00] TO BUS 786994 [G24-334GEN1 13.8.00] CKT 1 | 48.0412 | PASS | 10.9377 | PASS | 10837.7396 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 786999 [G24-334-C2 345.00] TO BUS 786997 [G24-334GEN2 13.8.00] CKT 1 | 48.0412 | PASS | 10.9377 | PASS | 10837.7388 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914715 [SKELETON__HV 345.00] TO BUS 914717 [SKELETON__T1 34.5.00] CKT 1 | 48.5673 | PASS | 10.9368 | PASS | 10836.8112 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914720 [SKELETON__HV 345.00] TO BUS 914722 [SKELETON__T1 34.5.00] CKT 1 | 48.5616 | PASS | 10.9374 | PASS | 10837.4019 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914801 [MINCO_IV__HV 345.00] TO BUS 914802 [MINCO IV HV2 345.00] CKT 1 | 48.5609 | PASS | 10.9375 | PASS | 10837.5173 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 914807 [MINCO_I_&_HV 345.00] TO BUS 914809 [MINCO_I_&_T1 34.5.00] CKT 1 | 48.5586 | PASS | 10.9376 | PASS | 10837.6275 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300139 [4FAIRFAX 138.00] TO BUS 300929 [2FAIRFAX 69.00] CKT 1 | 48.5518 | PASS | 10.9379 | PASS | 10837.9102 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 300141 [4STILWTR 138.00] TO BUS 301413 [2STILWTRKAMO 69.00] CKT 1 | 48.5556 | PASS | 10.9374 | PASS | 10837.3533 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515044 [SEMINOL4 138.00] TO BUS 515055 [MAUD 4 138.00] CKT 1 | 48.5476 | PASS | 10.9378 | PASS | 10837.7597 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515224 [MUSKOGE7 345.00] TO BUS 515302 [FTSMITH7 345.00] CKT 1 | 48.515 | PASS | 10.9379 | PASS | 10837.9043 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515852 [DGRASSE7 345.00] CKT 1 | 48.4367 | PASS | 10.9077 | PASS | 10807.6622 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 516106 [BOBCAT 7 345.00] CKT 1 | 48.4439 | PASS | 10.9389 | PASS | 10838.8895 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532782 [BUFFALO7 345.00] CKT 1 | 48.4414 | PASS | 10.9409 | PASS | 10840.9361 | 43.99 | 50.4
GEN-2026-PR14 PSIS | 04 SOUTHEAST | 29WP | GEN-2026-PR14 | 345kV Bus at OGE Sooner - Cleveland Substation, Pawnee County, OK | OPEN LINE FROM BUS 562900 [G15052_1 345.00] TO BUS 562901 [G15052_2 34.5.00] CKT 1 | 48.568 | PASS | 10.9383 | PASS | 10838.2673 | 43.99 | 50.4

## WSCR
* WSCR is not applicable for this study.